## Slide 1
2017 RTP
TPL Sensitivity Analysis

## Slide 2
Overview
Purpose
Protocol Requirements
Scenario Specifications
Assumption and Methodology

## Slide 3: Purpose and Protocol Requirements
The purpose is to study the impact of varying one or more of the system conditions as listed in R 2.4.3 of NERC TPL-001-4 reliability standards.
Requirement 2.4.3 of NERC Standard TPL-001-4 states:
2.4.3. For each of the studies described in Requirement R2, Parts 2.4.1 and 2.4.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in performance:
 Load level, Load forecast, or dynamic Load model assumptions.
 Expected transfers.
 Expected in service dates of new or modified Transmission Facilities.
 Reactive resource capability.
 Generation additions, retirements, or other dispatch scenarios.

## Slide 4: Assumption and Methodology
Sensitivity analysis will be performed on summer peak base cases for 2019 (year 2) and 2022 (year 5) and an off-peak case for 2020 (year 3)
All assumptions and performance criteria will be held consistent with the 2017 RTP scope and process document

## Slide 5: Scenario Specifications
Condition | Region | Variable | Study years
Summer peak | All regions | Dispatch: Wind and Hydro units in all weather zones will be modeled offline (None in East and Coast weather zones) (Units will be taken completely out of service, including reactive support) | 2019, 2022
Off-peak | All regions | Dispatch and Demand: Wind generation dispatch is increased with a moderate change in system wide demand to simulate HWLL conditions | 2020

## Slide 6: Assumptions No Wind No Hydro for Summer Peak Cases
All hydro units in each study region are turned off in the respective base cases
The table below summarizes the status of wind units for each study region
Region | Wind Units Offline | Wind Units Online
South/South Central/East/Coast | Wind units in South and South Central zones | Wind units in West, Far West, and North zones
North/North Central/West/Far West | Wind units in West, Far West, and North zones | Wind units in South and South Central zones

## Slide 7: Assumptions No Wind No Hydro for Summer Peak Cases
The following table summarizes the change in dispatch (MW of wind and hydro generation being turned off) resulting from the sensitivity
Year | Wind (MW) in RTP Cases |  |  |  | Hydro (MW) in RTP Cases |  |  | 
 | EC | NNC | WFW | SSC | EC | NNC | WFW | SSC
2019 | - | 492 | 307 | 726 | - | 124 | 92 | 228
2022 | - | 492 | 307 | 726 | - | 124 | 92 | 228

## Slide 8: Assumptions High Wind Low Load for Off Peak Cases
Wind
Use the historical capacity factors for wind units based on top 20 high wind conditions for each zone:
  91.9% capacity factor for PANHANDLE
  63.6% capacity factor for SOUTH (COASTAL)
  92.6% capacity factor for WEST and NORTH
Applying the historical capacity factors, the dispatchable wind in the HWLL case is approximately 12,872 MW

## Slide 9: Assumptions High Wind Low Load for Off Peak Cases
Load
The load level was determined by reviewing historical load levels during top wind hours
The following table summarizes the change in dispatch and demand resulting from the sensitivity
Year | 2017 RTP Min Case Load (MW) | 2017 RTP HWLL Case Load (MW)
2020 | 33,692 | 37,938