## Slide 1
UFLS Workshop Discussion #3
Matt Mereness
Director of Compliance
June 28, 2017

## Slide 2: UFLS Discussion outline
Antitrust Admonition
Recap of Workshops #1 & 2
  Background on issues being considered regarding the UFLS Compliance Survey and the Operations/Planning expectations
Workshop #3 Goals
  ERCOT to discuss follow-up items
  Market Participants to consider draft NOGRR
Appendix
  NERC requirement excerpt
  UFLS examples
  Potential Load Resource data to provide

## Slide 3: Recap- Background on UFLS Survey Requirement
ERCOT Compliance coordinates and conducts an annual survey with the TSPs and DSPs to ensure that the required automatic under-frequency load shed circuits are configured to provide the appropriate load relief in an under-frequency event as required by table below from Operating Guides 2.6.1(1) Requirements for Under-Frequency Load Shedding:
2016 results were 7.2% / 12.2% / 12.6% for total of 31.23%

## Slide 4: Recap- Current Issues with UFLS (why being discussed)
ERCOT Compliance was asked at OWG in 2016 about clarifying the assumptions for measurement of UFLS in the survey, as well as emerging operational concerns.
For reference:
NERC Requirements reflect Planning Coordinator shall have a “UFLS program design”
  See Appendix for NERC details
Operating Guide 2.6.1 is the design of ERCOT Automatic Load Shedding
  In effect since zonal Operating Guides in 2010
Issues:
For the survey just reviewed, current OpGuide language reflects the approach of “At least 25% of the ERCOT System Load that is not equipped with high-set under-frequency relays shall be equipped at all times with provisions for automatic under-frequency load shedding.”
  Survey data collected does not identify or align circuits with Load Resources for exclusion
There has also been some “double-counting” discussions over whether Load Resources that deploy at 59.7 Hz can be counted towards the UFLS response at 59.3Hz

## Slide 5: Recap- First two workshops
Key discussions to date
  Recognize there are at least two scenarios of UFLS being activated
    Sudden event: normal day but then significant loss of generation (starting point of 60Hz and no LR deployed)
    Slow-burn event: system is in emergency operations (EEA2), LR deployed, and then loss of generation
  In both cases, need for 25% of armed UFLS to arrest frequency
  ERCOT view that as frequency drops from 60 to 59.7 to 59.3, that the measurement of 25% response is tied to what the Load was when crossing 59.3 and initiating UFLS levels.
  Agreement that annual Compliance survey measurement should align with expected Operations compliance (post event reports and analysis)
  ERCOT was asked about creating initial draft reflecting expectations
    Draft NOGRR created and reviewed briefly at April meting
  ERCOT asked about providing inventory of LRs in DSP footprint
    ERCOT noted this is in network model but can also be provided
  ERCOT asked about providing historical trends/deployments
    ERCOT offered to provide annually if market can agree how to summarize (min, max, avg, annual, hourly, etc)

## Slide 6: Goals for this workshop
Today is review 3 action items from April meeting
  Input from ERCOT
    Is DSP the appropriate role/definition for compliance in the NOGRR?
      Consider whether TO is proper entity as the DSP agent (see ERCOT’s updated draft NOGRR)
      TO designation reflects current survey responses
    Is it feasible (with a system change) for TSPs to receive real-time telemetry status of Load Resources from ERCOT?
      Yes, in a similar manner to how all generation is observable by TSPs in telemetry
      Project needed for configuration work to make available
      ERCOT still also open to providing an annual analysis of Load Resources
    Based on percentage of time individual Load Resources are armed, is there a probability approach that would best model expected Load Resources response to see if there is a P90-type fit?
      ERCOT would like to discuss in more detail how this might work
  Input from Market Participants
    STEC comments on a P90 type probabilistic solution
    Potential concern over using DSP or TO as defined participant

## Slide 7
APPENDIX:
NERC requirement excerpt
UFLS examples
Potential Load Resource data to provide

## Slide 8: Appendix- NERC Requirement
NERC standard PRC-006-2 — Automatic Underfrequency Load Shedding:
Requirement 9. Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. [VRF: High][Time Horizon: Long-term Planning]
Measurement 9. Each UFLS Entity shall have dated evidence such as spreadsheets summarizing feeder load armed with UFLS relays, spreadsheets with UFLS relay settings, or other dated documentation that it provided automatic tripping of load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, per Requirement R9.

## Slide 9: Example
Load 20MW
Load 20MW
Load 20MW
Load 20MW
Load 20MW
LR = 1MW
Current Annual Survey language could imply this methodology:
Actual System Load = 100 MW
#1
#2
#4
#3
#5
LR = 10MW
TDSP
X
X
Survey System Load = 100 – 40 (Feeders with any LR) = 60 MW
TDSP Breaker #1 armed at 59.3 = 20MW shed (20/60 = 33%)
TDSP Breaker #2 armed at 58.9 = 20MW shed (20/60 = 33%)
TDSP Breaker #3 armed at 58.5 = 20MW shed (20/60 = 33%)

## Slide 10: Example
Load 20MW
Load 20MW
Load 20MW
Load 20MW
Load 20MW
LR = 1MW
ERCOT assumption in Planning and Operations:
System Load at 60Hz = 100 MW
#1
#2
#4
#3
#5
LR = 10MW
TDSP
X
X
System Load in EEA3 or 59.7 = 100 – 11MW LR = 89 MW
TDSP Breaker #1 armed at 59.3 = 20MW shed (20/89 = 22%)
TDSP Breaker #2 armed at 58.9 = 20MW shed (20/89 = 22%)
TDSP Breaker #3 armed at 58.5 = 20MW shed (20/89 = 22%)
Load 19MW
----------------
Load 10MW
-----------------

## Slide 11: Potential Load Resource data to be provided
TDSP shown on Registration Form
  TDSP Duns
From the Load Resource Asset Registration Form
  Dispatch Asset Code
  ESIID (Load Resources for NOIEs will have a non-settlement ESIID)
  Station the Load Resource is mapped to in the Network Operations Model
  PTI Number
  Transmission Transformer Load Name
  Maximum Registered Interruptible Load
Historical Data (more analysis needed)
  Average hourly RRS Responsibility for LR during a predefined date range
  Maximum RRS Responsibility during the same time period