## Slide 1
NOGRR-169
OWG discussion
Bill Blevins
June 28, 2017

## Slide 2
Agenda
Overview of PRC-002-2
Existing ERCOT Guides
Alignment of Guides with PRC-002

## Slide 3: Phased in PRC-002-2
Each Transmission Owner, and Generator Owner shall maintain documentation to demonstrate compliance with PRC-018-1 until that entity meets the requirements of PRC-002-2 in accordance with the NERC Implementation Plan.
PRC-018-1 Midnight of the day immediately prior to six (6) years after the effective date of PRC-002-2 in the particular jurisdiction in which the new standard is becoming effective.

## Slide 4: Implementation Plan for PRC-002-2 Requirements R1 and R5 (07/01/2016):
R1 covers sequence of events recording (SER) and fault recording (FR) identified by Transmission owners using attachment 1 as the methodology.
Requires Transmission Owners to identify and notify BES locations for SER and FR.
R5 covers dynamic Disturbance recording (DDR) and is identified by ERCOT.
Evaluate the list every 5 years.

## Slide 5: Implementation Plan for PRC-002-2 Requirements R2, R3, R4, R6, R7, R8, R9, R10, R11:
Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date.
Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date.
Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list.

## Slide 6: Implementation Plan for PRC-002-2 Requirements R12 (10/01/2016):
Each Transmission Owner and Generator Owner shall, within 90-calendar days of the discovery of a failure of the recording capability for the SER, FR or DDR data, either:
  Restore the recording capability, or
  Submit a Corrective Action Plan (CAP) to the Regional Entity and implement it.

## Slide 7: Guide Revision summary
6.1.1, Introduction
6.1.2, Fault Recording Equipment
6.1.2.1, Triggering Requirements
6.1.2.2, Location Requirements
6.1.2.3, Data Recording Requirements
6.1.2.4, Data Retention and Reporting Requirements
6.1.2.5, Maintenance and Testing Requirements (delete)
6.1.3, Phasor Measurement Recording Equipment
6.1.3.1, Recording Requirements
6.1.3.2, Location Requirements
6.1.3.3, Data Recording and Redundancy Requirements
6.1.3.4, Data Retention and Reporting Requirements
6.1.4, Maintenance and Testing Requirements (new)
6.1.4, Equipment Reporting Requirements
6.1.5, Review Process
8, Attachment M, Selecting Buses for Capturing Sequence of Events Recording and Fault Recording Data (new)

## Slide 8: Guide Revision summary
ERCOT proposes a new attachment to Section 8, rather than broadly referencing the North American Electric Reliability Corporation (NERC) Reliability Standards. The new attachment is consistent with Attachment 1 to NERC Reliability Standard PRC-002-2, Define Regional Disturbance Monitoring and Reporting Requirements.
ERCOT proposes to insert the time required to comply with Fault Recording and Sequence of Events Recording Equipment installations, which align with the required NERC implementation timeline.
ERCOT inserts paragraphs (1)(a) through (e), (2), and (3) in Section 6.1.3.2, Location Requirements, to address new requirements for existing generation under NERC Reliability Standard PRC-002-2, Define Regional Disturbance Monitoring and Reporting Requirements, R5. This allows for generation identified to align their dynamic disturbance recording required locations with the NERC timeline.
ERCOT also restores the 18-month implementation date for phasor measurement recording equipment in paragraph (4)(b) of Section 6.1.3.2. The 18-month implementation date was added on June 1, 2015 after approval of NOGRR142, Phasor Measurement, and just became effective for new units on January 1, 2017.