| NOGRR Number | 170 | NOGRR Title | Alignment with NPRR824, Alignment of EEA Level 3 with NERC Reliability Standards EOP-011-1 and BAL-001-2 |
| --- | --- | --- | --- |
| Date of Decision |  | June 28, 2017 |  |
| Action |  | Approved |  |
| Timeline |  | Normal |  |
| Effective Date |  | Upon system implementation of Nodal Protocol Revision Request (NPRR) 824, Alignment of EEA Level 3 with NERC Reliability Standards EOP-011-1 and BAL-001-2 |  |
| Priority and Rank Assigned |  | Not applicable |  |
| Nodal Operating Guide Sections Requiring Revision |  | 4.5.3, Implementation 4.5.3.1, General Procedures Prior to EEA Operations |  |
| Related Documents Requiring Revision/Related Revision Requests |  | NPRR824 |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) revises the Nodal Operating Guide to be consistent with NPRR824 language relating to North American Electric Reliability Corporation (NERC) Reliability Standards EOP-011-1, Emergency Operations, and BAL-001-2, Real Power Balancing Control Performance. Pursuant to paragraph (5) of Section 1.3.1, Introduction, this NOGRR does not modify Section 4.5.3.3, EEA Levels. An Alignment NOGRR will be posted upon ERCOT Board approval of NPRR824 to maintain alignment of Protocol Section 6.5.9.4.2, EEA Levels, with NOG Section 4.5.3.3. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | This NOGRR aligns the Nodal Operating Guide with the Protocols and applicable NERC Reliability Standards. |  |
| OWG Decision |  | On 4/20/17, the Operations Working Group (OWG) was in consensus to recommend approval of NOGRR170 as submitted. On 5/18/17, OWG was in consensus to endorse and forward to ROS the 4/20/17 OWG Report and Impact Analysis for NOGRR170. |  |
| Summary of OWG Discussion |  | On 4/20/17, participants reviewed the situational differences between EEA Level 3 with and without firm Load shed and noted the need for an Alignment NOGRR for Section 4.5.3.3. On 5/18/17, there was no discussion. |  |
| ROS Decision |  | On 6/8/17, ROS unanimously voted to recommend approval of NOGRR170 as recommended by OWG in the 5/18/17 OWG Report. All Market Segments were present for the vote. |  |
| Summary of ROS Discussion |  | On 6/8/17, there was no discussion. |  |
| TAC Decision |  | On 6/28/17, TAC unanimously voted via email to approve NOGRR170 as recommended by ROS in the 6/8/17 ROS Report. All Market Segments were present for the vote. |  |
| Summary of TAC Discussion |  | On 6/28/17, there was no discussion. |  |

| Sponsor |  |
| --- | --- |
| Name | Stephen Solis |
| E-mail Address | stephen.solis@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-6772 |
| Cell Number | 512-426-4721 |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Cory Phillips |
| E-Mail Address | cory.phillips@ercot.com |
| Phone Number | 512-248-6464 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None |  |

Market Rules Notes

Administrative changes to the language were made and authored as “ERCOT Market Rules.”

Proposed Guide Language Revision

- 4.5.3	Implementation

(1)	ERCOT shall be responsible for monitoring system conditions, initiating the EEA levels below, notifying all Qualified Scheduling Entities (QSEs) and Transmission Operators (TOs), and coordinating the implementation of the EEA conditions while maintaining transmission security limits.  QSEs and TOs will notify all the Market Participants they represent of each declared EEA level.

(2)	During the EEA, ERCOT has the authority to obtain energy from non-ERCOT Control Areas using Direct Current Tie(s) (DC Tie(s)) or by using Block Load Transfers (BLTs) to move load to non-ERCOT Control Areas.  ERCOT maintains the authority to curtail energy schedules flowing into or out of the ERCOT System across the DC Ties in accordance with North American Electric Reliability Corporation (NERC) scheduling guidelines.

(3) 	ERCOT, at management’s discretion, may at any time issue an ERCOT-wide appeal through the public news media for voluntary energy conservation.

(4)	There may be insufficient time to implement all levels in sequence.  ERCOT may immediately implement Level 3 of the EEA any time the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes and shall immediately implement Level 3 any time the steady-state frequency is below 59.5 Hz for any duration.

(5)	Percentages for Level 3 Load shedding will be based on the previous year’s TSP peak Loads, as reported to ERCOT, and will be reviewed by ERCOT and modified annually.

(6)	The ERCOT System Operator shall declare the EEA levels to be taken by QSEs and TSPs.  QSEs and TSPs shall implement actions under that level (and all above if not previously accomplished) and if ordered by the ERCOT shift supervisor or his designate, shall report back to the ERCOT System Operator when the requested level has been completed.

(7)	During EEA Level 3, ERCOT must be capable of shedding sufficient firm Load to arrest frequency decay and to prevent generator tripping.  The amount of firm Load to be shed may vary depending on ERCOT Transmission Grid conditions during the event.  Each TSP will be capable of shedding its allocation of firm Load, without delay.  The maximum time for the TSP to interrupt firm Load will depend on how much Load is to be shed and whether the Load is to be interrupted by Supervisory Control and Data Acquisition (SCADA) or by the dispatch of personnel to substations.  Since the need for firm Load shed is immediate, interruption by SCADA is preferred.  The following requirements apply for an ERCOT instruction to shed firm Load:

(a)	Load interrupted by SCADA will be shed without delay and in a time period not to exceed 30 minutes;

(b)	Load interrupted by dispatch of personnel to substations to manually shed Load will be implemented within a time period not to exceed one hour;

(c)	The initial clock on the firm Load shed shall apply only to Load shed amounts up to 1000 MW total.  Load shed amount requests exceeding 1000 MW on the initial clock may take longer to implement; and

(d)	If, after the first Load shed instruction, ERCOT determines that an additional amount of firm Load should be shed, another clock will begin anew.  The time frames mentioned above will apply.

(8)	Each TSP, or its designated agent, will provide ERCOT a status report of Load shed progress within 30 minutes of the time of ERCOT’s instruction or upon ERCOT’s request.

(9)	During EEA Level 2 or 3, for those constraints that meet the criteria identified in paragraph (3)(a) of Section 4.2.2, Advisory, ERCOT may control the post-contingency flow to within the 15-Minute Rating in SCED.   After Physical Responsive Capability (PRC) is restored to at least 3,000 MW or the Emergency Condition has ended, whichever is later, and ERCOT has determined that system conditions have improved such that the chance of re-entering into an EEA Level 2 or 3 is low, ERCOT shall restore control to the post-contingency flow to within the Emergency Rating for these constraints that utilized the 15-Minute Rating in Security Constrained Economic Dispatch (SCED).

(10)	During EEA Level 2 or 3, for those constraints that meet the criteria identified in paragraph (3)(b) of Section 4.2.2, ERCOT shall continue to enforce constraints associated with double-circuit contingencies throughout an EEA if the double-circuit failures are determined to be at high risk of occurring, due to system conditions.  For all other double-circuit contingencies identified in paragraph (3)(b) of Section 4.2.2, ERCOT will enforce only the associated single-circuit contingencies during EEA Level 2 or 3.  ERCOT shall resume enforcing such constraints as a double-circuit contingency after PRC is restored to at least 3,000 MW or the Emergency Condition has ended, whichever is later, and ERCOT has determined that system conditions have improved such that the chance of re-entering into an EEA Level 2 or 3 is low.  For constraints related to stability limits that are not IROLs, ERCOT may elect not to enforce double-circuit contingencies during EEA Level 3 only.

- 4.5.3.1 	General Procedures Prior to EEA Operations

(1)	Prior to declaring EEA Level 1 detailed in Section 4.5.3.3, EEA Levels, ERCOT may perform the following operations consistent with Good Utility Practice:

(a)	Provide Dispatch Instructions to QSEs for specific Resources to operate at an Emergency Base Point to maximize Resource deployment so as to increase Responsive Reserve levels on other Resources;

(b)	Commit specific available Resources as necessary that can respond in the timeframe of the emergency.  Such commitments will be settled using the Hourly Reliability Unit Commitment (HRUC) process;

(c)	Start Reliability Must-Run (RMR) Units available in the time frame of the emergency.  RMR Units should be loaded to full capability;

(d)	Utilize available Resources providing Non-Spinning Reserve (Non-Spin) services as required; and

(e)	ERCOT shall use the PRC and system frequency to determine the appropriate Emergency Notice and EEA levels.