## Slide 1
PDCWG Report to ROS
Chair: Percy Galliguez, Brazos Electric Power Cooperative, Inc.
Vice Chair: Lei Ye, Austin Energy
ROS
July 13th, 2017

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-1 FMEs & IMFR
    2 FME in the month of May
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 6/14/17
  NPRR 815/828 Discussion
  Regulation & Frequency Control Reports
  GREDP Performance Analysis
  BAL-001-TRE-01 R6 Combined Cycle Steam Unit Discussion
  MOD-026-1 Discussion
    NOGRR Proposal/Review Status
  Two FMEs Reviewed for May
    5/19/2017 19:25:37
      Loss of 416 MW
      800 MW/0.1Hz
      2 of 21 Evaluated RRS Providers had less than 75% of their expected Initial Primary Frequency Response.
      1 of 21 Evaluated RRS Providers had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 4: Meeting Minutes
PDCWG Meeting 6/14/17(Cont’d)
  Two FMEs Reviewed for May(Cont’d)
    5/21/2017 18:25:03
      Loss of 448 MW
      830 MW/0.1Hz
      2 of 19 Evaluated RRS Providers had less than 75% of their expected Initial Primary Frequency Response.
      2 of 19 Evaluated RRS Providers had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 5: Frequency Measurable Events Performance
May 2017

## Slide 6: Frequency Measurable Events
There was 2 FMEs in May
  5/19/2017 19:25:37
    Loss of 416 MW
    Interconnection Frequency Response:
    12 of 42 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    9 of 42 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  5/21/2017 18:25:03
    Loss of 448 MW
    Interconnection Frequency Response:
    6 of 47 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    5 of 47 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 7: Interconnection Minimum Frequency Response (IMFR) Performance
IMFR Performance currently 941.63 MW/0.1Hz

## Slide 8: Frequency Control Report
May 2017

## Slide 9: CPS1 Performance

## Slide 10: RMS1 Performance of ERCOT Frequency

## Slide 11: Frequency Profile Analysis

## Slide 12: Time Error Corrections
There were no Time Error Corrections (TEC) in May
Notes: TEC occurred on 12/03/2016 at 23:30. Time Error was 30.06

## Slide 13: ERCOT Total Energy

## Slide 14: ERCOT Total Energy from Wind Generation

## Slide 15: ERCOT % Energy from Wind Generation

## Slide 16
Questions?