## Info
Header Information
TDSP | Operator of the Major Transmission Element.
Major Transmission Element (MTE) | Transmission Element which was, or scheduled to be, on outage and has been associated with one or more high congestion(s).
Equip. Type | Equipment Type of the MTE.
kV | Voltage Level of the MTE.
Congestion Year/Month | Year and Month the associated congestion occurred.
Contingency | Contingency associated with the MTE.
Overload | Overload associated with the MTE.
Source | Source of the information: RT = Based on historical Real-Time congestion, ST = Based on Outage Coordination Studies. ADD = Addition Requests (both Private and Public)
Outage Type | Outage Type is categorized to be either Planned (PL) and Forced (FR, FE, UE, M1, M2, M3)
Cancel | Outage(s) for the specific MTE was Cancelled, Rejected, or Withdrawn.
Removal Requestor | Stakeholder who is requesting to remove the MTE from the list (Organization)
Addition Requestor | Stakeholder who is requesting to add the MTE from the list (Organization)
Reason for Addition | Justification for adding the MTE to the list. Details of the specific scenarios that the MTE may cause high congestion, including but not limited to: 1. ERCOT Load Level: Peak, Off-Peak (or 35GW, 70GW, etc). 2. Any specific regional load condition: High Houston Load, etc. 3. Wind Generation Level: High, Mid, Low, or N/A. 4. Solar Geneartion Level: High, Mid, Low, or N/A. 5. Any specific abnormal transmission equipment status: i.e. 345 kV line from A to B out-of-service, etc. 6. For Private Submissions, any specific generator output level: i.e. Resource A at 300 MW or above, etc. 7. (Optional) PSSE or PowerWorld case if available.
Reason for Removal | Justification for removing the MTE from the list. Usually entails a Transmission Upgrade Project.
OCITF Consensus | Consensus after OCITF meetings.
Decision | Final (TAC) Decision of the Addition/Removal Request for Non-Consensus items.
Discussion Items | Any other information that stakeholder(s) want to discuss during the OCITF meetings.

## MTE(2017)
TDSP | Major Transmission Element (MTE) | Equip. Type | kV | Congestion Year/Month | Contingency | Overload | Source | Outage Type | Cancel | Removal Requestor | Reason for Removal | OCITF Consensus | Decision | Discussion Items
AEN | Aen Dunlap - Techridge | LN | 138 | 15/4, 15/5 | DCKT Hutto to Round Rock & Gabriel 138 kV, Hutto Sw Auto MR1 345/138 kV | Gilleland - McNeil LCRA 138 kV, Pflugerville - Gilleland 138 kV | RT, ST | Planned
AEN | Austrop - Aen Dunlap | LN | 138 | 16/10, 15/2 | DCKT Sandow Sw to Austrop 345 kV, DCKT Garfield Lcra to Lytton Springs & Austrop to Zorn 345 kV | Gilleland - Mcneil Lcra 138 kV, Garfield Aen Auto AT1 345/138 kV | RT, ST | Planned, Forced
AEN | Austrop - Daffin Gin | LN | 138 | 15/5, 16/6, 16/10, 16/4 | Howard Lane Tap to Wells Branch 138 kV, DCKT Garfield Aen to Hicross Aen & Onion Creek to Stoney Ridge 138 kV, DCKT Sandow Sw to Austrop 345 kV, DCKT Garfield to Stoney Ridge & Hicross 138 kV | McNeil - Howard Lane Tap 138 kV, McNeil Lcra - McNeil Aen 138 kV, Gilleland - Mcneil Lcra 138 kV | RT, ST | Planned
AEN | Brodie - Slaughter Lane | LN | 138 | 16/8 | DCKT Ferguson to Granite Mountain & Wirtz to Paleface 138 kV | Flat Rock - Wirtz 138 kV | ST | Planned
AEN | Decker Power Plant - Aen Dunlap | LN | 138 | 15/4, 15/5 | DCKT Hutto to Round Rock & Gabriel 138 kV, DCKT Garfield Aen to Stoney Ridge & Hicorss 138 kV | Gilleland - McNeil LCRA 138 kV, McNeil Lcra - McNeil Aen 138 kV | RT, ST | Planned
AEN | Garfield Aen - … - Onion Creek | LN | 138 | 15/4 | DCKT Garfield Lcra to Lytton Springs & Austrop to Zorn 345 kV | Decker - Aen Dunlap | ST | Planned
AEN | Garfield Aen - Hicross | LN | 138 | 15/4 | DCKT Garfield Lcra to Lytton Springs & Austrop to Zorn 345 kV | Decker - Aen Dunlap | ST | Planned
AEN | Hamilton Aen CB HM_950 | CB | 138 | 15/4 | DCKT Burleson to Carson Creek 138 kV & Pedernales to Advanced Micro Devices Aen 138 kV | Manesium Plant - Northlan 138 kV | RT | Forced
AEN | Howard Lane Aen - Techridge | LN | 138 | 17/1 | DCKT Austrop to Daffin Gin & Aen Dunlap to Decker 138 kV | Howard Lane Tap - Howard Lane Aen 138 kV | ST | Planned
AEN | Lytton Springs - Pilot Knob | LN | 138 | 16/9 | DCKT Austrop to Daffin Gin & Aen Dunlap to Decker 138 kV | McNeil Aen - Howard Lane Aen 138 kV | ST | Planned
AEN | Lytton Springs Auto AT1 | XF | 345 | 16/1 | DCKT Garfield to Stoney Ridge & Hicross 138 kV | Lytton Springs Auto AT2 345/138 kV | ST | Forced
AEN | Sprinkle - Daffin Gin | LN | 138 | 15/6 | DCKT Round Rock to Hutto & Gabriel 138 kV | Gilleland - McNeil Lcra 138 kV | ST | Planned
AEN, LCRA | Fayette Plant 2 - Holman Aen | LN | 345 | 16/7, 17/4 | DCKT Lost Pines Aen to Austrop & Aen Dunlap 345 kV, DCKT Lost Pines Aen to Fayette Plant 1 345 kV | Fayetteville Auto AT2 345/138 kV | RT, ST | Planned, Forced
AEN, LCRA | Fayette Plant 2 - Lytton Springs | LN | 345 | 16/7, 17/4 | DCKT Lost Pines Aen to Austrop & Aen Dunlap 345 kV, DCKT Lost Pines Aen to Fayette Plant 1 345 kV | Fayetteville Auto AT2 345/138 kV | RT, ST | Planned, Forced | Y
AEN, LCRA | Lytton Springs Bus #1 (CB 21400, 950, etc.) | BUS | 138 | 16/8 | DCKT Garfield to Stoney Ridge & Hicross 138 kV | Lytton Springs Auto AT2 345/138 kV | ST | Planned
AEN, LCRA | Lytton Springs Bus #2 (CB 21420, 951, etc.) | BUS | 138 | 16/8 | DCKT Garfield to Stoney Ridge & Hicross 138 kV | Lytton Springs Auto AT1 345/138 kV | ST | Planned
AEN, LCRA | McNeil Lcra - McNeil Aen | LN | 138 | 15/5 | Howard Lane Tap to Wells Branch 138 kV | McNeil - Howard Lane Tap 138 kV, McNeil Lcra - Howard Lane Tap 138 kV | RT, ST | Planned | Y
AEP | Air Liquid Sw - Oxychem Ingleside | LN | 138 | 16/4 | Dupont Pp1 Ingleside to Ingleside Cogen Sw 138 kV (3A) | Duppont Pp1 Ingleside - Duppont Sw Ingleside 138 kV | ST | Planned
AEP | Airline - Cabniss | LN | 138 | 15/10 | Alazan to Barney Davis 138 kV | Barney Davis - Rodd Field 138 kV | ST | Forced |  | AEP | SPS revised to eliminate this and new construction by end of year to remove SPS
AEP | Ajo - Rio Hondo | LN | 345 | 16/2, 17/2 | DCKT Lon Hill to North Edinburg 345 kV & Orange Grove Sw 138 kV | Celanese Bishop - Nelson Sharpe 138 kV, Lon Hill - Bessel 138 kV | ST | Planned
AEP | Armstrong Aep - … - Raymondville 2 | LN | 138 | 16/3 | Valley Import | N/A | RT | Forced
AEP | Aspermont Aep - Paint Creek | LN | 138 | 16/4 | Scurry Sw to Sun Sw 138 kV | Paint Creek Auto 69-2 138/69 kV | RT | Forced
AEP | Barney Davis - ... - Nelson Sharpe | LN | 138 | 16/4, 16/9, 16/10, 16/11 | Gila to Hiway 9 138 kV, DCKT Barney Davis to Airline Aep & Rodd Field 138 kV, Cabaniss to Airline Aep 138 kV | Morris Street - Gila 138 kV, Airline AEP - Cabaniss 138 kV, Rodd Field - Holly 138 kV | ST | Planned |  | AEP | New cables in service currently and reconfigured back to original by Fall, new circuit between Cabiness and Airline by end of year
AEP | Barney Davis Bus #1 (CB 6755, etc.) | BUS | 138 | 16/10 | DCKT Barney Davis to Airline Aep 138 kV | Barney Davis - Rodd Field 138 kV | ST | Planned | Y
AEP | Barney Davis Bus #2 (CB 5200, etc.) | BUS | 138 | 16/10, 17/2, 17/3 | Airline Aep to Barney Davis 138 kV | Rodd Field - Holly 138 kV | ST | Planned, Forced | Y
AEP | Beeville - … - Victoria | LN | 69 | 17/4 | Hecker to WhitePoint 138 kV | Whitepoint - Rincon 138 kV | RT | Planned
AEP | Bessel - Lon Hill | LN | 138 | 15/9 | Lobo Auto A2 345/138 kV | Alice - North Ella 69 kV | ST | Planned |  | AEP | 2nd Lobo 345kv auto in service as of July 2017 so contingency does not have same result
AEP | Bevo - Asherton | LN | 138 | 15/11 | Basecase | Low Voltage from Dimmit to DC Eagle Pass | ST | Forced
AEP | Bruni - Crestonio | LN | 138 | 15/5, 15/6 | Laquinta to Lobo 138 kV | Bruni Auto 69_1 138/69 kV | ST | Planned | Y, N
AEP | Celanese Bishop Bus #1 (CB 6305, 8425) | BUS | 138 | 16/10 | Airline Aep to Barney Davis 138 kV | Rodd Field - Holly 138 kV | ST | Planned | Y
AEP | Celanese Bishop Bus #2 (CB 6075, 8425) | BUS | 138 | 16/10 | Airline Aep to Barney Davis 138 kV | Rodd Field - Holly 138 kV | ST | Planned | Y
AEP | Coleto - Lon Hill | LN | 345 | 17/3, 15/3, 16/1, 16/12 | DCKT Whitepoint to Hecker & Dupont Sw Ingleside 138 kV, Coleto Creek to Pawnee Sw 345 kV, Pawnee Sw to Lon Hill 345 kV | Whitepoint - Rincon 138 kV, Kenedy Sw - Coleto Creek 138 kV, Magruder - Victoria 138 kV, Kenedy Sub - Kenedy Sw 69 kV | RT, ST | Planned, Forced | Y, N
AEP | Coleto - Victoria (COLETO_VICTOR1) | LN | 138 | 17/4 | Coleto Creek 345_138h 345/138 kV | Coleto Creek - Victoria 138 kV | RT | Planned
AEP | Del Sol - … - North Edinburg | LN | 345 | 16/10, 17/1 | Valley GTC | N/A | ST | Planned | Y
AEP | Dupont Sw Ingleside - ... - Portland | LN | 138 | 15/1 | DCKT Dupont Sw Ingleside to Whitepoint & Hecker 138 kV | Rincon - Whitepoint 138 kV | ST | Planned
AEP | Encinal - … - North Laredo Sw | LN | 138 | 15/9, 17/2 | Lobo Auto A2 345/138 kV | Freer - San Diego 69 kV, Asherton - Catarina 138 kV | ST | Planned | Y | AEP | 2nd Lobo 345kv auto in service as of July 2017 so contingency does not have same result
AEP | Falcon Sw - Roma Sw | LN | 138 | 15/5 | Lobo Auto A2 345/138 kV | Asherton - Catarina 138 kV | ST | Planned |  | AEP | 2nd Lobo 345kv auto in service as of July 2017 so contingency does not have same result
AEP | Falfurrias - King Ranch Gas Plant | LN | 138 | 16/7 | Lobo Auto A2 345/138 kV | Dilley Sw Aep - Jardin 138 kV | RT | Forced |  | AEP | 2nd Lobo 345kv auto in service as of July 2017 so contingency does not have same result
AEP | Fannin Sub - Victoria | LN | 69 | 17/4 | Coleto Creek 345_138h 345/138 kV | Coleto Creek - Victoria 138 kV | RT | Planned
AEP | Garza - Roma Sw | LN | 138 | 16/11 | Generator Stability | N/A | ST | Planned |  | AEP | Generation has moved to 345kv and is off 138kv system
AEP | Gila - Hiway 9 (GILA_HIWAY_1) | LN | 138 | 17/4 | Hecker to WhitePoint 138 kV | Whitepoint - Rincon 138 kV | RT | Forced |  | AEP | Only 1 cable was in service but 2nd was in model with outage. Both cables are now in service
AEP | Gila - Hiway 9 (GILA_HIWAY_2) | LN | 138 | 17/4 | Hecker to WhitePoint 138 kV | Whitepoint - Rincon 138 kV | RT | Forced |  | AEP | Only 1 cable was in service but 2nd was in model with outage. Both cables are now in service
AEP | Haine Drive - La Palma | LN | 138 | 17/4 | DCKT Rio Hondo to North Endinburg 345 kV & Harlingen Sw | Burns Sub - Rio Hondo 138 kV | RT | Planned
AEP | Hecker - Dupont Sw Ingleside (HECKER_I_DUPS0) | LN | 138 | 17/4 | Hecker to WhitePoint 138 kV | Whitepoint - Rincon 138 kV | RT | Planned
AEP | Hecker - Dupont Sw Ingleside (HECKER_I_DUPS2) | LN | 138 | 17/4 | Hecker to WhitePoint 138 kV | Whitepoint - Rincon 138 kV | RT | Planned
AEP | Hecker - Whitepoint (HECKER_WHITE_1) | LN | 138 | 17/3 | DCKT Whitepoint to Hecker & Dupont Sw Ingleside 138 kV | Whitepoint - Rincon 138 kV | RT | Planned
AEP | Hiway 9 Auto 69A2 138/69 kV | XF | 138 | 17/4 | Lon Hill Auto 69A1 138/69 kV | Koch Up River Auto 69A1 138/69 kV | RT | Forced
AEP | Industrial Aep - Nueces Bay | LN | 69 | 17/4 | Lon Hill Auto 69A1 138/69 kV | Koch Up River Auto 69A1 138/69 kV | RT | Forced
AEP | Ingleside - Dupont Sw | LN | 138 | 17/4 | Rockport to Rincon 138 kV | Gregory - Rincon 69 kV | ST | Forced
AEP | Jim Treece - Riley | LN | 345 | 16/11 | Panhandle GTC | N/A | ST | Planned
AEP | Jim Treece - Tesla | LN | 345 | 16/11 | Panhandle GTC | N/A | ST | Planned | Y
AEP | Joslin Bus #1 (CB 8315, etc.) | BUS | 138 | 17/3 | Formosa Unit FORMOSG12, Formosa Unit FORMOSG3 | Formosa - Lolita 138 kV | RT | Planned
AEP | Koch Hearns Ferry - Koch Up River | CB | 138 | 16/5 | Gila to Hiway 9 138 kV | Morris Street - Gila 138 kV | ST | Planned |  | AEP | 2nd cable in service and Morris street line will be reterminated into N. Bay and disconnect from Gila by Aug
AEP | La Palma Bus #2 (CB 5875, etc.) | BUS | 138 | 17/2 | North Edinburg Auto 1382 345/138 kV | Burns Sub - Rio Hondo 138 kV | RT | Planned
AEP | Las Pulgas - Raymondville 2 | LN | 138 | 17/4 | DCKT Rio Hondo to North Endinburg 345 kV & Harlingen Sw | Burns Sub - Rio Hondo 138 kV | RT | Planned
AEP | Las Pulgas - Rio Hondo | LN | 138 | 17/4 | Loyola Sub to Kleberg Aep 138 kV | Loyola Sub Auto 69_1 138/69 kV | ST | Planned
AEP | Lobo - Laquinta | LN | 138 | 15/5 | Crestonio to Falfurrias 138 kV | Bruni Auto 69_1 138/69 kV | ST | Planned | Y
AEP | Lobo - Laredo Vft North | LN | 138 | 15/4 | Laredo VFT North to Lobo 138 kV | Asherton - Catarina 138 kV | ST | Planned
AEP | Lon Hill - Equistar | LN | 138 | 16/4 | Gila to Hiway 9 138 kV | Morris Street - Gila 138 kV | ST | Planned |  | AEP | 2nd cable in service and Morris street will be reterminated into N. Bay and disconnect from Gila by Aug
AEP | Lon Hill - Nelson Sharpe | LN | 345 | 15/2, 15/10, 16/3, 16/4 | DCKT Lon Hill to North Edinburg 345 kV & Orange Grove Sw 138 kV, Ajo to Rio Hondo 345 kV | Bunsen - Lon Hill 138 kV, Celanese Bishop - Kleberg 138 kV | ST | Planned | Y
AEP | Lon Hill Auto 69A2 138/69 kV | XF | 138 | 17/4 | Hecker to WhitePoint 138 kV, Lon Hill Auto 69A1 138/69 kV | Whitepoint - Rincon 138 kV, Koch Up River Auto 69A1 138/69 kV | RT | Planned
AEP | Lon Hill Bus #1 (CB 6005, etc.) | BUS | 138 | 15/5 | Lobo Auto A2 345/138 kV | Asherton - Catarina 138 kV | ST | Planned |  |  | 2nd Lobo 345kv auto in service as of July 2017 so contingency does not have same result
AEP | Lopeno - Zapata | LN | 138 | 16/7 | Lobo Auto A2 345/138 kV | Asherton - Catarina 138 kV | ST | Planned |  | AEP | 2nd Lobo 345kv auto in service as of July 2017 so contingency does not have same result
AEP | Molina - … - Rio Bravo | LN | 138 | 16/7 | Goodwin to La Grulla 138 kV | Bates - Liston 138 kV | ST | Forced |  | AEP | Generation has moved to 345kv and is off 138kv system
AEP | Morris Street - Gila | LN | 138 | 16/5, 17/2, 17/3 | DCKT Koch Up River to Gila & Lon Hill to Nueces Bay 138 kV, Jumbo to Koch Up River 138 kV | Gila - Hiway 9 138 kV | ST | Planned | Y | AEP | Circuit will be reterminated into N.Bay by Aug. 1st and so will not exist next year
AEP | Morris Street - Nueces Bay | LN | 138 | 17/4 | Hecker to WhitePoint 138 kV | Whitepoint - Rincon 138 kV | RT | Forced |  | AEP | Circuit was in model but not available. 2nd cable is now in service so overload not correlated to outage.
AEP | Naval Base - … - Port Aransas | LN | 69 | 17/4 | Hecker to WhitePoint 138 kV | Whitepoint - Rincon 138 kV | RT | Planned
AEP | North Edinburg - Lon Hill | LN | 345 | 17/3, 15/3, 16/3 | Nelson Sharpe to Ajo 345 kV, Nelso Sharpe to Ajo 345 kV, DCKT Rio Hondo to North Edinburg 345 kV & Harlingen Sw 138 kV, Valley GTC | Raymondville 2 - Yturria Sub 138 kV, Celanese Bishop - Nelson Sharpe 138 kV, Burns Sub - Rio Hondo 138 kV, N/A | RT, ST | Planned, Forced
AEP | North Edinburg - Rio Hondo | LN | 345 | 16/3 | North Edinburg to Lon Hill 345 kV | Burns Sub - Rio Hondo 138 kV | ST | Planned
AEP | North Edinburg Auto 138 345/138 kV | XF | 345 | 17/2 | North Edinburg Auto 1382 345/138 kV | Burns Sub - Rio Hondo 138 kV | RT | Planned
AEP | North Edinburg Bus #1 (CB 5010, etc.) | BUS | 138 | 16/9 | North McAllen to North Edinburg 138 kV | North Edinburg - McColl Road 138 kV | ST | Planned
AEP | North Laredo Sw - … - Reveille | LN | 138 | 16/6 | Lobo Auto A2 345/138 kV | Asherton - Catarina 138 kV | ST | Planned | Y, N | AEP | 2nd Lobo 345kv auto in service as of July 2017 so contingency does not have same result
AEP | North McAllen - North Pharr | LN | 138 | 17/4 | North Pharr to Pharr Magic Valley 138 kV | North Mcallen - West Mcallen 138 kV | RT | Forced |  | AEP | circuit did not exist at this time but was in model for future in service but overload was flagged due to line derating that has been fixed
AEP | North Pharr - McColl Road | LN | 138 | 17/4 | North Pharr to Pharr Magic Valley 138 kV | North Mcallen - West Mcallen 138 kV | RT | Forced |  | AEP | circuit did not exist at this time but was in model for future in service but overload was flagged due to line derating that has been fixed
AEP | North Pharr - North Alamo | LN | 138 | 17/4 | North Pharr to Pharr Magic Valley 138 kV | North Mcallen - West Mcallen 138 kV | RT | Forced |  | AEP | N.McAllen-W.McAllen derating has been fixed and now is significantly more capability
AEP | Paint Creek Bus #1 (CB 4135, etc.) | BUS | 138 | 16/5, 16/6, 17/1 | Scurry Sw to Sun Sw 138 kV, Salt Creek Bepc to Salt Creek Reactor 138 kV | Eskota Sw - Longworth 69 kV, Aspermont Auto 69T1 138/69 kV | ST | Planned
AEP | Port Aransas - Seawall Aep | LN | 69 | 17/3 | DCKT Whitepoint to McCambell & Dupons Sw Ingleside 138 kV, DCKT Whitepoint to Hecker & Dupont Sw Ingleside 138 kV | Whitepoint - Rincon 138 kV | RT | Planned
AEP | Raymondville 2 - … - Rio Hondo | LN | 138 | 16/12 | Loyola Sub to Kleberg Aep 138 kV | Loyola Sub Auto 69_1 138/69 kV | ST | Planned
AEP | Rio Bravo - … - Wormser Rd | LN | 138 | 15/2 | Bates to Frontera 138 kV | Frontera - Goodwin 138 kV | RT | Planned |  | AEP | Generation has moved to 345kv and is off 138kv system
AEP | Rio Grande City - Garceno | LN | 138 | 16/11 | Generator Stability | N/A | ST | Planned |  | AEP | Generation has moved to 345kv and is off 138kv system
AEP | San Angelo Concho - Rusthill | LN | 138 | 15/6 | San Angelo College Hills Auto 69T1 138/69 kV | San Angelo Power Station Auto 69T1 138/69 kV | RT | Forced
AEP | San Angelo Concho Auto 69T1 | XF | 138 | 15/2, 15/6, 15/7 | San Angelo North Auto 69T1 138/69 kV, San Angelo College Hills Auto 69T1 138/69 kV | San Angelo College Hills Auto 69T1 138/69 kV, San Angelo Power Station Auto 69T1 138/69 kV | RT | Planned, Forced
AEP | San Angelo Red Creek Auto T2 345/138 kV | XF | 345 | 16/10 | San Angelo Red Creek Auto T1 345/138 kV | Nicole - Orient 138 kV | RT | Planned
AEP | South Carbide - Hwy 511 Sub | LN | 138 | 16/6 | South Carbide to Loma Alta Sub 138 kV | La Palma - Villa Cavazos 138 kV | ST | Planned
AEP | Stratton - King Rach Gas Plant | LN | 138 | 15/9 | Lobo Auto A2 345/138 kV | Dilley Sw - Jardin 138 kV | ST | Forced |  | AEP | 2nd Lobo 345kv auto in service as of July 2017 so contingency does not have same result
AEP | Tesla - Jim Treec | LN | 345 | 17/2 | Panhandle GTC | N/A | ST | Planned
AEP | West Batesville Bus #1 (CB 1005, etc.) | BUS | 138 | 15/4 | Lobo to San Miguel 345 kV | Hamilton Road - Maverick 138 kV | ST | Planned
AEP, BRAZOS | Salt Creek Bepc - … - Spur | LN | 138 | 16/3, 16/10 | Aspermont Aep to Spur 138 kV | Spur Auto 69_1 138/69 kV | ST | Planned | Y, N
AEP, CROSS | Gray - Tesla (GRAY_TESLA_1) | LN | 345 | 17/1 | Panhandle GTC | N/A | RT | Forced
AEP, CROSS, SHARYLAND | Tesla - … - Tule Canyon (1) | LN | 345 | 16/5, 16/11, 16/12 | Panhandle GTC | N/A | RT, ST | Planned, Forced
AEP, CROSS, SHARYLAND | Tesla - … - Tule Canyon (2) | LN | 345 | 16/5, 16/11, 16/12 | Panhandle GTC | N/A | RT, ST | Planned, Forced
AEP, STEC | Lobo - San Miguel | LN | 345 | 15/11, 16/4 | Rio Bravo to Zapata 138 kV, Javalina Tap to Rio Bravo 138 kV | Freer - San Diego 69 kV, Voltage Collapse | ST | Planned
AEP, STEC | Loop 463 - Victoria | LN | 138 | 16/3 | Four Corners to Sam Rayburn Sw 138 kV | Sam Rayburn Switching Station Auto 69_2 138/69 kV | ST | Planned
AEP, STEC | Moore Sw - Downie Sw | LN | 138 | 16/10, 17/4 | Downie Switching Station to Uvalde Aep 138 kV | Downie Switching Station Auto AX1 138/69 kV | ST | Planned | Y
AEP, WET | Edith Clarke - Wett_Cottonwood (COTTON_EDITHC3) | LN | 345 | 16/11, 16/12, 17/1, 17/2, 17/3, 17/4 | Panhandle GTC | N/A | RT, ST | Planned, Forced
AEP, WET | Edith Clarke - Wett_Cottonwood (COTTON_EDITHC4) | LN | 345 | 16/11, 16/12, 17/1, 17/2, 17/3, 17/4 | Panhandle GTC | N/A | RT, ST | Planned, Forced
BPUB | Palo Alto Sub - Titan Sub | LN | 138 | 16/5 | South Carbide to Loma Alta Sub 138 kV, Loma Alta Sub T1 138/69 kV | La Palma - Villa Cavazos 138 kV | RT | Planned
BPUB | Waterport Sub - Loma Alta Sub 138 kV | LN | 138 | 16/5 | South Carbide to Loma Alta Sub 138 kV, Loma Alta Sub T1 138/69 kV | La Palma - Villa Cavazos 138 kV | RT | Planned
BPUB, TMPA | Gibbons Creek - Btu_Jack_Creek | LN | 345 | 17/4, 16/1 | DCKT Jewett to Singleton 345 kV | Gibbons Creek - Twin Oak Sw 345 kV, BTU_Jack_Creek Auto XF1 345/138 kV | RT, ST | Planned | Y
BRAZOS | Jaybird - Stephenville Bepc | LN | 138 | 16/11 | Mineral Wells to Mineral Wells West 138 kV | Bunker - RW Miller 138 kV | ST | Planned
BRAZOS | Navo - Krugerville | LN | 138 | 15/10 | Jim Christal Sub to West Denton 138 kV | Pockrus Sub - Teasely Sub 138 kV | ST | Forced
BRAZOS | Rw Miller - Jaybird | LN | 138 | 16/11 | Mineral Wells to Mineral Wells West 138 kV | Bunker - RW Miller 138 kV | ST | Planned
BRAZOS | San Miguel Auto ATA | XF | 345 | 15/3, 16/2 | DCKT Lon Hill to North Edinburg 345 kV & Orange Grove Sw 138 kV, Pawnee Sw to San Miguel 345 kV | Fannin Sub - Victoria 69 kV, San Miguel Auto ATB 345/138 kV | ST | Planned | Y
BRAZOS | San Miguel Auto ATB | XF | 345 | 15/10 | Lobo Auto AT2 345/138 kV | San Miguel Auto ATA 345/138 kV | ST | Planned
BRAZOS | Stephenville Bepc Auto FMR1 | XF | 138 | 15/3 | Oran Sub to Mineral Wells & RW Miller 138 kV | Bunker - RW Miller 138 kV | ST | Planned
BRAZOS | Whitney Bus 1525 (CB 5075, etc.) | BUS | 138 | 16/12 | Bosque Sw to Elm Mott 345 kV | Bosque Sw - Rogers Hill Bepc 138 kV | ST | Forced
BRAZOS | Whitney Bus BB1 (CB 210, etc.) | BUS | 69 | 16/12 | Bosque Sw to Elm Mott 345 kV | Bosque Sw - Rogers Hill Bepc 138 kV | ST | Forced
BRAZOS, DME, ONCOR | Arco - Navo - Collin Ses | LN | 138 | 16/6, 16/7, 16/8, 16/9, 17/3 | Fort Worth Sub to West Denton 138 kV, Jim Christal Sub to West Denton 138 kV, DCKT Lewisville Sw to Krum West Sw & Roanoke Sw 345 kV | Jim Christal Sub - West Denton 138 kV, Fort Worth Sub - West Denton 138 kV, Corinth (Oncor) - Pockrus Sub 138 kV | RT | Planned
BRAZOS, ONCOR | Carrollton Northwest - Lewisville Sw | LN | 345 | 17/3 | Jones Street Tnp to Lewisville | Ti Tnp - West Tnp 138 kV | RT | Planned
BRAZOS, ONCOR | Elm Mott - Bosque Sw | LN | 345 | 16/3 | Whitney Auto FMR2 345/138 kV | Whitney Auto WHT1 345/138 kV | ST | Planned
BRAZOS, ONCOR | Holder - Brownwood Sw | LN | 138 | 17/4 | Mercers Gap Sw to Comanche Sw (Oncor) 138 kV | Evant - Goldthwaite 138 kV | ST | Planned | Y
BRAZOS, TMPA | Gibbons Creek - Keith Sw 138 kV | LN | 138 | 16/10 | Gibbons Creek to Btu_East 138 kV | Gibbons Creek - Btu_Greens_Prairie 138 kV | RT | Planned
BTU | Btu_Dansby - Btu_Atkins | LN | 138 | 17/3 | Btu_Industrial_Park to Btu_North 69 kV | Btu_East - Btu_Shady_Lane 69 kV | RT | Planned
BTU | Btu_Dowling - Btu_Texas_Am | LN | 138 | 17/3 | Btu_Industrial_Park to Btu_North 69 kV | Btu_East - Btu_Shady_Lane 69 kV | RT | Planned
BTU | Btu_East - Btu_Shady_Lane 69 | LN | 69 | 16/6 | Btu_Atkins Auto FMR1 138/69 kV | Btu_Briarcrest - Btu_Nall_Lane 69 kV | RT | Forced
CNP | Airpro - Shell | LN | 138 | 16/8 | DCKT Chambers to King & Cedar Bayou to Jordan 345 kV | Aritek - Chorin 138 kV | RT | Forced
CNP | Bayton - … - Haney | LN | 138 | 16/4 | DCKT Chambers to King & Cedar Bayou Plant to Jordan 345 kV | Center - Ph Robinson 345 kV | ST | Planned
CNP | Bellaire - Wa Parish | LN | 345 | 16/10 | DCKT Wa Parish to Jeanetta 345 kV | Bellaire - Smithers 345 kV | ST | Planned
CNP | Bigvue - Power Systems Arco Cogen | LN | 138 | 17/4 | DCKT Cedar Bayou Plant to Quanum & Strang 138 kV | Channelview - Lynch 138 kV | RT | Planned
CNP | Cedar Bayou Plant - Decker Power Plant | LN | 138 | 15/3 | DCKT Cedar Bayou Plant to Baytown & Strang 138 kV | South Channel - Shell 138 kV | ST | Planned
CNP | Center - Ph Robinson | LN | 345 | 16/5, 16/3 | Meadow to Ph Robinson 345 kV, Ph Robinson Auto AT4 345/138 kV, DCKT Chambers to King & Cedar Bayou Plant to Jordan 345 kV, DCKT Cedar Bayou Plant to Chambers & Jordan 345 kV, DCKT Chambers to King & Cedar Bayou Plant to Jordan 345 kV | Meadow Auto AT1 345/138 kV, Cedar Bayou Plant Auto AT3 345/138 kV, Brine - Langston 138 kV, Cedar Bayou Plant - Strang 138 kV, Chorin - Strang 138 kV | RT, ST | Planned | Y
CNP | Dow Chemical - South Texas Project | LN | 345 | 16/9 | DCKT WA Parish to Bailey & Hillje 345 kV | Dow Chemical - South Texas Project 345 kV | RT | Planned
CNP | East Bernard - Orchard | LN | 138 | 15/10 | South Lane City to Dyann 138 kV | Peters - Sealy 138 kV | ST | Planned | Y
CNP | East Bernard CB G510 & G530 and DSC 2605 | CB, DSC | 138 | 16/1 | DCKT Texas Gulf Sulphur to West Columbia (04) & South Lane City (60) 138 kV | El Campo - Lane City Pump 138 kV | ST | Planned | Y
CNP | Eastside - University | LN | 138 | 16/2 | DCKT Bellaire to Kirby (37) & Garrott to HO Clarke (90) | Downtown - Crockett 138 kV | ST | Planned | Y
CNP | Flewellen - … - Peters | LN | 138 | 16/4 | DCKT Flewellen to Obrien & Mason Road 138 kV | Betka - Hockley 138 kV | ST | Planned
CNP | Flewellen - Obrien | LN | 138 | 16/12 | Mason Road to Obrien 138 kV | Betka - Hockley 138 kV | ST | Planned
CNP | Fort Bend - Reading | LN | 138 | 15/2 | DCKT Flewellen to Obrien & Mason Road 138 kV | Tomball - Hockley 138 kV | RT | Planned
CNP | Goodyear - Lydell | LN | 138 | 17/4 | DCKT Greens Bayou to Gable & Hardy to Crockett 138 kV | Midtown - Garrott 138 kV | RT | Planned
CNP | Greens Bayou Auto AT2 | XF | 345 | 16/2 | DCKT Greens Bayou to King 345 kV | Greens Bayou Auto AT1 345/138 kV | ST | Planned
CNP | Hillje - Wa Parish (HLJWAP64) | LN | 345 | 16/3 | DCKT South Texas Project to Dow Chemial & Jones Creek 345 kV | South Texas Project - Wa Parish 345 kV | RT | Planned
CNP | Jeanetta Auto AT3 345/138 kV | XF | 345 | 17/4 | Bellaire to Smithers 345 kV | Bellaire - Wa Parish 345 kV | RT | Planned
CNP | Jewett - Limestone (225) | LN | 345 | 15/3 | DCKT Limestone to Twin Oak Sw 345 kV | Big Brown Ses - Jewet (50) | ST | Planned
CNP | Jewett - Limestone (226) | LN | 345 | 15/3 | DCKT Limestone to Twin Oak Sw 345 kV | Big Brown Ses - Jewet (50) | ST | Planned
CNP | Oasis - Dow Chemical (DOWOAS27) | LN | 345 | 16/9 | DCKT WA Parish to Bailey & Hillje 345 kV | Oasis - Dow Chemical 345 kV (18) | RT | Planned, Forced
CNP | Obrien - Flewellen | LN | 138 | 16/4 | Mason Road to Obrien 138 kV | Betka - Hockley 138 kV | RT | Planned, Forced
CNP | Ph Robinson - Center | LN | 345 | 15/3 | DCKT Chambers to King & Cedar Bayou Plant to Jordan 345 kV | Brine - Langston 138 kV | ST | Planned
CNP | Ph Robinson Auto AT2 345/138 kV | XF | 345 | 16/6 | Ph Robinson Auto AT1 345/138 kV | Meadow Auto AT1 345/138 kV | RT | Planned
CNP | Roans Prairie - Singleton | LN | 345 | 16/1 | DCKT Gibbons Creek to Singleton 345 kV | Jewett - Singleton 345 kV (240) | RT | Planned
CNP | Singleton - Zenith (SNGZEN98) | LN | 345 | 15/12, 17/1, 17/2, 17/3, 17/4, 15/7 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV, DCKT Singleton to Tomball & Roans Prairie 345 kV, DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV, Kuykendahl to Rothwood 345 kV, DCKT Singleton to Tomball & Roans Prairie 345 kV | Singleton - Zenith 345 kV (99), Bellville South - Peters 138 kV, Singleton - Zenith 345 kV (99), Singleton - Tomball 345 kV (74) | RT, ST | Planned, Forced | Y
CNP | Singleton - Zenith (SNGZEN99) | LN | 345 | 15/12, 17/2, 17/3, 17/4, 17/1 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV, DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV, Kuykendahl to Rothwood 345 kV | Singleton - Zenith 345 kV (98), Bellville South - Peters 138 kV, Singleton - Zenith 345 kV (98), Singleton - Tomball 345 kV (74) | RT, ST | Planned | Y
CNP | South Lane City - New Gulf | LN | 138 | 15/12 | DCKT Wharton to East Bernard & Dyann 138 kV (UNSOLVED) | N/A | ST | Planned
CNP | South Texas Project Bus A (CB Y500, etc.) | BUS | 345 | 16/3 | DCKT Dow Chemical to South Texas Project 345 kV | South Texas Project - Hillje 345 kV (3124) | ST | Planned | Y
CNP | Wa Parish - Jeanetta (64) | LN | 345 | 17/4 | Bellaire to Smithers 345 kV | Bellaire - Wa Parish 345 kV | RT | Forced
CNP | Wa Parish - Jeanetta (72) | LN | 345 | 17/4 | Bellaire to Smithers 345 kV | Bellaire - Wa Parish 345 kV | RT | Planned
CNP | White Oak - Jeanetta | LN | 345 | 15/9 | DCKT Bellaire to WA Parish & Smithers 345 kV | Bellaire - Sharpstown 138 kV | ST | Forced
CNP | White Oak Auto AT3 345/138 kV | XF | 345 | 16/6 | DCKT Britmoore to Sauer 138 kV | Bellaire - San Felipe 138 kV | RT | Planned
CNP, CPS | South Texas Project - Elm Creek (STPELM18) | LN | 345 | 16/4 | DCKT Marion to Clear Springs & Zorn 345 kV | Comal - Henne 138 kV | ST | Planned
CNP, CPS | South Texas Project - Elm Creek (STPELM27) | LN | 345 | 16/4 | DCKT Marion to Clear Springs & Zorn 345 kV | Comal - Henne 138 kV | ST | Planned
CNP, ONCOR | Jewett - Singleton (240) | LN | 345 | 15/10, 16/2 | DCKT Gibbons Creek to Singleton 345 kV | Jewett - Singleton 345 kV (260) | ST | Planned
CNP, ONCOR | Jewett - Singleton (260) | LN | 345 | 16/1, 15/10 | DCKT Gibbons Creek to Singleton 345 kV | Jewett - Singleton 345 kV (240) | RT, ST | Planned
CNP, TMPA | Gibbons Creek - Singleton (SNGXGC99) | LN | 345 | 15/12, 17/4, 17/1 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV, DCKT Jewett to Singleton 345 kV | Singleton - Zenith 345 kV (98), Singleton - Zenith 345 kV (99), Singleton - Gibbons Creek 345 kV (75), Singleton - Gibbons Creek 345 kV (75), Sandow Sw - Bell County East Sw (421) | RT, ST | Planned | Y
CNP, TMPA | Gibbons Creek Bus 5200 (CB 5030, etc.) | BUS | 345 | 17/3 | DCKT Jewett to Singleton 345 kV | Singleton - Gibbons Creek 345 kV (75) | ST | Planned
CNP, TMPA | Singleton - Gibbons Creek (SNGXGC75) | LN | 345 | 17/1, 17/4 | DCKT Jewett to Singleton 345 kV | Gibbons Creek - Singleton 345 kV, Singleton - Gibbons Creek 345 kV (99), Singleton - Gibbons Creek 345 kV (99), Sandow Sw - Bell County East Sw (421) | RT, ST | Planned
CPS | Ballpark - … - Olmos | LN | 138 | 15/5 | DCKT Calaveras to Walzem & Skyline 138 kV | Ball Park - Fern 138 kV | RT | Planned
CPS | Cagnon Auto MR3 | XF | 345 | 15/6 | Cagnon Auto MR1 345/138 kV | Cagnon Auto MR4 345/138 kV | ST | Planned | Y
CPS | Cibolocr - ... - Green_Mt | LN | 138 | 15/2 | DCKT Hill Country to Marion & Elmcreek 345 kV | Marion - Skyline 345 kV | RT | Planned
CPS | Elmcreek - Hill Country | LN | 345 | 15/10 | DCKT Marion to Hill Country & Skyline 345 kV | EC Mornhinweg - Parkway Lcra 138 kV | ST | Planned
CPS | Hill Country Bus #1 (CB 11T4, etc.) | BUS | 138 | 15/6 | Cagnon Auto MR1 345/138 kV | Cagnon Auto MR4 345/138 kV | ST | Planned | Y
CPS | Holbrook - Kirby 138 kV | LN | 138 | 16/10 | DCKT Calaveras to Hotwells & Laredo1 138 kV | Kirby - St_Hedwg 138 kV | RT | Planned
CPS | Laredo 1 - Five Pts | LN | 138 | 15/5 | DCKT Calaveras to Walzem & Skyline 138 kV | Ball Park - Fern 138 kV | RT | Planned
CPS | Nacdches - Wb Tuttle | LN | 138 | 17/1 | DCKT Cagnon to Tcc & Pinn_Rd 138 kV | Medinabs - 36Th Street 138 kV | ST | Planned
CPS | Skyline - Elmcreek (P4_E5_1) | LN | 345 | 16/11 | DCKT Hill Country to Marion & Elmcreek 345 kV | Cibolo - Schertz 138 kV | RT | Planned
CPS | Skyline - Elmcreek (P4_E5_2) | LN | 345 | 16/11 | DCKT Hill Country to Marion & Elmcreek 345 kV | Cibolo - Schertz 138 kV | RT | Planned
CPS | Txresrch (V3) - Castrvll (D1) | LN | 138 | 16/8, 16/10 | Somerset to Howard 138 kV | Pleasanton Sub - Tordillo 69 kV | ST | Planned | Y
CPS | Weiderstein - Randolph | LN | 138 | 15/9 | DCKT Skyline to Harmony & Nachches 138 kV | Fratt - Parkway Lcra 138 kV | ST | Planned | Y
CROSS | Gray South Bus (CB G130, etc.) | BUS | 345 | 16/5 | DCKT Alibates to Tule Canyon 345 kV | Low Voltage in Panhandle area | ST | Planned | Y
CROSS | Railhead - Gray | LN | 345 | 16/3, 16/5 | Panhandle GTC, Panhandle GTC, DCKT Alibates to Tule Canyon 345 kV | N/A, N/A, Low Voltage in Panhandle area | RT, ST | Planned | Y
CROSS, SHARYLAND | Alibates - Gray | LN | 345 | 16/3, 16/5 | Panhandle GTC, DCKT Alibates to Tule Canyon 345 kV | N/A, Low Voltage in Panhandle area | ST | Planned | Y
DME | Cooper Creek Sub - Industrial Sub | LN | 138 | 15/7 | Lewisville Sw Auto FMR2 345/138 kV | Pockrus Sub - Teasely Sub 138 kV | ST | Planned
DME | Teasley - Forth Worth | LN | 138 | 15/10 | Denton Arco to North Denton Interchange 138 kV | Hickory - Locust 69 kV | ST | Planned
DME, TMPA | Cooper Creek Sub - … - Denton Arco | LN | 138 | 15/7 | Lewisville Sw Auto FMR2 345/138 kV | Pockrus Sub - Teasely Sub 138 kV | ST | Planned
DME, TMPA | Fort Worth Sub - West Denton | LN | 138 | 16/10 | DCKT Lewisville Sw to Krum West Sw & Roanoke Sw 345 kV | Jim Christal Sub - West Denton 138 kV | ST | Planned | Y
DME, TMPA | North Denton - Arco - Denton Arco | LN | 138 | 15/7, 16/4, 16/5 | DCKT Lewisville Sw to Krum West Sw & Roanoke Sw 345 kV, DCKT Roanoke Sw to West Denton & Lewisville Sw to Krum West Sw 345 kV | Teasley Sub - Pockrus Sub 138 k, Fort Worth Sub - West Denton 138 kV | RT | Planned, Forced
GAR | Elmgrove - … - Olinger | LN | 138 | 15/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned
GAR | Elmgrove - Wylie Sw | LN | 138 | 16/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned
GAR | Wylie Sw - Olinger (WYL_OLI1) | LN | 138 | 16/4 | Greenville Steam to Shelby 138 kV | Shelby Auto BT1 138/69 kV | ST | Forced
GAR | Wylie Sw - Olinger (WYL_OLI2) | LN | 138 | 15/9, 16/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned
GAR | Wylie Sw - Olinger (WYL_OLI3) | LN | 138 | 16/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned
GEUS, TMPA | Diesel - Greenville Steam | LN | 69 | 15/7 | Shelby Auto BT1 138/69 kV | Greenville Steam Auto XT1 138/69 kV | ST | Planned
LCRA | Bakersfield Sw - Big Hill | LN | 345 | 17/2, 17/3 | Bakersfield GTC | N/A | RT | Planned
LCRA | Bevo Auto BEVO | XF | 138 | 15/6 | Bevo Sub to Asherton 138 kV | Hamilton Road - Maverick 138 kV | RT | Planned
LCRA | Clear Springs - Gilleland | LN | 345 | 15/3 | Lytton Springs Auto AT2 345/138 kV | Lytton Springs Auto AT1 345/138 kV | ST | Planned
LCRA | Clear Springs - Zorn | LN | 345 | 16/4 | DCKT Marion to Clear Springs & Zorn 345 kV | Clear Spring Auto AT1 345/138 kV | ST | Planned
LCRA | Fayette Plant 1 - Fayette Plant 2 | LN | 345 | 15/3, 16/4 | DCKT Lost Pines Aen to Austrop & Aen Dunlap 345 kV | Fayetteville Auto AT2 345/138 kV | ST | Planned
LCRA | Fayette Plant 1 - Fayetteville | LN | 345 | 15/2, 15/3 | DCKT Lost Pines to Austrop & Dunlop 345 kV | Fayette Plant 1 - Fayette Plant 2 345 kV | RT | Planned
LCRA | Fayette Plant 1 - Salem Lcra | LN | 345 | 17/4 | DCKT Lost Pines Aen to Austrop & Aen Dunlap 345 kV | Fayetteville Auto AT2 345/138 kV | ST | Planned
LCRA | Ferguson - Gillespie Lcra | LN | 138 | 15/4, 16/5 | DCKT Ferguson to Granite Mountain & Wirtz to Paleface 138 kV | Flat Rock - Wirtz 138 kV | ST | Planned | Y
LCRA | Ferguson - Sandy Creek Sw | LN | 138 | 17/2 | DCKT Ferguson to Granite Mountain & Wirtz to Paleface 138 kV | Bertram - Burnet 69 kV | ST | Planned
LCRA | Ferguson - Wirtz (40T1891) | LN | 138 | 16/2 | DCKT Ferguson to Wirtz & Coronado 138 kV | Sandy Creek Sw Auto AT1 138/69 kV | ST | Planned
LCRA | Gilleland - McNeil Lcra | LN | 138 | 15/6, 15/10 | Hutto Sw Auto MR1 345/138 kV, DCKT Aen Dunlap to Austrop & Lost Pines Aen 345 kV | Gilleland - Pflugerville 138 kV, Austrop Auto AT1 345/138 kV | RT, ST | Planned
LCRA | Gilleland Auto AT1 | XF | 345 | 15/10 | DCKT Marble Falls to Lakeway & Palefact to Wirtz 138 kV | Flat Rock - Wirtz 138 kV | ST | Planned
LCRA | Goldthwaite - … - Lampasas | LN | 138 | 17/1 | Mercers Gap Sw to Comanche Sw (Oncor) 138 kV | Camp Bowie - Brownwood Sw 138 kV | ST | Planned | Y
LCRA | Marion - Zorn | LN | 345 | 16/3 | DCKT South Texas Project Unit 1 & 2 | Marion - Clear Springs 345 kV | RT | Planned
LCRA | McElmurray Tap Sw DSC MOS_19119 | DSC | 138 | 16/5 | Sweetwater Downtown to Haynes Sub 138 kV | Eskota Sw - Trent 69 kV | ST | Planned
LCRA | Moore Lcra DSC MOS_13021 | DSC | 138 | 16/5 | Sweetwater Downtown to Haynes Sub 138 kV | Eskota Sw - Trent 69 kV | ST | Planned
LCRA | Paleface - ... - Wirtz | LN | 138 | 16/12 | DCKT Ferguson to Coronado & Granite Mountain 138 kV | Sandy Creek Sw Auto AT1 138/69 kV | ST | Planned | Y
LCRA | Sim Gideon - Winchester | LN | 138 | 17/1 | DCKT Fayette Plant 1 to Salem Lcra & Fayettville 345 kV | Smithville - Winchester 138 kV | ST | Planned
LCRA | Twin Buttes Auto AT1 345/138 kV | XF | 345 | 16/10 | San Angelo Red Creek Auto T1 345/138 kV | Nicole - Orient 138 kV | RT | Planned
LCRA | Warvue CB W120 | CB | 138 | 16/5 | DCKT Chambers to King & Cedar Bayou Plant to Jordan 345 kV | Chev - Cedar Bayou Plant 138 kV | ST | Planned | Y, N
LCRA | York Creek - Seguin | LN | 138 | 15/9 | DCKT Zorn to Marion & Clear Springs 345 kV | Comal - Henne 138 kV | ST | Forced
LCRA | Zorn - Hays Energy (388T388) | LN | 345 | 15/11 | Cagnon to Kendall 345 kV & Cico to Menger Creek 138 kV | Medina Lake - Pipe Creek 138 kV | RT | Forced
LCRA | Zorn - Hays Energy (6T227) | LN | 345 | 15/11 | Cagnon to Kendall 345 kV & Cico to Menger Creek 138 kV | Medina Lake - Pipe Creek 138 kV | RT | Forced
LCRA | Zorn - Hutto | LN | 345 | 15/3 | Lytton Springs Auto AT2 345/138 kV | Lytton Springs Auto AT1 345/138 kV | ST | Planned
LCRA | Zorn - Lytton Spring | LN | 345 | 15/2 | Lytton Springs Auto AT1 345/138 kV, Lytton Springs Auto AT2 345/138 kV | Lytton Springs Auto AT2 345/138 kV, Lytton Springs Auto AT1 345/138 kV | ST | Planned
LCRA, ONCOR | Butman - ... - Eskota Sw | LN | 138 | 17/3, 17/4 | Sweetwater Downtown to Haynes Sub 138 kV | Eskota Sw - Trent 69 kV | ST | Planned | Y
LCRA, ONCOR | Elgin Sw - Gilleland | LN | 138 | 16/10 | DCKT Sandow Sw to Austrop 345 kV | Taylor West - Taylor (Oncor) 138 kV | ST | Planned
LCRA, ONCOR | Pflugerville - Gilleland | LN | 138 | 17/1 | Hutto Sw Auto MR1 345/138 kV | Gilleland - McNeil Lcra 138 kV | ST | Planned
LCRA, ONCOR | Round Rock Southeast - Gilleland | LN | 138 | 17/1 | Hutto Sw Auto MR1 345/138 kV | Gilleland - McNeil Lcra 138 kV | ST | Planned
LST, ONCOR | Big Brown Ses - Navarro (10) | LN | 345 | 17/2, 17/4 | DCKT Big Brown Ses to Jewett 345 kV, DCKT Trinidad Ses to Richland Chambers 345 kV | Trinidad Ses - Richland Chambers 345 kV, Big Brown Ses - Jewett 345 kV | RT | Planned
LST, ONCOR | Big Brown Ses - Navarro (60) | LN | 345 | 17/2, 17/4 | DCKT Big Brown Ses to Jewett 345 kV, DCKT Trinidad Ses to Richland Chambers 345 kV, DCKT Limestone to Navarro 345 kV | Trinidad Ses - Richland Chambers 345 kV, Big Brown Ses - Jewett 345 kV | RT, ST | Planned
ONCOR | Anna Sw - Valley Ses (71) | LN | 345 | 15/10, 17/1 | DCKT Valley South to Paris Sw & Valley Ses 345 kV | Payne Sw - Memc West Tap 138 kV, Valley Ses Auto MR1 345/138 kV | ST | Planned | Y
ONCOR | Anna Sw - Valley South | LN | 345 | 16/5 | Valley Ses to Anna Sw 345 kV | Farmersville Sw - Valley South 138 kV | ST | Planned
ONCOR | Anna Sw Auto XF1 | XF | 345 | 16/10 | Anna Sw Auto XF2 345/138 kV | Payne Sw - Memc West Tap 138 kV | ST | Planned
ONCOR | Anna Sw Auto XF2 | XF | 345 | 16/10 | Anna Sw Auto XF1 345/138 kV | Memc West Tap - Van Alstyne 138 kV | ST | Planned
ONCOR | Anna Sw Bus North (CB 7600, etc.) | BUS | 345 | 16/10 | Anna Sw Auto XF1 345/138 kV | Memc West Tap - Van Alstyne 138 kV | ST | Planned
ONCOR | Argyle Bus #1 (CB 1585, etc.) | BUS | 138 | 15/8 | Jim Christal Sub to West Denton 138 kV | Pockrus Sub - Teasely Sub 138 kV | ST | Planned | Y
ONCOR | Benbrook Sw - Sycamore Creek | LN | 345 | 17/2, 17/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Lewisville Sw - Jones Street Tnp 138 kV | RT | Forced
ONCOR | Big Brown Ses - Jewett (50) | LN | 345 | 17/4 | DCKT Trinidad Ses to Richland Chambers 345 kV | Big Brown Ses - Jewett 345 kV | RT | Forced
ONCOR | Brownwood - … - Brownwood Sw | LN | 138 | 17/4, 17/2, 17/3 | Mercers Gap Sw to Comanche Sw (Oncor) 138 kV | Holder Auto FMR1 138/69 kV, Holder Auto FMR1 138/69 kV | RT, ST | Planned | Y
ONCOR | Calmont Sw - … - Eagle Mountain Ses (6185) | LN | 138 | 17/4 | DCKT Eagle Mountain to Saginaw Sw 138 kV | Eagle Mountain Ses - Morris Dido 138 kV (6265) | RT | Planned
ONCOR | Calmont Sw - … - Eagle Mountain Ses (6190) | LN | 138 | 15/6, 15/7, 17/4 | DCKT Eagle Mountain SES to Parker Sw & Hicks Sw 345 kV, DCKT Eagle Mountain SES to Parker Sw & Hicks Sw 345 kv, DCKT Eagle Mountain to Saginaw Sw 138 kV | Calmont Sw - … - Eagle Mountain Ses (6185), Calmont Sw - … - Eagle Mountain Ses (6190), Eagle Mountain Ses - Morris Dido 138 kV (6265) | RT | Planned, Forced
ONCOR | Carrollton Northwest - … - Plano Tennyson (840) | LN | 138 | 16/1, 16/6 | DCKT Carrollton Northwest to Lewisville Sw 345 kV, Lewisville Sw Auto FMR2 345/138 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Fort Worth Sub - West Denton 138 kV | RT | Planned
ONCOR | Carrollton Northwest Bus #1 | BUS | 345 | 17/4 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | RT | Planned
ONCOR | Cedar Crest Sw - … - Mountain Creek Ses (3160) | LN | 138 | 16/12 | Mountain Creek to Cedar Hill Sw 138 kV | Cedar Hill Sw - Mountain Creek Ses 138 kV (3210) | ST | Planned
ONCOR | Cedar Crest Sw - … - Sargent Road 138 kV | LN | 138 | 16/9 | Mountain Creek Ses Unit Unit8 | Industrial Blvd - Compton Street 138 kV | RT | Planned, Forced
ONCOR | Cedar Crest Sw - … - Watermill Sw (3170) | LN | 138 | 16/10 | West Levee Sw Auto MR1 345/138 kV | Industrial Blvd - Compton Street 138 kV | ST | Planned | Y
ONCOR | Cedar Crest Switch East Bus (CB 025, etc.) | BUS | 138 | 15/9 | DCKT Mountain Creek to Cedar Hill Sw & Westmoreland 138 kV | West Levee Sw - Dallas West 138 kV | ST | Planned
ONCOR | Cedar Hill Sw - … - Watermill Sw (3080) | LN | 138 | 16/10 | West Levee Sw Auto MR1 345/138 kV | Industrial Blvd - Compton Street 138 kV | ST | Planned | Y
ONCOR | Cedar Hill Sw - Mountain Creek Ses (3200) | LN | 138 | 15/9, 16/10, 16/11, 16/9 | Polk Street to Oak Cliff South 138 KV, Mountain Creek Ses Auto MR1 138/69 kV, DCKT Mountain Creek Ses to Cedar Crest Sw 138 kV, West Levee Sw Auto MR1 345/138 kV, Spur - … - Salt Creek Bepc, Polk Street to Oak Cliff South 138 kV | Cedar Crest Sw - Oak Cliff South 138 kV, Irving Hunter Ferrell Tap 2 - Trinity River Authority 138 kV, Industrial Blvd - Compton Street 138 kV, Cedar Crest Sw - Oak Cliff South 138 kV | RT, ST | Planned, Forced
ONCOR | Cedar Hill Sw - Mountain Creek Ses (3210) | LN | 138 | 15/9, 16/10, 16/11, 16/9 | Polk Street to Oak Cliff South 138 KV, Mountain Creek Ses Auto MR1 138/69 kV, DCKT Mountain Creek Ses to Cedar Crest Sw 138 kV, West Levee Sw Auto MR1 345/138 kV, Polk Street to Oak Cliff South 138 kV | Cedar Crest Sw - Oak Cliff South 138 kV, Irving Hunter Ferrell Tap 2 - Trinity River Authority 138 kV, Industrial Blvd - Compton Street 138 kV, Cedar Crest Sw - Oak Cliff South 138 kV | RT, ST | Planned, Forced
ONCOR | Cedar Hill Sw CB 015 | CB | 138 | 16/9 | DCKT Norwood Sw to Liggett Sw & Cedar Hill Sw 345 kV | Cedar Hill Sw - Mountain Creek Ses 138 kV | ST | Planned | Y
ONCOR | Centerville Road Sw - … - Parkdale Sw (3680) | LN | 138 | 16/8 | Scyene Road to Prairie Creek 138 kV | Prairie Creek Sw - Prairie Creek 138 kV | ST | Planned | Y
ONCOR | Centerville Road Sw - Forney Sw | LN | 345 | 15/1 | DCKT Royse Sw to Forney Sw 345 kV | Forney Sw Auto MR3 345/138 kV | ST | Planned
ONCOR | Centerville Road Sw - Garland Road (3240_A) | LN | 138 | 15/9, 16/8 | DCKT Greenville Ave Sw to Parkdale Sw 138 kV, DCKT Allen Sw to Royse Sw & Monticello Ses 345 kV | Centerville Road Sw - Garland Road (3250), Apollo - Richardson East 138 kV | ST | Planned
ONCOR | Cockrell Hill - Mountain Creek Ses | LN | 138 | 15/5 | DCKT Norwood Sw to Liggett Sw & Cedar Hill Sw 345 kV | Trinity River Authority - Mountain Creek Ses 138 kV | ST | Planned | Y
ONCOR | Comanch Peak Ses - Everman Sw | LN | 345 |  | Comanch Peak Ses to Mitchell Bend 345 kV | Comanch Peak Ses - Wolf Hollow 345 Sw 345 kV | ADD
ONCOR | Comanch Peak Ses - Johnson Sw | LN | 345 |  | Comanch Peak Ses to Mitchell Bend 345 kV | Comanch Peak Ses - Wolf Hollow 345 Sw 345 kV | ADD
ONCOR | Comanche Peak Ses - Parker Sw (6016) | LN | 345 |  | Comanch Peak Ses to Johnson Sw & Everman Sw 345 kV | Comanch Peak Ses - Wolf Hollow 345 Sw 345 kV | ADD
ONCOR | Comanche Peak Ses - Parker Sw (6062) | LN | 345 |  | Comanch Peak Ses to Johnson Sw & Everman Sw 345 kV | Comanch Peak Ses - Wolf Hollow 345 Sw 345 kV | ADD
ONCOR | Dealey Street - West Levee Sw | LN | 138 | 16/5 | Watermill Sw Auto MR1 345/138 kV | Industrial Blvd - Compton Street 138 kV | ST | Planned | Y
ONCOR | Eagle Mountain Ses - … - Saginaw Sw (6260) | LN | 138 | 17/4 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned
ONCOR | Eagle Mountain Ses - … - Saginaw Sw (6265) | LN | 138 | 17/4 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned
ONCOR | Eagle Mountain Ses - … - Weatherford Sw | LN | 138 | 16/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Eagle Mountain Poi - Eagle Mountain Ses 138 kV | ST | Planned
ONCOR | Eagle Mountain Ses - Eagle Mountain POI | LN | 138 | 16/1 | Rosen Heights to Rosen Heights Tap 2 | Eagle Mountain Ses - Eagle Mountain Compressor 138 kV | ST | Planned
ONCOR | Eagle Mountain Ses Auto MR1 | XF | 345 | 16/10 | Roanoke Sw Auto MR1 345/138 kV | Roanoke Sw Auto MR2 345/138 kV | ST | Planned | Y
ONCOR | Eagle Mountain Ses Bus West (CB 570, etc.) | BUS | 345 | 16/10 | Roanoke Sw Auto MR1 345/138 kV | Roanoke Sw Auto MR2 345/138 kV | ST | Planned | Y
ONCOR | East Levee Sw - West Netowrk | LN | 138 | 15/5, 15/6 | DCKT West Levee Sw to 800/900 Network 138 kV | East Levee Sw - Reagan Street 138 kV (3410_A) | RT | Planned
ONCOR | East Levee Sw Bus West (CB 032, etc.) | BUS | 138 | 15/11 | Norwood Sw AUTO MR1 345/138 kV | Amelia Street - UT SW Medical Center (3415) | ST | Planned
ONCOR | Elkton - Forney Sw | LN | 345 | 15/4 | Tyler Grande to Martin Lake Ses 345 kV | Elkton Auto MR3 345/138 kV | ST | Planned | Y
ONCOR | Elkton - Martin Lake Ses | LN | 345 | 15/4 | SOP 110 | N/A | ST | Planned
ONCOR | Euless - … - Grapevine Ball Street (1065) | LN | 138 | 17/4 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
ONCOR | Euless - … - Grapevine Ball Street (745) | LN | 138 | 17/4 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned, Forced
ONCOR | Euless - … - Hackberry (745) | LN | 138 | 16/12, 17/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Lewisville Sw - Jones Street Tnp 138 kV | RT | Planned
ONCOR | Euless - … - Liggett Sw (1150) | LN | 138 | 16/6 | DCKT Hackberry to Norwood Sw & Carrollton Northwest 345 kV | Dfw D-East 1 - Dfw C-East (1140) | ST | Planned | Y
ONCOR | Euless - … - Roanoke Sw (1065) | LN | 138 | 16/12, 17/1, 17/2, 17/3, 16/10 | DCKT Carrollton Northwest to Lewisville Sw 345 kV, DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Lewisville Sw - Jones Street Tnp 138 kV, Tyler Northwest - Shamburger Sw 138 kV | RT, ST | Planned
ONCOR | Forest Grove Sw - … - Trinidad Ses | LN | 138 | 16/10 | Trinidad Ses Auto MR7 345/138 kV | Athens - Trinidad Ses 69 kV | ST | Planned
ONCOR | Forney Sw - Royse Sw (200) | LN | 345 |  | Forney Sw - Centerville Road Sw 345 kV | Forney 345/138 kV Auto MR3 | ADD
ONCOR | Forney Sw - Royse Sw (210) | LN | 345 |  | Forney Sw - Centerville Road Sw 345 kV | Forney 345/138 kV Auto MR3 | ADD
ONCOR | General Tire Sw - … - Sandhills Tap | LN | 138 | 16/11 | DCKT Permian Basin Ses to Moss Sw & Holt Sw 138 kV | Yucca Drive Sw - Monahans 138 kV | ST | Planned | Y
ONCOR | Greenville Ave Sw Bus East (CB 025, etc.) | BUS | 138 | 17/2 | West Levee Sw Auto MR1 345/138 kV | Industrial Blvd - Compton Street 138 kV | ST | Planned
ONCOR | Greenville Ave Sw Bus West (CB 022, etc.) | BUS | 138 | 17/2 | West Levee Sw Auto MR1 345/138 kV | Industrial Blvd - Compton Street 138 kV | ST | Planned
ONCOR | Hackberry - … - Liggett Sw (1140) | LN | 138 | 16/6 | DCKT Hackberry to Norwood Sw & Carrollton Northwest 345 kV | Dfw D-East 1 - Irving North 138 kV (1150) | ST | Planned | Y
ONCOR | Hackberry - … - Norwood Sw (100) | LN | 345 | 16/3, 16/7, 17/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Lewisville Sw - Jones Street Tnp 138 kV | RT | Planned
ONCOR | Hicks Sw - … - Saginaw Sw (6270) | LN | 138 | 16/2, 16/3, 17/1 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV, Rosen Heights to Eagle Mountain Compressor 138 kV | Eagle Mountain Ses - Morris Dido 138 kV, Rosen Heights Tap 2 - Morris Dido 138 kV, Wagley Robertson - Summerfield 138 kV | RT, ST | Planned, Forced
ONCOR | Hicks Sw - … - Saginaw Sw (6271) | LN | 138 | 16/2, 16/3, 16/12, 17/1, 16/1, 16/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV, Rosen Heights to Eagle Mountain Compressor 138 kV, Rosen Heights to Eagle Mountain Compressor, DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Eagle Mountain Ses - Morris Dido 138 kV, Rosen Heights Tap 2 - Morris Dido 138 kV, Wagley Robertson - Summerfield 138 kV, Eagle Mountain Ses - Morris Dido 138 kV, Eagle Mountain Poi - Eagle Mountain Ses 138 kV | RT, ST | Planned, Forced
ONCOR | Hicks Sw - Alliance (106) | LN | 345 | 16/4 | Rosen Heights to Eagle Mountain Compressor 138 kV, Eagle Mountain Ses Auto MR1 345/138 kV, DCKT Eagle Mountain Ses to Saginaw Sw 138 kV | Rosen Heights Tap 2 - Morris Dido 138 kV, Eagle Mountain Ses Auto AX2 345/138 kV, Eagle Mountain Ses - Morris Dido 138 kV | RT, ST | Planned | Y
ONCOR | Hicks Sw - Eagle Mountain Ses 138 kV (6276) | LN | 138 | 17/1 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Wagley Robertson - Summerfield 138 kV | RT | Planned
ONCOR | Hicks Sw - Eagle Mountain Ses 138 kV (6277) | LN | 138 | 17/1 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Wagley Robertson - Summerfield 138 kV | RT | Forced
ONCOR | Hicks Sw Bus West (CB 13580, etc.) | BUS | 138 | 16/12, 17/1 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Eagle Mountain Ses - Morris Dido 138 kV, Wagley Robertson - Summerfield 138 kV | RT | Planned
ONCOR | Hicks Sw CB 11615 | LN | 345 | 16/12 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Eagle Mountain Ses - Morris Dido 138 kV, Wagley Robertson - Summerfield 138 kV | RT | Forced
ONCOR | Hutto - … - Round Rock (1660) - … - Georgetown South (1680) 138 kV | LN | 138 | 16/9 | DCKT Temple Sw to Knob Creek Sw 345 kV & Bell County 138 kV | Round Rock - Chief Brady 138 kV | RT | Planned
ONCOR | Hutto Sw Auto MR1 | XF | 345 | 16/10 | DCKT Sandow Sw to Austrop 345 kV | Taylor West - Taylor (Oncor) 138 kV | ST | Planned
ONCOR | Hutto Sw Bus BB1 (CB 7480, etc.) | BUS | 138 | 16/4 | DCKT Hutto Sw to Zorn & Gilleland 345 kV | Hutto Sw - Pflugerville 138 kV | ST | Planned
ONCOR | Jewett Bus #1 (CB 3900, etc.) | BUS | 345 | 16/11 | DCKT Gibbons Creek to Singleton 345 kV | Jewett - Singleton 345 kV (240) | RT, ST | Planned, Forced
ONCOR | Jewett Bus #2 (CB 4000, etc.) | BUS | 345 | 16/9 | DCKT Twin Oak Sw to Gibbons Creek & Btu_Jack_Creek 345 kV | Jewett - Singleton 345 kV (260) | ST | Planned
ONCOR | Kaufman South - … - Trinidad Ses | LN | 138 | 16/10 | Trinidad Ses Auto MR7 345/138 kV | Athens - Trinidad Ses 69 kV | ST | Planned
ONCOR | Keller Tap DSC 3293 | DSC | 138 | 16/6 | DCKT Eagle Mountain Ses to Sagninaw Sw 138 kV | Eagle Mountain Ses - Morris Dido 138 kV | ST | Planned | Y
ONCOR | Lake Creek Ses - … - Wace West | LN | 138 | 16/10 | Waco Lasalle to Waco East 138 kV | ElmMott - Northcrest Tap 138 kV | ST | Planned | Y
ONCOR | Lake Creek Ses Bus #1 (CB 2840, etc.) | BUS | 138 | 15/9 | Waco Mm Mars 2 to Robinson 138 KV, Valley South to Anna Sw & Farmersville Sw 345 kV | Elm Mott - Northcrest Tap 138 kV, Pink Hills Pod - Payne Sw 138 kV | RT, ST | Planned
ONCOR | Lake Hubbard Ses Bus West (CB 280, etc.) | BUS | 138 | 16/4, 17/4 | DCKT Centerville Road Sw to Lake Hubbard Ses 138 kV, DCKT Lake Hubbard Ses to Prairie Creek Sw & Lake June Pump 138 kV | Prairie Creek Sw - Lake Hubbard Ses 138 kV, Centerville Road Sw - Lake Hubbard Ses 138 kV | ST | Planned | Y
ONCOR | Lake Hubbard Ses East Bus (CB 570, etc.) | BUS | 138 | 15/5, 16/3 | DCKT Lake Hubbard Ses to Centerville Road Sw 138 kV | Lake Hubbard Ses - Saint Augustine Tap 138 kV | ST | Planned
ONCOR | Lewisville Sw Auto FMR2 345/138 kV | XF | 345 | 17/4 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | RT | Planned
ONCOR | Lufkin - … - Nacogdoches Se (1350) | LN | 138 | 16/9 | DCKT Mt Enterprise to Trinidad Ses & Martin Lake Ses to Stryker Creek Ses | Herty North Sw - Nacogdoches Se 138 kV | ST | Planned
ONCOR | Lufkin South - … - Lufkin Sw (1370) | LN | 138 | 16/7 | Nacogdoches Se to Mt Enterprise 345 kV | Lufkin - Lufkin Sw 138 kV | RT | Planned
ONCOR | Lufkin Sw - Stryker Creek Ses | LN | 345 | 15/9, 15/10 | Nacogdoches Se to Mt Enterprise 345 kV | Centerville I45 - Pleasant Springs (Hcec) 138 kV | RT | Planned, Forced
ONCOR | Lufkin Sw Auto MR1 | XF | 345 | 15/10 | Nacogdoches Se to Mt Enterprise 345 kV | Centerville I45 - Pleasant Springs (Hcec) 138 kV | RT | Forced
ONCOR | Martin Lake Ses - Mt Enterprise | LN | 345 | 15/3 | SOP 110 | N/A | ST | Planned
ONCOR | Martin Lake Ses - Styker Creek Ses | LN | 345 |  | DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV | Martin Lake Ses - Shamburger Sw 345 kV | ADD
ONCOR | Martin Lake Ses - Tyler Grande | LN | 345 |  | DCKT Martin Lake Ses to Styker Creek Ses & Mt Enterprise 345 kV | Martin Lake Ses - Shamburger Sw 345 kV | ADD
ONCOR | Martin Lake Ses Bus #1 (CB 12645, etc.) | BUS | 345 | 15/4 | DCKT Mt Enterprise to Trinidad & Martin Lake Ses to Stryker Creek Ses | Stryker Creek Ses - Gresham Road Sw 138 kV | ST | Planned
ONCOR | Martin Lake Ses Bus #3 (CB 4780, etc.) | BUS | 345 | 15/3 | SOP 110 | N/A | ST | Forced
ONCOR | Midessa South Sw - Odessa Ehv Sw | LN | 345 | 16/11 | Moss Sw to Odessa Ehv Sw 345 kV | Odessa EHV Sw - Trigas Odessa Tap 138 kV | RT | Planned
ONCOR | Monticello Ses - Sulphur Springs Sw | LN | 345 | 16/3 | DCKT Paris Sw to Valley Ses & Valley South 345 kV | Monticello Ses - Sulphur Springs Sw 345 kV | RT | Planned
ONCOR | Monticello Ses to Farmersville Sw (410) | LN | 345 | 17/3 | DCKT Monticello Ses to Allen Sw & Sulphur Spring Sw 345 kV | Monticello Ses to Farmersville Sw 345 kV (380) | ST | Forced
ONCOR | Mountain Creek Ses - … - West Levee Sw (3380) | LN | 138 | 16/10 | Mountain Creek Ses Auto MR1 138/69 kV | Cedar Crest Sw - Oak Cliff South 138 kV | RT | Planned
ONCOR | Mountain Creek Ses Bus East (CB 600, etc.) | BUS | 138 | 15/11, 15/12, 16/5, 16/11 | Cedar Crest Sw to Mountain Creek Ses 138 kV, Basecase , DCKT Mountain Creek to Cedar Hill Sw & Westmoreland 138 kV, DCKT Watermill Sw to Simpson Stuart 138 kV | Cedar Crest Sw - Oak Cliff South 138 kV (3160), Cedar Crest Sw - Dealy Street 138 kV | ST | Forced
ONCOR | Mountain Creek Ses Bus West (CB 270, etc.) | BUS | 138 | 15/10, 16/11 | Irving Norwood to Norwood Sw 138 kV, Irving Hunter Ferrell to Irving Hunter Ferrell Tap 2 138 kV | Cedar Crest Sw - Oak Cliff South 138 kV (3150) | ST | Planned | Y
ONCOR | Mt Enterprise - Trinidad Ses | LN | 345 |  | DCKT Elkton to Forney & Tyler Grande to Tri Corner 345 kV | Elkton 345/138 kV Auto MR3 | ADD
ONCOR | Nacogdoches - … - Nacogdoches Ses (1450) | LN | 138 | 16/9 | DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV | Tyler Northwest - Shamburger Sw 138 kV | ST | Planned
ONCOR | Navy Kickapoo Sw Auto FMR1 | XF | 138 | 16/7 | Scotland to Scotland (Oncor) 138 kV | Markley (Oncor) - Rice Sw | ST | Planned
ONCOR | Norwood Sw - … - Mountain Creek Ses (3405) | LN | 138 | 16/6 | DCKT Mountain Creek Ses to Cedar Crest Sw 138 kV | Cedar Hill Sw - Mountain Creek Ses 138 kV | ST | Planned | Y
ONCOR | Norwood Sw Auto MR1 | XF | 345 | 15/2 | DCKT Norwood Sw to Mountain Creek & East Levee Sw | Reagan Street - Amelia Street 138 kV | ST | Forced
ONCOR | Norwood Sw Bus #1 (CB 315, etc.) | BUS | 345 | 15/12 | Watermill Sw to Sargent Road & West Levee Sw 345 kV | Norwood Sw Auto MR1 345/138 kV | ST | Planned | Y
ONCOR | Odessa Ehv Sw - … - Spraberry Sw | LN | 138 | 16/10, 16/11 | Moss Sw to Odessa Ehv Sw 345 kV | Odessa EHV Sw - Trigas Odessa Tap 138 kV | RT | Planned
ONCOR | Paris Sw – Monticello Ses | LN | 345 |  | DCKT Paris Sw to Valley Ses & Valley South 345 kV | Paris Sw 345/138 kV Auto MR1 | ADD
ONCOR | Paris Sw - Valley Ses | LN | 345 |  | Paris Sw to Monticello Ses 345kV | Paris Sw 345/138 kV Auto MR1 | ADD
ONCOR | Paris Sw - Valley South | LN | 345 |  | Paris Sw to Monticello Ses 345kV | Paris Sw 345/138 kV Auto MR1 | ADD
ONCOR | Paris Sw Auto MR1 | XF | 345 | 16/1, 17/3 | Sulphur Springs Sw Auto MR1, DCKT Allen Sw to Royse Sw & Monticello Ses 345 kV | Low Voltage around Monticello Mining 138 kV | ST | Planned | Y
ONCOR | Paris Sw Bus BB1 (CB 5195, etc.) | BUS | 138 | 17/3 | DCKT Allen Sw to Royse Sw & Monticello Ses 345 kV | Low Voltage around Monticello Mining 138 kV | ST | Planned | Y
ONCOR | Paris Sw Bus BB2 (CB 6790, etc.) | BUS | 345 | 16/4 | DCKT Paris Sw to Valley Ses & Valley South 345 kV | Paris Sw Auto MR1 345/138 kV | ST | Planned
ONCOR | Paris Sw CB_8635 | CB | 345 |  | DCKT Paris Sw to Valley Ses & Valley South 345 kV | Paris Sw 345/138 kV Auto MR1 | ADD
ONCOR | Park Vista POI DSC 13266 | DSC | 138 | 16/6 | DCKT Eagle Mountain Ses to Sagninaw Sw 138 kV | Eagle Mountain Ses - Morris Dido 138 kV | ST | Planned | Y
ONCOR | Parkdale Sw Bus #2 (CB 600, etc.) | BUS | 138 | 16/10 | DCKT Parkdale Sw to Cenerville Road Sw 138 kV | Prairie Creek Sw - Prairie Creek 138 kV | ST | Planned | Y
ONCOR | Permian Basin Ses - Wink Sub | LN | 138 | 15/6 | Chevron Has to Wickett Whiting Oil 138 kV | Northward - Wink Sub 69 kV | RT | Planned
ONCOR | Permian Basin Ses Bus #2 (CB 2460, etc.) | BUS | 138 | 17/4 | Ward Gulf Tap to Wink Sub 138 kV, Chevron Has to Ward Gulf Tap South 138 kV | Permian Basin Ses Auto MR1 138/69 kV | RT, ST | Planned
ONCOR | Rice Sw - Markley | LN | 138 | 16/2 | Scotland to Scotland (Oncor) 138 kV | Cottonwodd Road Sw - Anarene 69 kV | ST | Planned | Y
ONCOR | Roanoke Sw - Hicks Sw | LN | 345 | 16/4 | Rosen Heights to Eagle Mountain Compressor 138 kV, Eagle Mountain Ses Auto MR1 345/138 kV, DCKT Eagle Mountain Ses to Saginaw Sw 138 kV, Rosen Heights to Rosen Heights Tap 2 | Rosen Heights Tap 2 - Morris Dido 138 kV, Eagle Mountain Ses Auto AX2 345/138 kV, Eagle Mountain Ses - Morris Dido 138 kV, Eagle Mountain Ses - Eagle Mountain Compressor 138 kV | RT, ST | Planned | Y
ONCOR | Roanoke Sw Bus #1 (CB 5550, etc.) | BUS | 345 | 17/4 | Roanoke Sw Auto MR2 345/138 kV | Eagle Mountain Ses - Morris Dido 138 kV | ST | Planned
ONCOR | Royse Sw Auto #1 | XF | 345 | 15/9 | Royse Switch Auto FMR3 345/138 KV | Forney Sw - Forney West 138 kV | RT | Planned
ONCOR | Royse Sw Bus South (CB 4645, etc.) | LN | 138 | 16/11 | DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV | Tyler Northwest - Tyler West 138 kV | ST | Forced
ONCOR | Sandow 5 Ses - Sandow Sw (1726) | LN | 138 |  | Sandow Sw to Sandow Ses 138 kV (1728) | Sandow Ses - Sandow Sw 138 kV (1725) | ADD
ONCOR | Sandow 5 Ses CB_S5360 | CB | 138 |  | Sandow Sw to Sandow Ses 138 kV (1728) | Sandow Ses - Sandow Sw 138 kV (1725) | ADD
ONCOR | Sandow Ses - Sandow Sw (1725) | LN | 138 |  | Sandow Sw to Sandow Ses 138 kV (1728) | Sandow 5 Ses - Sandow Sw 138 kV (1726) | ADD
ONCOR | Sandow Ses CB_5300 | CB | 138 |  | Sandow Ses to Sandow Sw 138 kV (1725) | Sandow 5 Ses - Sandow Sw 138 kV (1726) | ADD
ONCOR | Sandow Ses CB_5320 | CB | 138 |  | Sandow Sw to Sandow Ses 138 kV (1728) | Sandow 5 Ses - Sandow Sw 138 kV (1726) | ADD
ONCOR | Sandow Sw - Austrop (440) | LN | 345 |  | DCKT Sandow Sw to Bell County East Sw | Taylor - Taylor West 138 kV | ADD
ONCOR | Sandow Sw - Austrop (450) | LN | 345 |  | DCKT Sandow Sw to Bell County East Sw | Taylor - Taylor West 138 kV | ADD
ONCOR | Sandow Sw - Bell County East Sw (421) | LN | 345 | 17/2, 17/4 | DCKT Sandow Sw to Austrop 345 kV | Hutto Sw - Taylor West 138 kV | RT, ST | Planned, Forced
ONCOR | Sandow Sw - Bell County East Sw (431) | LN | 345 | 17/2 | DCKT Sandow Sw to Austrop 345 kV | Hutto Sw - Taylor West 138 kV | RT | Forced
ONCOR | Sandow Sw - Sandow Ses (1728) | LN | 138 |  | Sandow Ses to Sandow Sw 138 kV (1725) | Sandow 5 Ses - Sandow Sw 138 kV (1726) | ADD
ONCOR | Sargent Road - Watermill Sw | LN | 345 | 15/3, 16/10 | Topeka Termination to West Levee Sw 345 kV, DCKT West Levee Sw to Sargent Road & Watermill Sw 345 kV | Cedar Hill Sw - Mountain Creek Ses 138 kV, Buntin Drive - Simpson Stuart 138 kV | RT, ST | Planned
ONCOR | Sargent Road - West Levee Sw 345 kV | LN | 345 | 16/9 | Mountain Creek Ses Unit Unit8 | Industrial Blvd - Compton Street 138 kV | RT | Planned
ONCOR | Spraberry Sw - Midessa South Sw 138 kV | LN | 345 | 16/9 | Moss Sw to Odessa Ehv Sw 345 kV | Odessa EHV Sw - Trigas Odessa Tap 138 kV | RT | Planned
ONCOR | Stryker Creek Ses - Trinidad Ses | LN | 345 |  | DCKT Elkton to Forney & Tyler Grande to Tri Corner 345 kV | Elkton 345/138 kV Auto MR3 | ADD
ONCOR | Temple Sw - Bell County East Sw | LN | 345 | 15/3 | Navarro to Watermill Sw 345 kV | Big Brown Ses - Richland Chambers 345 kV | RT | Planned
ONCOR | Tri Corner - Tyler Grande | LN | 345 |  | DCKT Trinidad Ses to Stryker Creek Ses & Mt Enterprise 345 kV | Elkton 345/138 kV Auto MR3 | ADD
ONCOR | Trinidad Ses Bus #1 (CB 4020, etc.) | BUS | 345 | 17/2 | DCKT Big Brown Ses to Jewett 345 kV | Trinidad Ses - Richland Chambers 345 kV | RT | Forced
ONCOR | Tyler East - … - Tyler Grande (1770) | LN | 138 | 16/10, 16/7 | DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV | Tyler Northwest - Shamburger Sw 138 kV | RT, ST | Planned | Y
ONCOR | Valley Ses Bus #2 (CB 3265, etc.) | BUS | 138 | 15/8 | Valley South to Anna Sw & Farmersville Sw 345 kV | Pink Hills Pod - Payne Sw 138 kV | ST | Planned | Y
ONCOR | Venus Sw Bus #1 (CB 4500, etc.) | BUS | 345 | 15/7 | Limits Generation | N/A | ST | Planned
ONCOR | Watermill Sw - West Levee Sw | LN | 345 | 15/3, 16/10 | Topeka Termination to West Levee Sw 345 kV, DCKT Norwood Sw to Liggett Sw & Cedar Hill Sw 345 kV | Cedar Hill Sw - Mountain Creek Ses 138 kV, Buntin Drive - Simpson Stuart 138 kV | RT, ST | Planned | Y
ONCOR | West Levee Sw Auto MR1 | XF | 345 | 16/12 | DCKT Mountain Creek Ses to Cedar Crest Sw 138 kV | Industrial Blvd - Compton Street 138 kV | ST | Planned
ONCOR | Wichita Falls South Sw - … - Windthorst Sw | LN | 138 | 16/10 | Markley (Oncor) to Rice Sw 138 kV | Anarene - Navy Kickapoo Sw 69 kV | ST | Planned
ONCOR, SHARYLAND | Buffalo Sharyland Utilities - … - Stanton East | LN | 138 | 16/11 | Stanton East Auto MR1 138/69 kV | Big Spring West - Stanton East 138 kV | ST | Forced
ONCOR, TMPA | Btu_Jack_Creek - Twin Oak Sw | LN | 345 | 16/12 | DCKT Jewett to Singleton 345 kV | Gibbons Creek - Twin Oak Sw 345 kV | ST | Planned | Y
SHARYLAND | Alibates - Aj Swope Sharyland Utilities | LN | 345 | 17/4 | Panhandle GTC | N/A | ST | Planned
SHARYLAND | Alibates - Tule Canyon (ALIB_TULE_2) | LN | 345 | 17/1 | Panhandle GTC | N/A | RT | Forced
SHARYLAND | Elbow - Bulldog Su | LN | 138 | 16/9 | Moss Sw to Odessa Ehv Sw 345 kV | Trigas Odessa Tap - Odessa Ehv Sw | ST | Planned | Y
SHARYLAND | Grandview Wind Farm - Alibates | LN | 345 | 15/5 | Isolates Generation | N/A | ST | Planned
SHARYLAND | Tule Canyon - White River (TULEC_WHIT_R1) | LN | 345 | 15/11 | Panhandle GTC | N/A | ST | Planned | Y
SHARYLAND | Tule Canyon - White River (TULEC_WHIT_R2) | LN | 345 | 15/11 | Panhandle GTC | N/A | ST | Planned | Y
SHARYLAND | Tule Canyon Bus #1 (CB TCN7100, etc.) | BUS | 345 | 15/6 | Panhandle GTC | N/A | ST | Planned
SHARYLAND | Tule Canyon Bus #2 (CB TCN7102, etc.) | BUS | 345 | 15/6 | Panhandle GTC | N/A | ST | Planned
SHARYLAND | White River - Wett_Cottonwood (WHIT_RV_W_CW1) | LN | 345 | 15/12 | Panhandle GTC | N/A | RT | Planned
SHARYLAND | White River - Wett_Cottonwood (WHIT_RV_W_CW2) | LN | 345 | 15/12 | Panhandle GTC | N/A | RT | Planned
SHARYLAND | Windmill Entire Station | ST | 345 | 16/8 | Basecase | Resource Isolation | ST | Planned | Y
STEC | Paredes Switching Station - Central Avenue Sub | LN | 138 | 16/1, 15/9 | Villa Cavazos to Military Highway Aep 138 kV, Los Fresnos to Loma Alta Sub 138 kV, Villa Cavazos to Military Highway Aep 138 kV | Los Fresnos - Loma Alta Sub 138 kV, La Palma - Villa Cavazos 138 kV, Los Fresnos - Loma Alta Sub 138 kV | RT, ST | Planned
STEC | Sam Rayburn - Vanderbilt | LN | 138 | 15/10 | Loop 463 to Sam Rayburn 138 kV | Sam Rayurn Swithcing Station Auto 69_2 138/69 kV | ST | Planned
STEC | Vanderbilt Sw - Sam Rayburn Sw 138 kV | LN | 138 | 16/1 | Pawnee Sw to Coleto Creek 345 kV | Magruder - Victoria 138 kV | ST | Planned | Y
TMPA | Olinger - … - Pruitt | LN | 138 | 15/7 | Basecase | Low Voltage at Pruitt 138 kV | ST | Planned | Y
TNMP | Dickinson - Freeway Park | LN | 138 | 15/8 | North Alvin Tnp to Meadow 138 KV | PH Robinson to Southshore TNP 138 kV | RT | Forced
TNMP | Freeway Park Tnp - Alvin Tnp | LN | 138 | 16/6, 16/8 | Ph Robinson Auto AT1 345/138 kV, Ph Robinson Auto AT1 345/138 kV, North Alvin Tnp to Meadow 138 kV | Seminole Tnp - Friendswood Tnp 138 kV, Seminole Tnp - Friendswood Tnp 138 kV, Southshore Tnp - Ph Robinson 138 kV | RT, ST | Planned | Y, N
TNMP | Gaf - Greenbelt | LN | 138 | 16/2 | Freeway Park Tnp to Heights Tnp 138 kV | Heights Tnp - Ph Robinson 138 kV | ST | Planned
TNMP | Greenbelt - Amoco Oil Cogen (G138_23) | LN | 138 | 16/2 | Greenbelt to Caddo Sw 138 kV | Greenbelt to Tejas 138 kV | ST | Planned

## Request for Addition (Private)
TDSP | Major Transmission Element (MTE) | Equip. Type | kV | Contingency | Overload | Addition Requestor | Reason for Addition

## Request for Addition (Public)
TDSP | Major Transmission Element (MTE) | Equip. Type | kV | Contingency | Overload | Addition Requestor | Reason for Addition | OCITF Consensus | Decision | Discussion Itesm