## Slide 1
PDCWG Report to ROS
Chair: Percy Galliguez, Brazos Electric Power Cooperative, Inc.
Vice Chair: Lei Ye, Austin Energy
ROS
August 3rd, 2017

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-1 FMEs & IMFR
    9 FME in the month of June
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 7/19/17
  NPRR 815/828 Discussion
  Regulation & Frequency Control Reports
  GREDP Performance Analysis
    Data will be provided but analysis will only be reported on request
  BAL-001-TRE-01 R6 Combined Cycle Steam Unit SAR
  MOD-026-1 & MOD-027-1 Discussion
    NOGRR Proposal/Review Status
Notes: PDCWG discussed NPRR 828 once again in its July meeting. PDCWG had previously discussed NPRR 828 at its June meeting and had laid out their concerns to ERCOT. In the July meeting ERCOT brought back responses to those concerns which included a draft set of comments to modify NPRR 828. ERCOT addressed PDCWG’s concerns. PDCWG discussed these responses further and did not have any additional actions for ERCOT. Three PDCWG members did have some reservations on the NPRR 828 and were planning on addressing their concerns individually.

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There was 9 FMEs in June
  6/2/2017 10:03:08
    Loss of 589 MW
    Interconnection Frequency Response:
    6 of 43 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    5 of 43 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  6/6/2017 18:08:00
    Loss of 452 MW
    Interconnection Frequency Response:
    14 of 45 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    12 of 45 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Frequency Measurable Events
  6/11/2017 3:52:34
    Loss of 443 MW
    Interconnection Frequency Response:
    13 of 49 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    15 of 49 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  6/11/2017 21:42:16
    Loss of 848 MW
    Interconnection Frequency Response:
    4 of 39 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    4 of 39 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 7: Frequency Measurable Events
  6/14/2017 16:55:34
    Loss of 522 MW
    Interconnection Frequency Response:
    13 of 53 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    11 of 53 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  6/16/2017 7:46:23
    Loss of 550 MW
    Interconnection Frequency Response:
    7 of 75 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    5 of 75 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 8: Frequency Measurable Events
  6/16/2017 16:14:23
    Loss of 508 MW
    Interconnection Frequency Response:
    12 of 56 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    10 of 56 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  6/19/2017 9:10:19
    Loss of 449 MW
    Interconnection Frequency Response:
    12 of 58 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    8 of 58 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 9: Frequency Measurable Events
  6/27/2017 15:50:36
    Loss of 594 MW
    Interconnection Frequency Response:
    8 of 46 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    7 of 46 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 10: Interconnection Minimum Frequency Response (IMFR) Performance
IMFR Performance currently 924.84 MW/0.1Hz

## Slide 11: Frequency Control Report
June 2017

## Slide 12: CPS1 Performance

## Slide 13: RMS1 Performance of ERCOT Frequency

## Slide 14: Frequency Profile Analysis

## Slide 15: Time Error Corrections
There were no Time Error Corrections (TEC) in May
Notes: TEC occurred on 12/03/2016 at 23:30. Time Error was 30.06

## Slide 16: ERCOT Total Energy

## Slide 17: ERCOT Total Energy from Wind Generation

## Slide 18: ERCOT % Energy from Wind Generation

## Slide 19
Questions?