## Slide 1
Fast Frequency Response
A Discussion On NPRR 828
19 July 2017 ERCOT Staff

## Slide 2
Discussion Outline
What is Fast Frequency Response (FFR)?
Who can provide FFR?
What are the benefits of having FFR?
What limitations will be applied on FFR?
What can be expected from FFR providers during normal & EEA conditions?

## Slide 3: What is Fast Frequency Response (FFR)?
  Fast Frequency Response (FFR)
  The automatic self-deployment and provision by a Resource of their full response within 30 cycles after frequency meets or drops below a preset threshold or via an ERCOT Verbal Dispatch Instruction (VDI). FFR includes Resources capable of automatically self-deploying and providing their full Ancillary Service Resource Responsibility within 30 cycles after frequency meets or drops below a preset threshold and sustaining a full response for at least 15 minutes. Once recalled, Resources providing FFR must restore their full RRS Ancillary Service Resource Responsibility within 15 minutes after cessation of deployment or as otherwise directed by ERCOT.

## Slide 4: Fast Frequency Response (FFR)
support frequency at 59.7 Hz.
will support frequency at 59.85 Hz* or higher.
Load Resource providing RRS
Resource providing FFR
Chart: Frequency at C-point (Hz)
| 59.7760009765625 | 59.877998352050781
2014 | 769.8328 | 581.5331
2017 | 731.2414 | 403.978 | 795.95 | 446.8429 | 429.204 | 823.344 | 374.7891 | 811.4357 | 727.4601 | 303.979 | 297.52 | 343.702 | 559.7545 | 368.5517 | 380.79 | 487 | 437.923 | 299.2148 | 189.7881 | 339.88 | 416.1594 | 447.9333 | 214.6429 | 638.3 | 588.8618 | 452.4579 | 471.6444 | 444 | 442.7623 | 847.9143 | 522.1853 | 550.4657
LR Trigger | 0
FFR Trigger Op 1 | 0
FFR Trigger Op 2 | 0
*This will be used to identify text in this deck that is different from NPRR 828 and is captured in the draft comment.

## Slide 5: Fast Frequency Response (FFR)
respond in 30 cycles, as well.
will automatically provide full response in 30 cycles after frequency is at/below frequency threshold.
  30 cycles includes delay time of under-frequency relay and breaker operation time.
Load Resource providing RRS
Resource providing FFR

## Slide 6: Fast Frequency Response (FFR)
sustain response till deployment is recalled.
will sustain full response for 15 minutes* or till ERCOT recalls deployment, whichever occurs first.
Load Resource providing RRS
Resource providing FFR
Chart: Frequency Recovery Time (sec)
| 1.7245370327145793E-3 | 2.8009259258396924E-3
2014 | 769.8328 | 581.5331
2017 | 731.2414 | 403.978 | 795.95 | 446.8429 | 429.204 | 823.344 | 374.7891 | 811.4357 | 727.4601 | 303.979 | 297.52 | 343.702 | 559.7545 | 368.5517 | 380.79 | 487 | 437.923 | 299.2148 | 189.7881 | 339.88 | 416.1594 | 447.9333 | 214.6429 | 638.3 | 588.8618 | 452.4579 | 471.6444 | 444 | 442.7623 | 847.9143 | 522.1853 | 550.4657
FFR Response Time | 0
8min Threshold | 0

## Slide 7: Recovery Times – Historic Trend
Time @A | Delta (Hz) | Tripped Resource #1 | Tripped Resource #2 | Calculated MW Loss | Hz at A | Hz at C | Hz at B | Total Recovery Time
7/21/2016 14:53 | 0.1173 | XYX-1 |  | 703 | 59.968 | 59.879 | 59.897 | 0:08:32
7/30/2016 16:39 | 0.0672 | XYZ-2 | XYZ-3 | 393 | 59.995 | 59.927 | 59.947 | 0:09:08
9/18/2016 12:00 | 0.0722 | XYZ-4 |  | 437 | 60.016 | 59.923 | 59.944 | 0:09:50
9/19/2016 16:23 | 0.0424 | XYZ-5 |  | 419 | 59.978 | 59.922 | 59.947 | 0:08:46
3/15/2017 1:36 | 0.1189 | XYZ-6 |  | 811 | 60.006 | 59.787 | 59.913 | 0:09:53
3/29/2017 19:54 | 0.0797 | XYZ-7 |  | 727 | 59.951 | 59.804 | 59.892 | 0:10:53

## Slide 8: Fast Frequency Response (FFR)
can take up to 3 hours to reset after deployment ends.
will restore and become available for next event within 15 minutes after deployment ends.
  *after deployment ends, may not withdraw energy from the grid till frequency recovers to 60 Hz.
Load Resource providing RRS
Resource providing FFR

## Slide 9: Fast Frequency Response (FFR)
can be deployed similarly during EEAs as well.
  upon such deployment, are obligated to sustain response till the deployment is recalled.
can be deployed via Verbal Dispatch instructions during EEAs.
  upon such deployment, are obligated to sustain response for 15 minutes or till ERCOT recalls deployment, whichever occurs first.
  *after deployment ends, will only be allowed to withdraw enrgy from the grid when the EEA has ended and frequency has recovered above 59.95 Hz.
Load Resource providing RRS
Resource providing FFR

## Slide 10: Who can provide FFR?
Generation Resources & Load Resources may provide FFR upto tested capability.
FFR Qualification
  ERCOT will qualify resources that can provide FFR via qualifications tests.
  Passing metric for the test will be,
      Resource’s response must be within 95% and 110% of Min(RRS, MW deployment). (MW deployment = telemetered HSL/MPC – LSL/LPC) AND
      Resource must sustain the response for 15 minutes.
  ERCOT may revoke a resource’s FFR qualification if it has 2 performance failures during actual deployments (manual or frequency triggered) within a rolling 365-day period.
    Resource can requalify for FFR after 6-months. Documentation will be required to identify actions taken to correct performance deficiencies along with the test.
  Storage
  Loads with shorter down-time

## Slide 11: FFR Performance Evaluations
FFR Performance Evaluations
  For any FFR deployment event, ERCOT will collect one or more of the following data:
    High speed event data from Resources that are not deployed via breaker action;
    High speed event data from recorders at ERCOT’s primary and back-up facilities;
    High speed event data from phasor measurement units available to ERCOT; and
    Telemetry data for all Resources providing FFR during the event; and
    Recording of ERCOT Frequency (Hz) and MW output with a resolution of no less than 32 samples* per second.
  Following metric will be used for evaluating response
    Resource deployed in 30 cycles after frequency reached trip threshold (or 10 minutes for manual deployment via VDI), AND
    Resource sustained the response for at least 15 minutes or till ERCOT recalls deployment, whichever occurs first, AND
    Resource was reset and made available for next event within 15 minutes after deployment ended.

## Slide 12: What are the benefits of having FFR?
Early response from FFR will aid in preserving Load Resource providing RRS for more severe events.
  With 59.85 Hz or higher frequency trigger, FFR will deploy more often than Load Resources in response to frequency events;
  With Resources providing fast response, most frequency events will not trigger Load Resources deployment.
  Thus preserving frequency response capabilities from Load Resources to be available for (the next) severe event.
Short restoration time for resources providing FFR will limit ERCOT’s exposure (i.e. inability to respond) to next event of similar magnitude.
  Upon recall of deployment, Resources providing FFR will reset and become available to respond to another event within 15 minutes.
  If a frequency event triggers deployment of RRS from Load Resources, for a 3 hour duration following such an event, ERCOT may not have adequate frequency responsive resources to respond to a large trip (~2700 MW trip).
    This is because Load Resources providing RRS after a deployment have 3 hours to reset and become available to respond to another event.

## Slide 13: What are the benefits of having FFR?
With the appropriately selected trip settings, FFR can help mitigate Critical Inertia and facilitate further increased penetration levels of renewables in ERCOT.
Chart: Critical Inertia
| 10-cycle FFR | 15-cycle FFR | 20-cycle FFR | 30-cycle FFR | No FFR
 | 86 | 88 | 90 | 90 | 90
Under 100 GW*s Inertia condition, 30-cycle / 20-cycle FFR is only able to slow down frequency decay by 6 ms / 8 ms before UFLS set-point (59.3Hz) being reached. Therefore, its impact on mitigating critical inertia is minimum compared to faster FFR services (10/15-cycle FFR).

## Slide 14: FFR (59.85 Hz) Limit* Determination
Chart: Case1 Inertia:100 GW*s 1150 MW PFR, 59.85 Hz & 30 cycles FFR

## Slide 15: Operational Expectations – Normal
During “normal”, non-EEA conditions, Resource providing FFR
  will automatically deploy when frequency reaches or drops below 59.85 Hz* (or a higher threshold) and provide full response within 30 cycles
    30 cycle includes delay time of under-frequency relay and breaker operation time.
  will sustain response for 15 minutes* or till ERCOT recalls deployment, whichever occurs first.
  will restore full A/S responsibility within 15 minutes after deployment ends.
    *after deployment ends, may not withdraw energy from the grid till frequency recovers to 60 Hz.

## Slide 16: Operational Expectations – EEA
During EEA conditions, Resource providing FFR
  may be deployed through Verbal Dispatch Instruction (VDI).
  will provide full response within 10 minutes of receiving VDI.
  will sustain response for 15 minutes* or till ERCOT recalls deployment, whichever occurs first.
  will restore full A/S responsibility within 15 minutes following cancellation of an EEA.
    *after deployment ends, may only withdraw energy from the grid when the EEA has ended and frequency has recovered above 59.95 Hz.

## Slide 17
Divider Slide
Divider Slide (optional)
Discussion