## Slide 1
Review of UFLS Draft NOGRR from UFLS Workshops
Matt Mereness
Director of Compliance
August 17, 2017

## Slide 2: UFLS Discussion outline
Recap of 3 UFLS Workshops
Review current draft NOGRR
Appendix
  NERC requirement excerpt
  UFLS examples
  Potential Load Resource data to provide

## Slide 3: Recap- Background on UFLS Survey Requirement
ERCOT Compliance coordinates and conducts an annual survey with the TSPs and DSPs to ensure that the required automatic under-frequency load shed circuits are configured to provide the appropriate load relief in an under-frequency event as required by table below from Operating Guides 2.6.1(1) Requirements for Under-Frequency Load Shedding:
2016 results were 7.2% / 12.2% / 12.6% for total of 31.9%
2017 results were 7.8% / 13.2% / 13.2% for total of 34.1%

## Slide 4: Recap- Current Issues with UFLS (why being discussed)
ERCOT Compliance was asked at OWG in 2016 about clarifying the assumptions for measurement of UFLS in the survey, as well as emerging operational concerns.
For reference:
NERC Requirements reflect Planning Coordinator shall have a “UFLS program design”
  See Appendix for NERC details
Operating Guide 2.6.1 is the design of ERCOT Automatic Load Shedding
  In effect since zonal Operating Guides in 2010
Issues:
For the survey just reviewed, current OpGuide language reflects the approach of “At least 25% of the ERCOT System Load that is not equipped with high-set under-frequency relays shall be equipped at all times with provisions for automatic under-frequency load shedding.”
  Survey data collected does not identify or align circuits with Load Resources for exclusion
There has also been some “double-counting” discussions over whether Load Resources that deploy at 59.7 Hz can be counted towards the UFLS response at 59.3Hz

## Slide 5: Recap- Summary of 3 UFLS workshops
Key discussions to date
  Recognize there are at least two scenarios of UFLS being activated
    Sudden event: normal day but then significant loss of generation (starting point of 60Hz and no LR deployed)
    Slow-burn event: system is in emergency operations (EEA2), LR deployed, and then loss of generation
    Conclusion that in both cases, need for 25% of armed UFLS to arrest frequency
  ERCOT view that as frequency drops from 60 to 59.7 to 59.3, that the measurement of 25% response is tied to what the Load was when crossing 59.3 and initiating UFLS levels.
  Agreement that annual Compliance survey measurement should align as closely as possible with expected Operations compliance (post event reports and analysis).
  ERCOT was requested to create initial NOGRR draft reflecting expectations
  ERCOT was requested to provide inventory of LRs in DSP footprint
    ERCOT noted this is in network model but can also be provided
  ERCOT asked about providing historical trends/deployments
    ERCOT offered to provide annually if market can agree how to summarize (min, max, avg, annual, etc)
  ERCOT asked about providing Load Resource telemetry to TO/DSPs
  Is DSP or TO the appropriate role/definition for compliance in the NOGRR?

## Slide 6: Goals for this discussion
Today is review of current NOGRR
  Review and confirm key aspects of current draft NOGRR (ERCOT, Workshop, STEC)
    In actual event, compliance with system Load measured at 59.3 Hz (2.6.1(1)).
    In annual survey, compliance with system Load at survey time (2.6.1(2)).
    Due to different scenarios in an actual event, compliance with annual survey does not ensure TO/DSP compliance in actual event
    NOGRR adds ERCOT requirement to annually provide registered Load Resources and capacity in TO/DSP footprint
  Potentially more work needed OWG
    Alignment of DSP and TO responsibilities
    Consideration to help TO/DSP manage risk around Load Resource impact to UFLS
      NOGRR does not currently provide trends of Load Resource status in TO/DSP footprint (eg, min, max, avg responsibility) – could be added with no project impacts to add
      NOGRR does not include telemetry of LR status to TO/DSP – project impacts

## Slide 7
APPENDIX:
NERC requirement excerpt
Potential Load Resource data to provide

## Slide 8: Appendix- NERC Requirement
NERC standard PRC-006-2 — Automatic Underfrequency Load Shedding:
Requirement 9. Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. [VRF: High][Time Horizon: Long-term Planning]
Measurement 9. Each UFLS Entity shall have dated evidence such as spreadsheets summarizing feeder load armed with UFLS relays, spreadsheets with UFLS relay settings, or other dated documentation that it provided automatic tripping of load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, per Requirement R9.

## Slide 9: Potential Load Resource data to be provided
TDSP shown on Registration Form
  TDSP Duns
From the Load Resource Asset Registration Form
  Dispatch Asset Code
  ESIID (Load Resources for NOIEs will have a non-settlement ESIID)
  Station the Load Resource is mapped to in the Network Operations Model
  PTI Number
  Transmission Transformer Load Name
  Maximum Registered Interruptible Load
Historical Data (more analysis needed)
  Average hourly RRS Responsibility for LR during a predefined date range
  Maximum RRS Responsibility during the same time period