## Slide 1
Freeport Area Master Plan Project -
ERCOT Independent Review Update
August 22, 2017

## Slide 2: Overview
CenterPoint submitted Freeport Masterplan Project for Regional Planning Group review. This is a Tier 1 project that is estimated to cost $246.7 million.
  Proposed for 2019 – 2021 timeframe
  To serve new committed loads
  Reliability Issues
    Severe low voltages
    Overloads
    Difficulty of maintenance outage scheduling
  Provide Operational Flexibility

## Slide 3: Study Assumptions
Steady-State Study Case
Constructed from latest 17RTP reliability cases 2019, 2020 and 2022 summer peak EC base cases (2017 June MIS posting)
Study Region will consist of Coast Weather Zone with focus on Freeport Area
Transmission Projects expected to be in-service within the study region by 2019, 2020 and 2022 at the time of the study were added to the cases
    PH Robinson 800 MVA autotransformer addition
RTP reliability projects in the study region that are not approved were backed out
    Freeport ‘Bridge the Gap Upgrades’; Bailey to Jones Creek 345 kV double circuits
Total Freeport Area Load (Industrial + Distribution) modeled in the study cases are
*Based on the in-service date of Oct 1st, 2019 Cortez and Levee Phase-3 loads (265 MW) are modeled only 2020 and onwards.
YEAR | TOTAL LOAD, IN MW
2019* | 1979
2020 | 2254
2022 | 2275

## Slide 4: Contingencies and Criteria
Initial Steady-State Reliability Analysis
  Contingencies for Study Region
    NERC TPL-001-4 and ERCOT Planning Criteria (http://www.ercot.com/content/wcm/current_guides/53526/04_050115.doc ):
      P0
      P1-1, P1-2, P1-3, P1-4,
      P2-1, P2-2, P2-3 (All EHV only)
      P3-1, P3-2, P3-3, P3-4, G-1+P7 {G-1 worst case only}
      P4-1, P4-2, P4-3, P4-4, P4-5 (All EHV only)
      P5-1, P5-2, P5-3, P5-4, P5-5 (All EHV only)
      P6: X-1 + (P1-1, P1-2, P1-3, P1-4, P7-1) {X-1 is 345 kV Auto outages}
      P7-1
  Criteria:
    Thermal
      Monitor all transmission lines and transformers in study region (excluding GSU and PUNs)
      Use Rate A for Normal Conditions
      Use Rate B for Emergency Conditions
    Voltages
      Monitor all busses 100 kV and above
      0.95 < 1.05 Normal
      0.92 < 1.05 Emergency
      Voltage deviations exceeding 8% on non-radial load busses

## Slide 5: Preliminary Results – 2019 Study Case Violations
Initial Steady State Contingency Analysis -
  DOW 345/138 kV autotransformers overloaded >160% under P6 (2 DOW company XFMRs outage)
  4th DOW autotransformer was added to study cases 2019 and onwards
For all the contingency categories tested, 2019 study case had no additional relevant bus or branch violations

## Slide 6: Preliminary Results – 2020 Study Case Violations
# Unsolved Contingency | Branch Violations | Bus Violations |  | 
 |  | Name | kV | Voltage (PU)
None | None | DOW | 345 | 0.905
 |  | Jones Creek | 345 | 0.908
 |  | DOW Chemical (POI buses) | 138 | 0.872
# Unsolved Contingency | Branch Violations |  |  | Bus Violations
 | Element | kV | Loading (%) | 
None | STP to Jones Creek Ckt 18 | 345 | 102.75 | None
P1, P2-1, P7 -> No Violations
P2-2, P2-3, P4-2, P4-3, P4-4, P4-5, P5 ->
P3 (G-1 + N-1) ->
P6-2 (X-1 + N-1) ->
# Unsolved Contingency | Branch Violations | Bus Violations |  | 
 |  | Name | kV | Voltage (PU)
None | None | DOW Chemical (POI buses) | 138 | 0.895

## Slide 7: Preliminary Results – 2022 Study Case Violations
P1, P2-1, P7 ->
P2-2, P2-3, P4-2, P4-3, P4-4, P4-5, P5 ->
# Unsolved Contingency | Branch Violations | Bus Violations |  | 
 |  | Name | kV | Voltage (PU)
None | None | DOW | 345 | 0.919
 |  | DOW Chemical (POI buses) | 138 | 0.895
Name | kV | Deviations(%)
Jones Creek | 345 | 9.06
Camden | 138 | 8.28
Sintek | 138 | 8.16
Post Contingency Voltage Deviations Above 8% ->
# Unsolved Contingency | Branch Violations |  |  | Bus Violations
 | Element | kV | Loading (%) | 
None | STP to Jones Creek Ckt 18 | 345 | 103.28 | None

## Slide 8: Preliminary Results – 2022 Study Case Violations
# Unsolved Contingency | Branch Violations |  |  | Bus Violations |  | 
 | Element | kV | Loading (%) | Name | kV | Voltage (PU)
2 | Oasis to WA Parish | 345 | 102.59 | DOW | 345 | 0.87
 | Basf to Hofman | 138 | 111.31 | Jones Creek | 345 | 0.871
 |  |  |  | DOW Chemical (POI buses) | 138 | 0.835
P3 (G-1 + N-1) ->
P6-2 (X-1 + N-1) ->
# Unsolved Contingency | Branch Violations | Bus Violations |  | 
 |  | Name | kV | Voltage (PU)
None | None | DOW | 345 | 0.908
 |  | Jones Creek | 345 | 0.911
 |  | DOW Chemical (POI buses) | 138 | 0.865

## Slide 9: Dynamic Analysis
Data:
  LT2023 DWG Flat start data set
  CNP Load model
  Contingencies filtered based on area of study
Case modifications:
  Load changes to match with forecasted increase in signed load for study area (confirmed with CenterPoint)

## Slide 10: Dynamic Analysis
Phase I:
  VSAT analysis with SSWG contingencies + project contingencies submitted by CNP
  P1, P2,P4,P5 and P7
  Filtering based on top limiting contingencies from voltage stability standpoint
  Convert and generate P3, P6 contingencies based on filtered set
Phase II:
  Transient study for events: VSAT analysis + CNP list + SSWG converted contingencies (Study area)
  Monitor bus Transient Voltage Recovery and relay trip events

## Slide 11: Next Steps
  Complete the Steady State and Dynamic Stability Analysis
  Identify and evaluate project alternatives
  Sensitivity Analysis
    Higher Load (potential loads)
    PGRR0042-Generator additions with Signed Interconnection Agreements that DO NOT meet Planning Guide Section 6.9 criteria in study region
  Tentative Timeline
    Final EIR update to RPG – September
    EIR recommendation to TAC – September
    BOD Endorsement – October

## Slide 12
?