## Slide 1
Load Review Process
Sandeep Borkar and Calvin Opheim
August 2017
RPG Meeting

## Slide 2: Agenda
Background
Process overview
Schedule and timeline
Next steps

## Slide 3: Background
PG section 3.1.7 specifies the process used for determining Load level used in start cases for RTP and Tier 1 independent review
SSWG load forecast was compared to ERCOT 90th percentile forecast for all weather zones
Load reviews performed for Coast and Far West weather zone for the 2017 RTP

## Slide 4: Load Forecast Review Process
ERCOT 90th percentile Forecast
SSWG Load Level
5% Bound
ERCOT 90th percentile Forecast
SSWG Load Level
5% Bound
ERCOT 90th percentile Forecast
SSWG Load Level
Justified?
RTP Load Level
RTP Load Level
RTP: Loads compared by weather zone
Tier 1 RPG review: Loads compared by TO (if necessary)

## Slide 5: RTP/Tier 1 Load Level
5% Bound
ERCOT 90th percentile Forecast
SSWG Load Level
5% Bound
ERCOT 90th percentile Forecast
SSWG Load Level
5% Bound
ERCOT 90th percentile Forecast
SSWG Load Level
SSWG Load Level
RTP Load Level
RTP Load Level
RTP Load Level

## Slide 6: Experience from 2017 Load Forecast Review
What evidence is accepted?
Is there a MW cutoff?
Confidentiality
How will the new loads be handled
Fast growing load area concerns?
Anything TOs can do ahead of time to make this easier

## Slide 7: Load Forecast Review Process
Notes: Philippe Petit's amazing World Trade Center - 1974

## Slide 8: Load Forecast Review Process
Comparison of Load Forecasts
  Weather Zone
  TSP
Required documentation to support the TSPs load forecast
Additional review of load delivery points
Example

## Slide 10: Load Forecast Comparison
If Weather Zone SSWG forecast is higher than ERCOT 90th percentile forecast + 5% bound
  TSP can provide signed financially binding agreements from customers as evidence of increased load in their territory
  These agreements are kept confidential by ERCOT

## Slide 11: Load Forecast Comparison
Review TSP SSWG forecast
  If TSP forecast looks significantly larger than the overall growth in a weather zone
  TSP can provide signed financially binding agreements from customers as evidence of increased load in their territory
  These agreements are kept confidential by ERCOT

## Slide 13: Load Forecast Comparison
Review TSP SSWG forecast
High growth but not from large customers
  Supporting documentation of the forecast
  Includes:
    Growth driver
    Forecast model

## Slide 14: Required Documentation
Signed financially binding document is required
  No speculative load is included
  If there is no signed financially binding document, the load is not included

## Slide 15: Review New Load Additions
Compare the load from the financially binding document to its actual load
  If it’s a new load delivery point, the kw listed is added to ERCOT’s forecast
  The kw value is not reduced at this time

## Slide 16: Review New Load Additions
Some documents were dated in the past
  Reviewed the current load level to the load level from historically signed documents time
  Revealed differences between contracted load and actual load

## Slide 17: Review New Load Additions
Example
  Customer signed agreement indicates 100 MW of load effective 1/1/2016
  Current load level is 10 MW
  TSP forecast is 100 MW in 2017

## Slide 18: Review New Load Additions
Example
  Customer signed agreement indicates 100 MW of load effective 1/1/2016
  Current load level is 10 MW
  TSP forecast is 100 MW in 2017
  ERCOT forecast adjustment is 10 MW

## Slide 19: Review New Load Additions
Example continued
  ERCOT’s proposal would be to contact the customer and receive an updated load forecast
  Also shows the difference between contracted load and actual
  ERCOT will be gathering data to quantify actual load versus contracted load

## Slide 20: Conclusion
ERCOT has developed procedures that will be used to review load forecasts
  The goal is to ensure that ERCOT is comfortable with the load forecasts
  ERCOT is appreciative of the support provided by TSPs

## Slide 21: Schedule and Timeline for RTP loads

## Slide 22: Tier 1 related load reviews
Any loads added in addition to those included in RTP cases will require load review
Timeline for this load review will be identified in the RPG Independent Review scope

## Slide 23: Next steps
Seek feedback about proposed changes
Propose that 5% threshold be used per Section 3.1.7 at the following meetings
  September TAC
  October Board

## Slide 24: Questions
Sandeep Borkar
Sandeep.Borkar@ercot.com
512-248-6642
Calvin Opheim
Calvin.Opheim@ercot.com
512-248-3944

## Slide 25
Appendix

## Slide 26: Bounded higher-of methodology (Conceptual)

## Slide 27: Load review process (Conceptual)
Rationale:
Historic load growth
Committed load additions
Forecast methodology
Past forecast performance
Special circumstances
Other?
Preliminary RTP start cases will be shared to allow TDSPs to review the impact of load distribution on pockets within the weather zones.

## Slide 28: Planning Guide 3.17 Reference
[PGRR042: Insert Section 3.1.7 below on January 1, 2018:]
3.1.7 Steady State Transmission Planning Load Forecast
(1) ERCOT shall use the following process for determining the Load level to be used in the starting base cases for the Regional Transmission Plan and in the steady-state evaluation of a Tier 1 project pursuant to Protocol Section 3.11.4, Regional Planning Group Project Review Process:
(a) ERCOT will compare the ERCOT 90/10 Load forecast with the summed SSWG bus-level Load forecast for each Weather Zone.
(b) If the ERCOT 90/10 Load forecast is higher, ERCOT will use this forecast for the Weather Zone.
(c) If the SSWG Load forecast is higher than or equal to the ERCOT 90/10 Load forecast, but below the ERCOT 90/10 Load forecast plus a boundary threshold determined in accordance with paragraph (f) below, ERCOT will use the SSWG Load forecast for the Weather Zone.
(d) If the SSWG Load forecast is higher than or equal to the ERCOT 90/10 Load forecast plus the boundary threshold, ERCOT will use the ERCOT 90/10 Load forecast plus the boundary threshold for the Weather Zone.

## Slide 29: Planning Guide 3.17 Reference (Cont.)
(e) If a TSP(s) believes that the ERCOT 90/10 Load forecast plus the boundary threshold does not adequately represent the Weather Zone or an area within the Weather Zone, the TSP(s) may present ERCOT with additional information to justify using a higher Load forecast, including the SSWG Load forecast, for that Weather Zone. ERCOT, in its sole discretion, may choose to use a higher Load forecast than indicated in paragraph (d) above if it reasonably determines that the Load forecast indicated in paragraph (d) above does not adequately represent the Weather Zone or an area within the Weather Zone. If ERCOT uses a Load forecast higher than the ERCOT 90/10 Load forecast plus the boundary threshold in the evaluation of a Tier 1 project, ERCOT must explain and document the basis for that choice, using aggregated information as needed to shield Protected Information, in its independent review.
(f) ERCOT-proposed revisions to the boundary threshold used to implement the requirements of this section will be recommended by the Technical Advisory Committee (TAC) and approved by the ERCOT Board.