## Slide 1
ERCOT UFLS Survey
2017 Results
Daniel Sanchez
Compliance Analyst

## Slide 2: Background on the ERCOT UFLS Survey and Requirements
ERCOT coordinated and conducted the survey on May 11, 2017 with TSPs and DSPs. The survey serves to ensure that the required automatic under-frequency load shed circuits are configured to provide the appropriate load relief in an under-frequency event. The table below, taken from the ERCOT Operating Guide 2.6.1(1) Requirements for Under-Frequency Load Shedding, lists the required load shed amounts:
Operating Guide 2.6.1 (2)
With the assistance of applicable Transmission Service Providers (TSPs), ERCOT will, prior to the peak each year, survey each Distribution Service Provider’s (DSP’s) compliance with the automatic Load shedding steps above, and report its findings to the Technical Advisory Committee (TAC). For minimum compliance, DSPs are obligated to meet the prescribed percent values at all times.
Frequency Threshold | Load Relief
59.3 Hz. | 5% of the ERCOT System Load (Total 5%)
58.9 Hz. | An additional 10% of the ERCOT System Load (Total 15%)
58.5 Hz. | An additional 10% of the ERCOT System Load (Total 25%)

## Slide 3: Timeline of the ERCOT UFLS Survey
Below is a list of dates and activities reflecting the timeline and coordination of this survey:
Date | Activity
Wednesday, March 29th | ERCOT announcement of survey timeline to the OWG.
Tuesday, April 4th | Market Notice sent by ERCOT Client Services to TSP/DSP Authorized Representatives.
Thursday, May 11th at 11:00 | Date and time of survey.
Thursday, June 15th | Survey results due to ERCOT.
June 28th | Survey results to be reported to the OWG.
August 3rd | Survey results to be reported to the ROS.
August 24th | Survey results to be reported to the TAC.

## Slide 4: Results of the ERCOT 2017 UFLS Survey
The overall results of the 2017 UFLS survey were successful and are reflected below:
The total ERCOT load at the time of the survey was 42,510 MW.
Only one participant failed to meet the requirement in one block (by less than one percent), however they did exceed the total minimum requirement. They are in the process of swapping a circuit from one block to another which will then satisfy requirement for the block response.
In comparison, the 2016 survey overall total was 31.9%.
Frequency Response Block | Minimum Requirement | Survey Measurement
Block 1 response at 59.3 Hz. | 5% | 7.8%
Block 2 response at 58.9 Hz. | 10% | 13.2%
Block 3 response at 58.5 Hz. | 10% | 13.2%
Total | 25% | 34.1%