## Slide 1
Analysis of the Impact of 4-CP Transmission Charges on Real Time Prices
Carl L Raish
Principal Load Profiling and Modeling
WMS – September 6, 2017

## Slide 2: How 4-CP Works
‘BUSIDRRQ’ customers ≥ 700 kW or served at transmission (69 kV) voltage are subject to 4-CP charges.
  Simple average of the metered load during ERCOT system monthly peak 15-minute intervals in four summer months -- June, July, August & September.
  Multiplied by the applicable prevailing TDSP Tariff, as approved by PUC.
  Is the basis for the monthly 4-CP-based rates for the following calendar year.
Analysis for this report addressed 4-CP in both the competitive and NOIE areas of ERCOT.
The analysis used settlement system interval data
  For ESIIDs in competitive ERCOT areas with ‘BUSIDRRQ’ profile types.
  Calculated interval data of the native load in NOIE areas … NOIE area boundary metered imports plus generation located inside the NOIE area

## Slide 3: Analysis Objective
Test quantification of 4-CP impact on real-time prices by:
Remove estimated amount of 4-CP response (adding it back to ERCOT load); and,
Estimate revised system lambda, taking price response from load and distributed generation into consideration.
Issues with generator behavioral response

## Slide 4: Analysis Methodology
Select 4-CP and Near-CP days in 2015 and 2016.
  8 4-CP days
  11 Near-CP days in 2015 and 14 Near-CP days in 2016
  Use intervals 48 – 96 for each of the 33 days (1,584 intervals)
Calculate revised system lambda with GTBD increased by the 4-CP response amount in each SCED interval
Develop ERCOT-level price response model for load and distributed generation
  Competitive area load using annual survey
  Load of NOIEs identified as responding to price
  Exports from distributed generators that respond to price
4. Iteratively:
  Calculate price response MW based on revised system lambda
  Modify GTBD based on price response
  Calculate revised system lambda at the modified GTBD
  Continue iterating until the point (GTBD adjusted for price response, revised system lambda) matches a point on the aggregated energy offer curve

## Slide 5: Competitive Load on 4 CP Days - 2016
CP Reduce = 436
CP Reduce = 626
CP Reduce = 452
CP Reduce = 577
Load reductions for ESIIDs that respond to 4-CP
Reductions start around noon and continue to midnight

## Slide 6: NOIE 4 Load on CP Days - 2016
CP Reduce = 440
CP Reduce = 783
CP Reduce = 481
CP Reduce = 552
Load reductions for NOIEs that respond to 4-CP
Reductions start around noon and continue to midnight

## Slide 7: Competitive + NOIE Response 2009 - 2016

## Slide 8: Max 4-CP/NearCP Reductions - Hour Ending 17:00
Slope = 21
Slope = 2
Slope = 88

## Slide 9: Growth of ESIIDs and NOIEs with 4-CP Response
Slope = 10

## Slide 10: Max CP/NearCP Reductions - Hour Ending 17:00
Slope = 2
Postage Stamp Transmission Rates
2002-2017
Currently $52.91
Postage Stamp rate for Transmission Cost of Service has more than tripled since 2002
>$7B in Competitive Renewable Energy Zone (CREZ) transmission investment
  $4.9B of CREZ activated in 2013 alone
>$2B in projects activated in 2016
Source: PUCT Dockets
The postage stamp rate (per 4-CP kW) is charged to DSPs, who in turn reimburse TSPs for their transmission investments

## Slide 11: System Lambda
SCED System Lambda λ
  The cost of providing one additional MWh of energy at the load electrical buses. Essentially the load weighted average marginal price for energy across nodes
Aggregate Energy Offer Curve
  Identify online generators
  Identify SCED energy offer curves for each
  Identify LASL and HASL for each
  Aggregate the SCED energy offer curves between LASL and HASL across the generators
Caveats
  This approach does not
  consider generator ramp rates, constraint changes, market behavior changes

## Slide 12: Preliminary Impact of 4-CP Back-cast on RT Prices
Final system lambda > $200 & Δ system lambda > $50
2015 - 3 days and 19 intervals
2016 - 7 days and 40 intervals
This approach does not consider generator ramp rates, constraint changes, market behavior changes.

## Slide 13: Back-cast Impact of 4-CP on Real Time Prices
Final system lambda <= $200 | Δ system lambda <= $50
2015 - 15 days and 701 intervals
2016 - 18 days and 824 intervals
This approach does not consider generator ramp rates, constraint changes, market behavior changes.

## Slide 14: Quantifying ERCOT level Price Response
ERCOT has conducted an annual survey of REPs to identify ESIIDs on several categories of demand/price response programs.
ERCOT has used the survey data to quantify the frequency and magnitude of response in competitive areas
ERCOT has used NOIE load as calculated from boundary meters to identify NOIEs the respond to price and has quantified the frequency and magnitude of that response.
ERCOT has used export data from distributed generators to identify those that respond to price and has quantified the frequency and magnitude of that response.

## Slide 15: Competitive Price Response Survey Results
 | 2015 MW | 2016 MW | ESIIDs Deployed 2015 | ESIIDs Deployed 2016 | ESIIDs Not Deployed 2015 | ESIIDs Not Deployed 2016
4-CP | 1,321 | 1,409 | 1,800 | 1,700 | 9,500 | 9,700
BI | 200 | 157 | 9,000 | 13,000 | - | -
OLC | 7 | 4 | 12,000 | 2,000 | 3,000 | 7,000
OTH | - | 15 | - | 34,000 | - | 34,000
PR | 30 | 28 | 45,000 | 79,000 | 452,000 | 435,000
RTP | 11 | 1 | 5,000 | 10,000 | - | -
TOU | - | - | 322,000 | 331,000 | - | -

## Slide 16: Load Price Response
Competitive Loads
  Use the 2015 and 2016 REP survey submissions to identify ESIIDs on Real Time Pricing and Block and Index Pricing.
  Quantify load reductions by load zone on high price days (at least 4 consecutive intervals with prices >= $200)
  Estimate regression model of load reduction as a function of price at the load zone level
NOIE Loads
  Quantify load reductions by NOIE on high price days (at least 4 consecutive intervals with prices >= $200) and classify as price responsive based on frequency and magnitude of response
  Estimate regression model of load reduction as a function of price at the load zone level
  Calculate aggregate model

## Slide 17: Distributed Generator Price Response
Registered Distributed Generators
  Selected generators being paid Load Zone prices for exports
  Eliminated any with primary fuel of sun, wind or other
  Does include exports from PUNs with generators that are not Generation Resources
Unregistered Distributed Generators
  Selected ESIIDs with DG profile type (exports are settled as negative energy)
  Eliminated Distributed Renewable Generators (PV and WND profile types)
Quantify Price Response
  Followed baseline methodology used for loads to quantify export increases on high price days (at least 4 consecutive intervals with prices >= $200)
  Classified generators as price responsive based on frequency and magnitude of response (47 of 109, name plate MW 428.9)
  Estimate regression model of export increase as a function of load zone price
  Create aggregate model

## Slide 18: Distributed Generator Baseline Examples

## Slide 19: Interaction of 4-CP and Price Response
Removal of 4-CP response would tend to increase prices
Price increases would trigger increased price response
Find the point on the aggregated offer curve where system lambda for the GTBD adjusted for price volume of price response is consistent with the price response modeled as a function of system lambda.
Limited analysis to days identified with significant changes to system lambda when adding 4-CP response.

## Slide 20: Adjust System Lambda for Price Response
Aggregate Energy Offer Curve
Actual
($75, 66,776.4 MW)

## Slide 21: Adjust System Lambda for Price Response
Increase GTBD by 1,020 MW of 4-CP Reduction
($6,991, 67,796.2 MW)

## Slide 22: Adjust System Lambda for Price Response
Lower GTBD by 408 MW of Price Response
($197, 67,388.2 MW)

## Slide 23: Adjust System Lambda for Price Response
Converges at 188 MW of Price Response
($725, 67,608.5 MW)

## Slide 24: Back-cast Impact of 4-CP on Real Time Prices
Accounting for anticipated DR/DG price response
2015 - 3 days and 19 intervals
This approach does not consider generator ramp rates, constraint changes, market behavior changes.
2016 - 7 days and 40 intervals

## Slide 25: Behavioral Issues
4-CP response is hard to predict including both the deployment days and magnitude
Only 10 of the 33 deployment days in 2015 and 2016, disregarding behavioral changes other than price DR and DG price response, could potentially result in significant real time price increases
2009
2010
2011
2012
2013
2014
2015
2016

## Slide 26: Behavioral Issues
Small changes in 4-CP response, disregarding behavioral changes other than price DR and DG price response, can result in significant changes in system lambda
Short term behavioral changes in response to higher prices would be likely to draw historically off-line resources into the market and would put significant and highly variable downward pressure on prices
Long term behavioral changes of all types would be likely and would further increase the downward pressure
2015

## Slide 27: Behavioral Issues (continued)
2016

## Slide 28: Behavioral Issues (continued)
2016 continued

## Slide 29: Observations
Back cast analysis of removing 4-CP load reductions without any other adjustment does show a significant and highly volatile impact on real time prices in 2015 and 2016 for ten days (59 intervals).
4-CP reduction across intervals and across days are highly variable and back cast prices are highly volatile.
The back cast analysis shows small changes on the remaining 23 days … days not likely to trigger DG and DR price response or behavioral changes among Generation Resources.
Considering price response from DG and DR in the back-cast analysis does show reductions in the impact on real time prices, but the volatility of the impact remains high.
On days with significant impacts, Generation Resources would be likely to modify their offer decisions based on the potential for the higher price increases identified above.
The short and long term potential for behavioral changes in DR, DG and Generation Resources clearly exists and likely would be highly variable as well.

## Slide 30: Questions?
ON
OFF
craish@ercot.com 512/248-3876