## Version History (hidden)
Version# | Date comments Provided/Recorded | Description of the Change | Change Type | RARF Location | Requested By | Recorded By | Additional Comments
0.01 | 2008-09-02 | Initial spreadsheet created | General |  | GSU Transformer Tab and Transmission Owned Assets Tab have been pulled out of RARF | Prafulla Nellutla
0.02 | 2008-09-04 | 1. Unit Info-GEN,Unit Info-CC, Unit Info-Wind Tabs: Updated the Data type of 'NERC Number' to 'Character' 2. Site Information Tab: Updated the Business Rules for the following fields :ESI ID,ESI ID 1-6, Competitive Retailer, Competitive Retailer Duns# 3.Sunsync Tab is not being considered for Phase1 | Business Rule Change | Unit Info/Site Information | Updated based on the comments from Angela Moy | Prafulla Nellutla
0.03 | 2008-09-07 | Added a new column 'Source' to capture the source of the Business Rules | General |  | Based on the suggestions from Rick Jones | Prafulla Nellutla
0.04 | 2008-09-09 | 1. Updated Unit Info-Wind Tab: Added Business Rules for Latitude and Longitude values, Type of turbine, MW of Turbine, Number of Turbine 2. Updated the Parameters-Wind Tab --> Hot Start Time, Intermediate Start Time, Cold Start Time are optional for wind resources. | Business Rule Change | Unit Info-Wind/ Parameters-Wind | Updated based on the comments from Angela Moy in Audit Reports meeting | Prafulla Nellutla
0.05 | 2008-09-10 | 1. Planning-Wind, Planning-GEN, Planning-CC: Updated the Basic validation rules based on the RARF Guide/RARF Glossary/RARF Forms 2.Protection-CC, Protection-Wind, Protection-GEN: Updated the Basic validation rules based on the RARF Guide/RARF Glossary/RARF Forms | Business Rule Change | Planning/Protection | Referring to the RARF Guide/RARF Glossary/RARF Forms | Prafulla Nellutla
0.06 | 2008-09-11 | Updated the Source of the Validation Rules | General |  |  | Prafulla Nellutla
0.07 | 2008-09-16 | All the Dropdown list fields are categorized as Business Rules as these business rules are defined in RARF Glossary Version 4.0 | General |  | RARF Glossary Version 4.0 | Prafulla Nellutla
0.08 | 2008-09-17 | Reactive Capability-Gen , Reactive Capability- CC, Reactive Capability-Wind : Updated the Business Rules | Business Rule Change | Reactive Capability | Based on the inputs from WeiHui | Prafulla Nellutla
0.09 | 2008-09-18 | 1. Added New Column "Destination Application" to identify the fields being used by NMMS 2. Reactive Capability-CC: Changed the Field type (if hydrogen cooled ,change the hydrogen pressure) from Required to optional. Alignment of Business Rules with Data fields was not proper in previous version, which has been corrected. | Business Rule Change | Reactive Capability-CC | Based on the inputs from Rick Jones and Angela Moy | Prafulla Nellutla
0.10 | 2008-09-23 | Ownership-CC, Ownership-GEN, Ownership-Wind: Added 'NMMS' as Destination Application | Business Rule Change | Ownership | Based on the inputs from Nitika Mago | Prafulla Nellutla
0.11 | 2008-09-25 | 1.Added Destination Application to the corresponding RARF Field 2.Reactive Capability Tab- Added 2 new Business Rules for NETMAX LEAD and NETMAXLAG fields | Business Rule Change | Reactive Capability | Based on the inputs from Art Deller/Rick Jones/WeiHui | Prafulla Nellutla
0.12 | 2008-10-07 | Updated Business Rules for Reactive Capability-Wind, GEN,CC Tabs | Business Rule Change | Reactive Capability | Based on the comments from Angela Moy | Prafulla Nellutla
0.13 | 2008-10-09 | Load Information Tab: Update Business Rules for LRL and HRL | Business Rule Change | Load Information | Based on the inputs from Scott Middleton | Prafulla Nellutla
0.14 | 2008-10-20 | Parameters-GEN,Parameters-CC,Parameters-CFG,Parameters-WIND Tabs: Added new Business Rules | Business Rule Change | Parameters | Based on the inputs from WeiHui | Prafulla Nellutla
0.15 | 2008-10-20 | Load Information Tab: Update Business Rule for ERCOT Load Zone field. Changed the Data type to Character. | Business Rule Change | Load Information | Based on the inputs from Angela Moy | Prafulla Nellutla
0.16 | 2008-10-24 | Load Information Tab: Removed the following fields 1. Notice Requirements to Interrupt 2.Name of End Use Customer Site Information Tab: Update the Business Rules for TDSP DUNS# and TDSP Providing Service to Resource(TDSP Name) | Business Rule Change | Load Information/Site Information | Based on the inputs from Angela Moy | Prafulla Nellutla
0.17 | 2008-10-24 | Parameters-CC Tab: Business rules for HRRL,LRRL should not be checked if the Primary Fuel Type in Parameters-CC Tab is 'STM'. | Business Rule Change | Parameters-CC | Based on the inputs from Scott Middleton | Prafulla Nellutla
0.18 | 2008-10-24 | Operational Parameters-CFG,GEN,Wind Tabs: Updated Business Rules for the following fields : Minimum online time, Minimum offline time, Hot start time, cold start time, max daily stars, Intermediate start time, Max Weekly Stars, Hot-to-Intermediate Time, Intermediate-to-cold time, Max online time, MW1 Site Information Tab: updated business rule for the following fields: Resource site name, Resource site code General Information Tab: update business rule for 'Resource Entity Duns#' Unit Info-GEN: Updated business rule for ' Resource Name' CC1-Config and CC1-Transitions: updated business rules | Business Rule Change | Operational Parameters/Site Information/General Information/Unit Info-GEN | Based on the inputs from Jamil Daouk | Prafulla Nellutla
0.19 | 2008-10-24 | CC1 Config, CC2 Config,CC3 Config, CC1 Transitions Tab: Updated the business rules | Business Rule Change | Configurations/Transitions | Based on the inputs from Jamil Daouk | Prafulla Nellutla
0.20 | 2008-10-30 | Unit Info-GEN, CC,Wind Tabs: Updated the business rule for 'ERCOT Interconnection Project Number-New Units only' Operational Parameters-CFG,GEN,Wind Tabs: Updated the business rules for 'Max Daily Starts' and 'Max Weekly Starts' Site-Information Tab: Updated the data type of ESI ID 1-6 as 'character' | Business Rule Change | Unit Info/Site Information/Operational Parameters | Based on the inputs from Angela Moy and Jamil Daouk | Prafulla Nellutla
0.21 | 2008-10-30 | CC1 Transitions Tab: Updated the business rule for Operational Configurations (Test_CC1_X to Test_CC1_X) | Business Rule Change | CC1 Transitions | Based on the inputs from Jamil Daouk | Prafulla Nellutla
0.22 | 2008-10-31 | General Information Tab: Fax# is made optional field. | Business Rule Change | General Information | Based on the inputs from Scott Middleton | Prafulla Nellutla
0.23 | 2008-11-05 | CC1,CC2,CC3 Transitions Tabs: updated the business rule | Business Rule Change | CC1,CC2,CC3Transitions | Based on the inputs from Scott Middleton | Prafulla Nellutla
0.24 | 2008-11-07 | Site Information Tab: Changed the data type of ESI ID to 'character' | Business Rule Change | Site Information | Based on the input from Buddy Bur | Prafulla Nellutla
0.25 | 2008-11-10 | Load Resource Information: changed the data type of the field 'ESI ID assigned to meter' to character | Business Rule Change | Load Resource Information | Based on the inputs from Angela Moy | Prafulla Nellutla
0.26 | 2008-11-11 | Load Resource Information: Updated the business rule for LRL | Business Rule Change | Load Resource Information | Based on the inputs from Angela Moy | Prafulla Nellutla
0.27 | 11/11//2008 | Ownership-GEN, Ownership-Wind: Updated the business rule for Fixed Ownership% | Business Rule Change | Ownership | Based on the inputs from Art Deller | Prafulla Nellutla
0.28 | 2008-11-13 | Load Resource Information: Updated the business rule for the field 'Load Resource Control Device' | Business Rule Change | Load Resource Information | Based on the inputs from Angela Moy | Prafulla Nellutla
0.29 | 2008-12-03 | Parameter-Gen,cc,cfg,wind Tabs: Updated the business rules for HRL,LRL,HRRRL,LRRRL Load Resource Information Tab: Updated the business rules for CLR HRRRL,CLR LRRRL | Business Rule Change | Parameters/ Load Resource Information | Based on the inputs from Jamil Daouk | Prafulla Nellutla
0.30 | 2009-01-28 | Correct >= signs on Continuous Rating, 2Hr, 15min to reflect Continuous Rating <= 2Hr <= 15min | Business rule change | Line Data tab | Weihui Fu | Scott Middleton
0.30 | 2009-01-28 | Change Low Tap Settings - Total Number of Tap Positions to >=2 | Business rule change | Transformer Data tab | Weihui Fu | Scott Middleton
0.30 | 2009-01-28 | Change High Tap Settings - Total Number of Tap Positions >= 2 | Business rule change | Transformer Data tab | Weihui Fu | Scott Middleton
0.30 | 2009-01-28 | Change all naming conventions (such as Line Name, Device Name, etc) to include a dash '-' as an acceptable special character | Business rule change | Line Data tab | Joel Koepke Joe Weatherly | Scott Middleton
0.30 | 2009-01-28 | Add Line Voltage must be <=345kV | Business rule change | Line Data tab | Joel Koepke Joe Weatherly John Adams | Scott Middleton
0.30 | 2009-01-28 | Remove TSP from the TO STATION Block and the ERCOT Station Code Mnemonic label | RARF Format / Label Change | Line Data tab | Joel Koepke Joe Weatherly John Adams | Scott Middleton
0.30 | 2009-01-28 | Move the TSP Name to the TO STATION block, make conditionally required based on new field Internal Line: Y/N and create a entry for each Line provided | RARF Format / Label Change Business Rule Change | Line Data tab | Joel Koepke Joe Weatherly John Adams | Scott Middleton
0.30 | 2009-01-28 | Each TO STATION - TSP Name field should contain a drop down list of valid TSP's | RARF Format / Label Change | Line Data tab | Angie Moy | Scott Middleton
0.30 | 2009-01-28 | Change TO STATION - PTI BUS NUMBER to be optional if Internal Line: Y/N = 'Y' | Business Rule Change | Line Data tab | Joel Koepke Joe Weatherly John Adams | Scott Middleton
0.30 | 2009-01-28 | Change "Connected Switching Device Name(s)" to read "Connected Device Name(s)" on both, the TO STATION block and the FROM STATION Block | RARF Format / Label Change | Line Data tab | Joel Koepke | Scott Middleton
0.30 | 2009-01-28 | Change FROM STATION - PTI BUS Number to be optional Include a warning if left blank | Business Rule Change | Line Data tab | Joel Koepke Joe Weatherly | Scott Middleton
0.30 | 2009-01-28 | Change Type (overhead / underground) to include 'BOTH' as a valid option | Business Rule Change | Line Data tab | Joel Koepke Joe Weatherly | Scott Middleton
0.30 | 2009-01-28 | Segment Length - Joel to provide additional business rule. | Business Rule Change | Line Data tab | Joel Koepke Joe Weatherly John Adams | Scott Middleton
0.31 | 2009-02-02 | Need somewhere in the RARF an identifier of the RARF version so a person is able to identify an out of date RARF | RARF Format / Label Change | General | Joe Weatherly | Scott Middleton
0.31 | 2009-02-02 | For all equipment, anywhere a Station reference is being requested as in the “Breaker Switch Data” for entry “ERCOT Station Code Mnemonic” a business rule of “2) Must match ERCOT records”, If the RARF is being filled out for a new substation, how can this rule be satisfied? Added "(unless new)" to each of these rules. | Business Rule Change | All tabs where applicable | Joe Weatherly | Scott Middleton
0.31 | 2009-02-02 | For all equipment, anywhere there is a name of the equipment as in the “Breaker Switch Data” business rule of 3) Must be <=14 characters, TAC050406-Naming_Convention.doc says “shall have the first 14 characters unique within the Transmission Element type within all of ERCOT”. I don’t know if this TAC rule is still in effect, and I don’t know what limit you would have in NMMS to keep an equipment name. | Business Rule Change | Line Data tab | Joe Weatherly | Scott Middleton
0.31 | 2009-02-02 | Need to remove field “Operating Status Requested for Model Entry” exists. This is for a prior to Approval to Energize status, which is not applicable under NODAL. If the “Start date” is too early for the generator or any other equipment not in service, the Resource can manage any needed switch states by the outage scheduler. | Business Rule Change RARF Format / Label Change | Line Data tab | Joe Weatherly | Scott Middleton
0.31 | 2009-02-02 | For all equipment, need to know what to do if more than 10 devices exist (are additional rows expected to be inserted, or only list the first 10?) on “Directly connected device name(s)”. In previous conversations with Joel K. it was thought that 5 - 10 devices would be enough to locate it. | Business Rule Change RARF Format / Label Change | All tabs where applicable | Joe Weatherly | Scott Middleton
0.31 | 2009-02-02 | Missing “Will this station will have or has a transmission level Voltage reading?” / “If yes, between this switch and what other switches does the Voltage telemetry exist (only need to list once per kV telemetry)” and have same business rule of “Voltage Level”. This is a slight change from an older RARF that asked erroneously which PTI bus# has the voltage. | Business Rule Change RARF Format / Label Change | Line Data tab | Joe Weatherly | Scott Middleton
0.31 | 2009-02-02 | For all equipment, a PTI bus number is desired, but not mandatory (at this point in time). Change all PTI Bus Numbers to Optional? Does this also apply to a line that goes to a TSP owned asset? | Business Rule Change | All tabs where applicable | Joe Weatherly | Scott Middleton
0.31 | 2009-02-02 | For “Line Data”, remove “Station Weather Zone / Station ID” from the “To Station” & “FROM Station”. This would be more meaningful if it were CSC zone ID (ERCOT map posted). | RARF Format / Label Change | Line Data tab | Joe Weatherly | Scott Middleton
0.31 | 2009-02-02 | For “Line Data”, possibly remove “Type (overhead / underground / both)” was in old SRs, but never utilized in Operations… don’t think any other department requires this information; possibly could be used in sanity checks. | RARF Format / Label Change | Line Data tab | Joe Weatherly | Scott Middleton
0.31 | 2009-02-02 | “Transformer Data” has comments that are longer than box shown, need to extend comment box size but cannot. | RARF Format / Label Change | Transformer Data tab | Joe Weatherly | Scott Middleton
0.31 | 2009-02-02 | “Transformer Data” needs comment that a single 3-winding transformer is to be modeled as three 2-winding transformers with a common 1kV neutral. 1kV neutral is not considered as LOW side designation. 1kV does not contain connecting devices. No PTI bus# needed for the 1kV neutral. ClarifiedChange to Be Noted in entry on 2/6/09 | Business Rule Change RARF Format / Label Change | Transformer Data tab | Joe Weatherly | Scott Middleton
0.31 | 2009-02-02 | “Transformer Data” needs to identify the manufactured “Nominal kV” done previously by SRs requesting Voltage at Center of Tap Range & Tap position at Center of Tap Range. This would be required data even if no Taps exist. Side note: This identifies transformers that were not manufactured with the utility standard Base kV, but that can obtain the Base kV by being set at a different Normal Tap position. | Business Rule Change RARF Format / Label Change | Transformer Data tab | Joe Weatherly | Scott Middleton
0.31 | 2009-02-02 | “Transformer Data” does not need “Voltage at Normal Tap Position”… this is nice for checks, but not used as input into the EMS. | Business Rule Change RARF Format / Label Change | Transformer Data tab | Joe Weatherly | Scott Middleton
0.31 | 2009-02-02 | “Transformer Data” remove field “Charging Susceptance (100 MVA Base)” because the EMS automatically calculates this value. | Business Rule Change RARF Format / Label Change | Transformer Data tab | Joe Weatherly | Scott Middleton
0.31 | 2009-02-02 | “Transformer Data” needs “Comments” | Business Rule Change RARF Format / Label Change | Transformer Data tab | Joe Weatherly | Scott Middleton
0.31 | 2009-02-02 | Possibly too hard to create for “Transformer Data”: would like to add Business Rule to provide WARNING that if the summation of name plate MVA ratings of Generator(s) associated is greater than the Continuous MVA rating ot this step-up transformer. | Business Rule Change | Transformer Data tab | Joe Weatherly | Scott Middleton
0.31 | 2009-02-02 | “Series Device Data” need to move cells to make Resistance & Reactance close together | RARF Format / Label Change | Transformer Data tab | Joe Weatherly | Scott Middleton
0.31 | 2009-02-02 | “One Line”, embedding document(s) of drawing files in AutoCAD or PDF appreciated since screen shots loose resolution. | RARF Format / Label Change | Transformer Data tab | Joe Weatherly | Scott Middleton
0.31 | 2009-02-02 | Need Resources to provide a Methodology on how their circuits are rated. This should fall under the RARF as a General Information checklist that a separate document has been submitted to ERCOT. Definitely don’t want the Resource to attach the file every time a RARF is updated. | Business Rule Change RARF Format / Label Change | Transformer Data tab | Joe Weatherly | Scott Middleton
0.31 | 2009-02-02 | the Transformer Name was not listed correctly. It should be <=14 characters & '_' and '-' are only special characters allowed. | Business Rule Change | Transformer Data tab | Angie Moy | Scott Middleton
0.31 | 2009-02-02 | ERCOT Station Name: Are any special characters allowed? Eg: _ or - | Business Rule Change | General | Angie Moy | Scott Middleton
0.31 | 2009-02-02 | Unit(s) associated with this transformer: This field is pre-populated in a pull down menu from the Unit tabs. Why would it be a warning and not an error if they list a different unit code? | Business Rule Change | Transformer Data tab | Angie Moy | Scott Middleton
0.34 | 2009-02-05 | Formula on Line Data - Segment Length: The formula to determine the length of a line based on the Resistance (R) and the Charging Susceptance (Chg) is 486 * SQRT(R_pu * Chg_pu) 25% variation This is a warning | Business Rule Change | Line Data tab | Joel Koepke | Scott Middleton
0.33 | 2009-02-04 | Add boundary conditions to Reactance, Resistance and Charging Susceptance (see table provided by J. Koepke | Business Rule Change | Line Data tab | Joel Koepke | Scott Middleton
0.36 | 2009-02-10 | Missing all validation for Line Data - FROM STATION - ERCOT Station Code Mnemonic | Business Rule Change | Line Data tab | Angie Moy | Scott Middleton
0.36 | 2009-02-10 | Missing rule on Capacitor and Reactor Data - ERCOT Station Code Mnemonic: Must match ERCOT records (unless new) | Business Rule Change | Capacitor and Reactor Data | Scott Middleton | Scott Middleton
0.35 | 2009-02-06 | Change all instances referring to High Side / Low Side to correctly read "High Side" and "Low Side" not just high/low | RARF Format / Label Change | Transformer Data tab | Joel Koepke Joe Weatherly | Scott Middleton
0.35 | 2009-02-06 | Added Column and business rules for High Side Manufactured Nominal Voltage | Business Rule Change RARF Format / Label Change | Transformer Data tab | Joel Koepke Joe Weatherly | Scott Middleton
0.35 | 2009-02-06 | Add Fields and business rules: 1) Master Name (can be same as this transformer) 2) Follower Name (can be same as this transformer) | Business Rule Change RARF Format / Label Change | Transformer Data tab | Joel Koepke Joe Weatherly | Scott Middleton
0.35 | 2009-02-06 | Add field and business rules for High Side Voltage Connection - Wye or Delta | Business Rule Change RARF Format / Label Change | Transformer Data tab | Joel Koepke Joe Weatherly | Scott Middleton
0.35 | 2009-02-06 | Add rule to all Low Tap Setting to reflect they should be blank if Low Side Voltage Level = 1kV | Business Rule Change | Transformer Data tab | Joel Koepke Joe Weatherly | Scott Middleton
0.35 | 2009-02-06 | Remove fields (from high / low tap settings sections): 1) Low Tap Settings - Voltage at Normal Tap Position 2) High Tap Settings - Voltage at Normal Tap Position | Business Rule Change RARF Format / Label Change | Transformer Data tab | Joel Koepke Joe Weatherly | Scott Middleton
0.35 | 2009-02-06 | Add Fields and business rules (to high / low tap settings section): 1) Low Tap Settings - Tap position at Manufactured Nominal Voltage 2) High Tap Settings - Tap position at Manufactured Nominal Voltage | Business Rule Change RARF Format / Label Change | Transformer Data tab | Joel Koepke Joe Weatherly | Scott Middleton
0.34 | 2009-02-05 | change label of "TO STATION - Station Weather Zone / Station ID" to read "TO STATION - Weather Zone / Weather Station (used for Dynamic Ratings)" | RARF Format / Label Change | Line Data tab | Joel Koepke Joe Weatherly | Scott Middleton
0.36 | 2009-02-10 | Modify business rules for TO STATION - Weather Zone / Weather Station (used for Dynamic Ratings) to reflect: 1) This field is conditionally required if "Line Rating (Static or Dynamic)" = 'DYNAMIC' (this field was previously required) | Business Rule Change | Line Data tab | Joel Koepke Joe Weatherly | Scott Middleton
0.36 | 2009-02-10 | Spelling error corrected | RARF Format / Label Change | Static Var Compensator | Scott Middleton | Scott Middleton
0.37 | 2009-02-11 | Corrected business rule for Static Var Compensator - SVC Name - this field is now required | Business Rule Change | Static Var Compensator | Matthew Boyda | Scott Middleton
0.37 | 2009-02-11 | Corrected Static Var Compensator - SVC Base Voltage Level | Business Rule Change | Static Var Compensator | Matthew Boyda | Scott Middleton
0.38 | 2009-02-16 | Change the order of Net Maximum Leading Operating Capability and Net Maximum Lagging Operating Capability Remove the "NET" identified from both labels. | RARF Format / Label Change | Reactive Capability | Joe Weatherly | Scott Middleton
0.40 | 2009-02-18 | Added business rules for 1) Low Tap Settings – Step Voltage Level 2) High Tap Settings – Step Voltage Level 3) High Tap Settings – Voltage at Lowest Tap Position | Business Rule Change | Transformer Data tab | Joel Koepke Khoi Nguyen | Scott Middleton
0.39 | 2008-02-17 | Add the following tabs and business rules: 1) Load Data tab 2) Pun Load Tab | Business Rule Change RARF Format / Label Change | Load Data tab Pun Load Tab | Several | Scott Middleton
0.41 | 2009-02-19 | Corrected grammatical error on Line Data - Reactance and Line Data Resistance | RARF Format / Label Change | Line Data tab | Khoi Nguyen | Scott Middleton
0.41 | 2009-02-19 | Changed Load HRL / LRL business rules such that they are now positive numbers per protocols | Business Rule Change | Load Resource Information | NPRR | Scott Middleton
0.31 | 2009-02-02 | Corrected "Minimum Threshold (post contingency) Reactive Power Limits" business rule to read "2) Value must be <= Maximum Threshold (post contingency) Reactive Power Limits" | Business Rule Change | Static Var Compensator | Angie Moy | Scott Middleton
0.31 | 2009-02-02 | Corrected "Minimum Voltage Threshold (100 MVA Base)" business rule to read "2) Value must be <= Maximum Voltage Threshold (100 MVA Base)" | Business Rule Change | Static Var Compensator | Angie Moy | Scott Middleton
0.31 | 2009-02-02 | Removed the following business rule: "3) This field is conditionally required if Automatic Voltage Regulation = 'Y'" from the Maximum Voltage Threshold (100 MVA Base) field. This field is now required. | Business Rule Change | Static Var Compensator | Angie Moy | Scott Middleton
0.31 | 2009-02-02 | Removed the following business rule: "3) This field is conditionally required if Automatic Voltage Regulation = 'Y'" from the Minimum Voltage Threshold (100 MVA Base) field. This field is now required. | Business Rule Change | Static Var Compensator | Angie Moy / Joel Koepke | Scott Middleton
0.32 | 2009-02-03 | Corrected Transformer Ratings to reflect the following: Continuous Rating: 1) This field is required 2) Value must be <= 2-hr Emergency Rating 3) Value must be <= 15-min Rating 2-hr Emergency Rating 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be <= 15-min Rating 15-min Rating 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be >= 2-hr Emergency Rating | Business Rule Change | Transformer Data tab | Angie Moy Joel Koepke | Scott Middleton
0.32 | 2009-02-03 | Corrected Series Device Ratings to reflect the following: Continuous Rating: 1) This field is required 2) Value must be <= 2-hr Emergency Rating 3) Value must be <= 15-min Rating 2-hr Emergency Rating 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be <= 15-min Rating 15-min Rating 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be >= 2-hr Emergency Rating | Business Rule Change | Transformer Data tab | Angie Moy Joel Koepke | Scott Middleton
0.32 | 2009-02-03 | Add rule: "This tab is conditionally required if Private Network - Private Network? = 'Y'" | Business Rule Change | Line Data tab | Joel Koepke | Scott Middleton
0.32 | 2009-02-03 | Add rule: "This tab is required" | Business Rule Change | Breaker and Switch Data Tab | Joel Koepke | Scott Middleton
0.32 | 2009-02-03 | Add rule: "This tab is conditionally required if Private Network - Private Network? = 'Y'" | Business Rule Change | Load Data | Joel Koepke | Scott Middleton
0.32 | 2009-02-03 | Add rule: "This tab is conditionally required if Private Network - Private Network? = 'Y'" | Business Rule Change | Transformer Data tab | Joel Koepke | Scott Middleton
0.33 | 2009-02-04 | Changed Connected Devices on all tabs to reflect a character limitation of <= 17. Fields that were modified: Line Data - TO STATION - Connected Device Name(s) (multiple) Line Data - FROM STATION - Connected Device Name(s) (multiple) Breaker and Switch Data - Side 1 / Side 2 - Directly connected device name(s) Capacitor and Reactor Data - Switching Device Name(s) - that this reactive device is directly connected to Transformer Data - Unit(s) associated with this transformer Transformer Data - Low Side Voltage Connected device(s) (list on separate lines) Transformer Data - High Side Voltage Connected devices (list on separate lines Static Var Compensator - Device Name(s) - that this reactive device is directly connected to Series Device Data - Side 1 - Connected Switching Device Name(s) Series Device Data - Side 2 - Connected Switching Device Name(s) Load Data - Device Name(s) - that this load is physically connected to | Business Rule Change | All tabs where applicable | Angie Moy | Scott Middleton
0.33 | 2009-02-04 | Added missing business rule for TO STATION - Internal Line | Business Rule Change | Line Data tab | Scott Middleton | Scott Middleton
0.34 | 2009-02-05 | Remove Business Rule for "Voltage Level Of Load Tap Changer" as it was removed from the RARF. | Business Rule Change | Transformer Data tab | Scott Middleton | Scott Middleton
0.42 | 2009-03-09 | Changed business rule for high / low side manufactured voltage to reflect the following: 2) If value > 60kV Accepted if value (using 5%) Deviates < ¦3.45¦ kV from 69 Deviates < ¦6.9¦ kV from 138 Deviates < ¦17.25¦ kV from 345 Warn if value (using >= 5% and <10%) Deviates > = ¦3.45¦ but deviates < ¦6.9¦ from 69 Deviates >= ¦6.9¦ but deviates < 13.8 from 138 Deviates >= ¦17.25¦ but deviates < 34.5 from 345 Error if value (using > =10%) Deviates >= ¦6.9¦ kV from 69 Deviates >= ¦13.8¦kV from 138 Deviates >= ¦34.5¦kV from 345 3) Warn if value > 345 | Business Rule Change | Transformer Data tab | Joe Weatherly | Scott Middleton
0.42 | 2009-03-09 | Change Label of "Location of Tap Changer" to read "Location of Load Tap Changer" | RARF Format / Label Change | Transformer Data tab | Joe Weatherly | Scott Middleton
0.42 | 2009-03-09 | Added warning for connected devices in the following scenario: "High side voltage level < 60kV and Low side voltage level = 1kV, then warn if no connected devices" | Business Rule Change | Transformer Data tab | Joe Weatherly | Scott Middleton
0.42 | 2009-03-09 | Change RARF form to not accept decimals (or display them) on PTI Bus Number fields (note that the database import did not include decimals). | RARF Format / Label Change | All tabs where applicable | Joe Weatherly | Scott Middleton
0.42 | 2009-03-09 | Added rule to reactance as follows: warn if value exceeds 1.0. Error! Reactance (value) > 1.0. Reactance should be expressed in terms of per unit (e.g. not percentage). | Business Rule Change | Transformer Data tab | Ed Geer | Scott Middleton
0.42 | 2009-03-09 | Added warning to reactance as follows: warn if value exceeds 1.0. Error! Reactance (value) > 1.0. Reactance should be expressed in terms of per unit (e.g. not percentage). | Business Rule Change | Transformer Data tab | Matthew Boyda | Scott Middleton
0.42 | 2009-03-09 | Removed "Second Condition: This field may be left blank if Low Voltage Level = 1" from High Tap Settings - Tap position at Manufactured Nominal Voltage | Business Rule Change | Transformer Data tab | Matthew Boyda | Scott Middleton
0.42 | 2009-03-09 | Modify Step Voltage label to read "Size of each Voltage Level Step" | RARF Format / Label Change | Transformer Data tab | Joe Weatherly | Scott Middleton
0.42 | 2009-03-09 | Modify Step Voltage (now "Size of each Voltage Level Step") to accept 10 decimal places. | RARF Format / Label Change | Transformer Data tab | Joe Weatherly | Scott Middleton
0.43 | 2009-03-10 | Modify Step Voltage label to read "Size of each Voltage Step" | RARF Format / Label Change | Transformer Data tab | Joe Weatherly Joel Koepke | Scott Middleton
0.43 | 2009-03-10 | Modified all Low / High tap settings to reflect the following rule: This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap | Business Rule Change | Transformer Data tab | Joe Weatherly Joel Koepke | Scott Middleton
0.43 | 2009-03-10 | Modified Low Side Voltage Level (no-load) business rule to reflect the following: If Generator Step-up Transformer = 'Y' AND Low Side Voltage Level (no-load) > 1kV THEN the Low Side Voltage Level (no-load) must be equal to Unit Info - GEN / CC / WIND - Unit Generating Voltage | Business Rule Change | Transformer Data tab | Joe Weatherly | Scott Middleton
0.43 | 2009-03-10 | Modified Business Rule for "High Tap Settings – Size of each Voltage Step" to reflect the following: Warn if < 0.002 *High Side Voltage Level (no-load) Warn if > 0.05 * High Side Voltage Level (no-load) | Business Rule Change | Transformer Data tab | Joe Weatherly | Scott Middleton
0.43 | 2009-03-10 | Modified Business Rule for "Low Tap Settings – Size of each Voltage Step" to reflect the following: Warn if < 0.002 *Low Side Voltage Level (no-load) Warn if > 0.05 * Low Side Voltage Level (no-load) | Business Rule Change | Transformer Data tab | Joe Weatherly | Scott Middleton
0.43 | 2009-03-26 | Updated the version history [Included the change log of Transmission Asset Business Rules (version 0.30 to 0.43)] | General | Business Rules Spread SS | Prafulla Nellutla | Prafulla Nellutla
0.44 | 2009-03-30 | Removed the condition that if something is a private use network, we require the line data to be filled out. | Business Rule Change | Line Data tab | Scott Middleton | Prafulla Nellutla
0.45 | 2009-03-31 | Modified the business rule to display an Error if Reactance value is > 1. Error! Reactance (value) > 1.0. Reactance should be expressed in terms of per unit (e.g. not percentage). | Business Rule Change | Transformer/Series Device/Line Data | Scott Middleton | Prafulla Nellutla
0.46 | 2009-04-01 | Added a business rule for the Wind sites that If the Unit Info-Wind tab shows multiple groups of turbines in a Unit, then the Reactive Curve tab must have the values for the corresponding multiple groups, Produce an error if the corresponding data is missing in the Reactive Capability-Wind Tab for those groups. | New Business Rule | Reactive-Capability-Wind and Unit-Info Wind | Angela Moy | Prafulla Nellutla
0.47 | 2009-04-06 | Updated Business Rules for Resource Category. Added 'Other', 'Wind Generation' to the list. Corrected Diesel to 'Reciprocating Engine' | Business Rule Change | Unit-Info Tabs | SIR#12198,NPRR159 | Prafulla Nellutla
0.48 | 2009-04-21 | Updated the Business Rules for Non-CLR Parameters Section & Fields: This Section is conditional: Required {if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | Business Rule Update | Load Resource Parameters | Scott Middleton | Prafulla Nellutla
0.49 | 2009-04-24 | Updated Business Rule for Tap position at Manufacturer Voltage | Business Rule Update | Transformer Data tab | Joe Weatherly | Prafulla Nellutla
0.5 | 2009-04-27 | Updated the Business Rules for MW and MVAR Value as: It should be >0 and generate a warning if = 0 | Business Rule Update | Load Data tab | Scott Middleton | Prafulla Nellutla
0.51 | 2009-04-29 | Updated the Business Rule for High Set Under frequency Relay Setting | Business Rule Update | Load Resource Information | Steve Krein | Prafulla Nellutla
0.52 | 2009-04-29 | HRL >= Both Summer Interruptible MW and Winter Interruptible MW Rating. High Reasonability Limit >=HSL or MPC.Low Reasonability Limit <= LSL or LPC | Business Rule Update | Load Resource Information | Steve Krein | Prafulla Nellutla
0.53 | 2009-05-05 | Site Code is validated against the existing records in ERCOT and an error should be generated when the site code submitted do not match with the existing records in ERCOT. | Business Rule Update | Site Information | Angela Moy | Prafulla Nellutla
0.54 | 2009-05-07 | Master Owner is Required Field and Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | Business Rule Update | Site Information | Angela Moy | Prafulla Nellutla
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Changed Data type to float for "What is the MVA base that the following data is based on?" | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Changed Data Type to float for "What is the kV base that the following data is based on?" | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Changed Data Type to float for "Machine Impedance Zeq (R+jX) - R" | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Changed Data Type to float for "Machine Impedance Zeq (R+jX) - X" | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Changed Data type to float for "Positive Sequence Z (R in p.u)" and added the following rule: 2) Value must be between 0 and 1 | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Changed Data type to float for "Positive Sequence Z ( X in p.u)" and added the following rule: 2) Value must be between 0 and 100 | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Changed Data type to float for "Negative Sequence Z ( X in p.u)" and added the following business rule: 2) Value must be between 0 and 1 | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Changed Data type to float for "Negative Sequence Z ( X in p.u) and added the following rule: 2) Value must be between 0 and 100 | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Changed Data type to float for "Zero Sequence Z ( X in p.u)" and added the following business rule: 2) Value must be between 0 and 1 | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Changed Data type to float for "Zero Sequence Z ( X in p.u)" and added the following rule: 2) Value must be between 0 and 100 | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Average Amount of Auxiliary Real Power: Changed data type to float Added the following business rules: 2) Value must be < Parameters - GEN - High Reasonability Limit 3) Warn if value > (High Reasonability Limit) * .75 4) Error if value > (High Reasonability Limit) * .66 | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Average Amount of Auxiliary Reactive Power: Changed data type to float Added the following business rules: 2) Value must be < Reactive Capability - GEN - Maximum Lagging Operating Capability (MVAR) 3) Warn if value > ( Maximum Lagging Operating Capability) * .75 4) Error if value > ( Maximum Lagging Operating Capability) * .66 | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Generator Form on file with ERCOT?: Added business rule: 1) This field is required | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Turbine-Governor Form on file with ERCOT?: Added business rule: 1) This field is required | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Excitation Form on file with ERCOT? : Added business rule: 1) This field is required | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Do you have a Power System Stabilizer?: Added business rule: 1) This field is required | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Do you have a Compensator? : Added business rule: 1) This field is required | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Do you have a Over Excitation Limiter?: Added business rule: 1) This field is required | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Do you have a Under Excitation Limiter?: Added business rule: 1) This field is required | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Direct Axis Sub transient reactance, X"di: Changed data type to float | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN,CC, WIND Tabs Direct Axis Transient reactance, X'di: Changed data type to float | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN, CC, WIND tabs Changed data types for all values except "Data type should be Integer" to float | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-04-21 | Note: change made for GEN, CC, WIND tabs Added business rule for all Time 1,2,3 as follows: 2) Time 1 < Time 2 < Time 3 (time points must increment) | Business Rule Update | Planning | Doug Evans | Scott Middleton
0.55 | 2009-05-18 | Business Rules for State , Zip code fields are updated | Business Rule Update | Site Information | Prafulla Nellutla/Angie Moy | Prafulla Nellutla
0.56 | 2009-05-18 | If the Internal Line Flag is 'Y', then the TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic can be same. If the internal Line Flag is 'N', TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic should be distinct | Business Rule Update | Line Data tab | Angela Moy/Khoi | Prafulla Nellutla
0.57 | 2009-05-20 | Removed RARF Data Fields as per RARF_V0.4 version for planning-GEN,Planning-Wind,Planning-cc tabs | Business Rule Update | Planning-GEN | Angela Moy | Prafulla Nellutla
0.58 | 2009-05-22 | MVA Base,KV Base values should be expressed as per unit values | Business Rule Update | Planning-GEN,CC,Wnd | Raja Kakarla | Prafulla Nellutla
0.59 | 2009-05-27 | 1.Low Reasonability Limit >= 0 for Non-PUN Sites. 3. For Pun Sites (If Private Network Flag = 'Y' in the Private Network Tab) then LRL should be equal to zero. Generate a WARNING If LRL is not equal to zero for PUN Sites | Business Rule Update | Parameters-GEN,CC,CFG | Kenneth Ragsdale | Prafulla Nellutla
0.60 | 2009-05-27 | Updated the Business Rules as mentioned below. 1)Instantaneous is optional 2) Each set should have at a minimum of 1 stage (TIME 1 = required) 3)TIME2, TIME3, TIME4 are optional 4)They may only fill in a stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage | Business Rule Update | Protection-GEN,CC,Wind | Raja Kakarla | Prafulla Nellutla
0.60 | 2009-05-28 | The under-frequency settings cannot be below 57.5 Hz and over-frequency settings cannot be above 62.5 Hz. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero | Business Rule Update | Protection-GEN,CC,Wind | Raja Kakarla | Prafulla Nellutla
0.61 | 2009-05-29 | New Business Rule#3 for Direct Axis Sub transient reactance, X"di,Direct Axis Transient reactance, X'di,Positive Sequence Z (saturated) R & X in p.u, Negative Sequence Z (saturated) R & X in p.u, Zero Sequence Z (saturated) R & X in p.u | New Business Rule | Planning-GEN,CC,Wnd | Ed Geer | Prafulla Nellutla
0.62 | 2009-06-03 | Time setting is dependent on frequency setting, cannot have time setting with out frequency setting. At least 1 protection settings is required.( Under voltage 1 is required, Under voltage 2,3,4 are optional,) Overvoltage 1 is required, Overvoltage 2,3,4 are optional,) Over Frequency 1 is required, Over frequency 2,3,4 are optional,) Under frequency 1 is required, Under frequency 2,3,4 are optional, Time1 is required, Time2,3,4 are optional) | New Business Rule | Protection-GEN,CC,Wind | Raja Kakarla | Prafulla Nellutla
0.63 | 2009-06-03 | If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined | New Business Rule | Protection-GEN,CC,Wind | Raja Kakarla | Prafulla Nellutla
0.64 | 2009-06-04 | Updated Rule#1 for Protection-GEN,CC Tabs that • Time1 is CONDITIONAL, not required if Instantaneous setting are defined. This is applicable for Plant Voltage Protection Section.• Time 1 CONDITIONAL, not required if Instantaneous setting are defined ,is only required if they have time delayed under or over frequency settings. This is applicable for Plant Frequency Protection Section | New Business Rule | Protection-GEN,CC,WIND | Raja Kakarla | Prafulla Nellutla
0.65 | 2009-06-08 | UnderVoltage1,OverVoltage1,Underfreq1,Overfreq1 is CONDITIONAL, Not required(optional) if Instantaneous setting is defined | New Business Rule | Protection-GEN,CC,WIND | Raja Kakarla | Prafulla Nellutla
0.66 | 2009-06-09 | Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab(frequency settings refer to under/over freq settings) “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab (voltage settings refer to time delayed under/voltage settings) | New Business Rule | Protection-GEN,CC,WIND | Raja Kakarla | Prafulla Nellutla
0.67 | 2009-06-09 | Removed Rule#3 for MVA Base and KV Base Fields | Business Rule Update | Planning-GEN,CC,Wnd | Scott Middleton | Prafulla Nellutla
0.67 | 2009-06-10 | Nominal MVAR should be >0 from Capacitor and < 0 for Reactor | Business Rule Update | Capacitor and Reactor Data | Angie Moy | Prafulla Nellutla
0.68 | 2009-06-22 | Added the Business Rule: Protection Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR | Business Rule Update | Protection-GEN,CC,Wind | Raja Kakarla/Jose | Prafulla Nellutla
0.68 | 2009-06-22 | Removed the Business Rule: The under-frequency settings cannot be below 57.5 Hz and over-frequency settings cannot be above 62.5 Hz | Removed the Rule | Protection-GEN,CC,Wind | Raja Kakarla/Jose | Prafulla Nellutla
0.69 | 2009-06-23 | 3) Generate a Warning if MVABASE > 2500 4)[ If MVABASE value is within +/- 25% range of Unit Name Plate Rating] OR [MVABASE value = 100, then it is OK.If MVABASE value is outside the +/- 25% range of Unit Name Plate Rating, then Generate a Warning that the MVABSE is outside the typical +/- 25% variation of unit name plate rating | New Business Rule | Planning-GEN,CC,Wnd | Ed Geer/Raja Kakarla | Prafulla Nellutla
0.69 | 2009-06-23 | 3) Generate a Warning if KVBASE > 40 4) If KVBASE value is within +/- 25% range of Unit KV value in the unit-information tab then it is OK.If If KVBASE value is outside the typical +/- 25% variation of Unit KV value in the unit-information tab then Generate a Warning that the KVBASE is outside the typical +/- 25% variation of Unit KV value | New Business Rule | Planning-GEN,CC,Wnd | Ed Geer/Raja Kakarla | Prafulla Nellutla
0.7 | 2009-06-24 | Generate a Warning when Total Number of Tap positions >=16 and Automatic Voltage Regulation ='N'. Generate a Warning when Total Number of Tap positions >=16 and Load Tap Changer ='N'. | New Business Rule | Transformer | Joe Weatherly | Prafulla Nellutla
0.7 | 2009-06-24 | Generate a warning when Total Number of Tap positions is <16 and Automatic Voltage Regulation ='Y'. | Removed the Rule | Transformer | Joe Weatherly | Prafulla Nellutla
0.8 | 2009-06-29 | MW1 >=0, MW2,MW3,MW4,MW5 >0 | New Business Rule | Reactive Capability-CC,GEN,WIND | Angela Moy | Prafulla Nellutla
0.9 | 2009-06-30 | Update the existing Warning Message for Segment Length Field to include the text '' This is applicable for Overhead lines only" | New Business Rule | Line Data tab | Joe Weatherly | Prafulla Nellutla
0.91 | 2009-07-17 | Change the error to Warning for Zero Sequence Impedance field when it is > 1.0 p.u | Business Rule Update | Planning-GEN,CC,Wnd | Ed Geer | Prafulla Nellutla
0.92 | 2009-07-17 | There are several instances where RE's notified us that they do not have automatic under/over voltage protection or under/over frequency protection. Updated the existing errors for protection settings to warnings. (Currently, we generate errors for stage1 settings when instantaneous is blank and stage1 settings are not filled in) Condition->We should generate a warning when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. This is to let the MP know that they may want to enter the Stage1 protection settings as they did not provided instantaneous values. They may ignore this warning if they do not have automatic protection trip Ex: If stage 1 settings (undervoltage1,time1) are blank and undervoltage2,3,4 are blank with instantaneous under voltage trip value blank ,warning should be : Undervoltage1 : Warning! Undervoltage1 is blank and the under voltage protection settings do not exist and instantaneous value is blank' Time1: Warning! Time1 is blank and the under voltage protection settings do not exist and instantaneous value is blank'. This is applicable for overvoltage/over frequency/under frequency protection settings | Business Rule Update | Protection-GEN,CC,Wind | Scott Middleton | Prafulla Nellutla
0.93 | 2009-07-17 | It is noticed that the protection voltage settings(instantaneous, under/over voltage) values are entered in volts rather than p.u value. And there was an instance when all the voltages entered as zeros. There is a need to include a boundary condition on all the voltage settings as : Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | New Business Rule | Protection-GEN,CC,Wind | Raja/Angie/Scott/Ed | Prafulla Nellutla
0.94 | 2009-07-17 | Rule updated for Line Name: The order of validations should be :The error that Line Name must not contain special characters should appear first preceded by the Warning that triggers when Line name is > 14 characters long. Update the Warning Message as : Warning! ERCOT Line Name () should not be > 14 characters long or the name will be truncated in the model which requires uniqueness. | Business Rule Update | Line Data tab | Joe Weatherly/Angie Moy | Prafulla Nellutla
0.95 | 2009-07-17 | We had few instances where incorrect Resource Category is entered for GEN(Non-CC,Non-Wind) units and the Audit report did not generate an error as the rules are Generic to all Resources. There is a need to update the validation for Resource Category List to include the specific list for each Resource Type: GEN,CC,Wind. Allowed values for Resource Category field are: Unit-Info-Wind : ‘Wind Generation Resource’. Unit-Info-CC : ‘Combined Cycle >90 MW* , Combined Cycle <=90MW*’. Unit-Info-GEN : Nuclear,Hydro,Coal and Lignite, Gas Steam- Super Critical Boiler, Gas Steam- Reheat Boiler, Gas Steam - Non Reheat or Boiler without air preheated, Simple Cycle <= 90 MW, Simple Cycle > 90 MW, Reciprocating Engine, Other. | Business Rule Update | Unit-Info-GEN/Unit-Info-CC,Unit-Info-Wind | Prafulla Nellutla | Prafulla Nellutla
0.96 | 2009-07-17 | Average Amount Of Real Power/ Average Amount Of Reactive Power should be 'Required' Fields for Planning-CC. When the MW/MVAR values are zero, the % values are not required(No error for GEN Aux Load% fields when ME /MVAR values are zeros) | Business Rule Update | Planning-CC | Raja/Samantha Garza | Prafulla Nellutla
0.97 | 2009-07-21 | Update the existing Warning messages for the Equipment Character length limits (line names, device names, transformer names, station codes/names etc) in all the transmission data tabs. Line Data: Updated Warning message for the fields: ERCOT Line Name, ERCOT Station Code Mnemonic Connected Devices: Transformer Data: Updated the Warning message for the fields :Transformer Name, Master Name and Follower Name fields, ERCOT Station Code Mnemonic: Capacitor Reactor Data: Updated the Warning message for the fields :ERCOT Station Code Mnemonic, Device Name, Device Name(s) - that this reactive device is directly connected to: Load Data: Updated the Warning message for Switch Name and ERCOT Station Code Mnemonic fields. Static Var Compensator Data: Updated the Warning message for the fields: Device Name, Station Name, SVC Name Series Device Data: Updated the Warning message for the fields: Series Device Name, Station Name, Device Names Breaker Switch Data: Updated the Warning message for the fields: Switch Name, Station Name, Device Name | Business Rule Update | Line, Transformer, Series Device, Capacitor Reactor, Breaker Switch, Load, Static Var Compensator | Joe Weatherly/Angie Moy | Prafulla Nellutla
0.97 | 2009-07-21 | Change the existing error message to Warning ,which is generated when Over Frequency value is >65 Hz. | Business Rule Update | Protection-GEN,CC,Wind | Scott Middleton | Prafulla Nellutla
0.98 | 2009-07-22 | Make all warnings for planning and protection data instead of error messages. | Business Rule Update | Planning/Protection | Raja Kakarla | Prafulla Nellutla
0.99 | 2009-07-23 | Resistance If value is < 0.0001 and Internal Line = 'Y' then Error! Resistance is less than 0.0001 the Line data is not required, connected devices need to be modeled on Breaker/Switch tab If value is <0.0001 and Internal Line = N then Warning. 'Warning! Resistance is less than 0.0001' Reactance If value is < 0.0001 and Internal Line = 'Y' then Error! Reactance is less than 0.0001 the Line data is not required, connected devices need to be modeled on Breaker/Switch tab If value is <0.0001 and Internal Line = N then Warning. 'Warning! Reactance is less than 0.0001' | Business Rule Update | Line Data tab | Woody/Ed | Prafulla Nellutla
1.0 | 2009-08-05 | Latitude of center of Wind Farm, Longitude of center of Wind Farm, Latitude of Meteorological Tower, Longitude of Meteorological Tower- Data type must be Float for these fields (Enter Decimal degrees) | Business Rule Update | Unit-Info-Wind | Angie Moy | Prafulla Nellutla
1.0 | 2009-08-05 | Location of Load Tap Changer is conditionally required if 'Does Transformer Have a Load Tap Changer ?' = 'Y' | Business Rule Update | Transformer Data Tab | Joe Weatherly | Prafulla Nellutla
1.0 | 2009-08-05 | 2.Each configuration in CC1 Transitions including Offline can be reached. Each configuration in CC1 Transitions including Offline can reach at least one of the other configurations including Offline . (**This rule is not applicable if the Private Network flag is 'Y' in the Private Network Tab*** REMOVE THIS CONDITION which excludes Private Use Networks from the Business Rule validation) | Business Rule Update | Transitions(CC1,CC2,CC3) | Scott Middleton | Prafulla Nellutla
1.0 | 2009-08-05 | ERCOT Station code Mnemonic(SUBSTATION_CODE) field should not allow any special characters other than underscore and dash. SUBSTATION_CODE should be UPPER CASE | Business Rule Update | Breaker and Switch Data Tab/Transformer Data Tab/Capacitor or Reactor Data Tab/Series Device Data/Load Data Tab | Rick Jones/Angie Moy | Prafulla Nellutla
1.1 | 2009-08-12 | If Line Data - Line Voltage Level = 345kV, Charging Susceptance must be <=2.2. Generate a Warning if rule fails. | Business Rule Update | Line Data Tab | Joe Weatherly | Prafulla Nellutla
1.1 | 2009-08-12 | 1.Series Device Data needs to allow negative Reactance (to represent Series Capacitors) 2. Transformer Data should allow negative Resistance & Reactance only when low side kV is 1kV… | Business Rule Update | Series Device Data, Transformer Data | Joe Weatherly | Prafulla Nellutla
1.1 | 2009-08-12 | Desired, Minimum, and Maximum voltage fields values should be within the range of 20% of the base kV..anything beyond should be a Warning. | Business Rule Update | Capacitor or Reactor | Joe Weatherly | Prafulla Nellutla
1.1 | 2009-08-12 | Update the Error message Text when Internal Line is 'N' and TO/FROM Station Codes are same, Error message should be : 'Error! TO and FROM Station Code ( ) should not be duplicated if Internal Line Flag = "N" ' | Business Rule Update | Line Data tab | Angie Moy | Prafulla Nellutla
1.1 | 2009-08-12 | If the internal Line Flag is 'N', ,FROM Station Code Mnemonic cannot be listed as a TO Station Code Mnemonic on any other lines. The Warning would occur on the secondary side (eg: they had DIESEL on the FROM station on the first line, and DIESEL on the TO Station on the second line then the TO station would produce the Warning) or (eg: DIESEL is on the TO station on the 3rd line and DIESEL on the FROM station on the 4th line then the FROM station would produce the Warning). | Business Rule Update | Line Data tab | Angie Moy | Prafulla Nellutla
1.1 | 2009-08-12 | Resistance: If value is < 0.0001 and Internal Line = 'Y' then Warning! Resistance should be less than 0.0001 If value is < 0.0001 and Internal Line = 'N' then Warning! Resistance should be less than 0.0001 Reactance: If value is < 0.0001 and Internal Line = 'Y' then Warning! Reactance should be less than 0.0001 If value is < 0.0001 and Internal Line = 'N' then Warning! Reactance should be less than 0.0001 | Business Rule Update | Line Data tab
1.1 | 2009-08-12 | 1. 1.If a RARF is submitted that does not have the first Transition from OFFLINE, Generate an ERROR. 2. Generate a Warning if the Transitions skip. For instance the transitions table has ‘Offline’ to ‘CC1_2’ and so it skips CC1_1. This is an acceptable possibility, but the resource needs to be notified of it because they would not be in RUC until the CC1_2 configuration, in this case would only be in RUC with both units available, not just the single unit associated to CC1_1. | Business Rule Update | Transitions(CC1,CC2,CC3) | Angie Moy | Prafulla Nellutla
1.2 | 2009-08-26 | 1. MW1 should be > 0. MW1 should be <=LRL 2. MW4 should be >=HRL. Generate an error when this rule fails. 3. Remove the rules for MW5. Do not display the field MW5 in the Audit report. 4. Removed the field: Meets Reactive Standard?. Do not show the field in the Audit report. | Business Rule Update | Reactive Capability-WIND | Joe Weatherly/Vijay Betanabhatla | Prafulla Nellutla
1.2 | 2009-08-26 | Substation Code should be UPPER Case. Generate an Error if the Substation Code is Lowercase. This field should not allow any special characters other than underscore and dash. Generate an Error if the rule fails | Business Rule Update | Transfomer,BREAKER_SWITCH SERIES_DEVICE_DATA,CAPREACT,STATIC_VAR_COMP,LOAD | Rick Jones/Angie Moy | Prafulla Nellutla
1.2 | 2009-08-26 | 1.Date Effective(Eff_Date) field will be included in the RARF form for all the Transmission Data to indicate the Effective date of the Devices. This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | New Business Rule | Transformer/Line/Breaker-Switch/Series Device Data/Capacitor or Reactor/Load Data | Scott Middleton/Woody/Angie | Prafulla Nellutla
1.2 | 2009-08-26 | For Jointly Owned Units(Generation and Wind Units), Unit name can not exceed 4 characters. Verify the UNIT_NAME in UNIT-INFO Tab and validate that it can not exceed 4 characters for a JOU. Generate an error if rule fails. Not required for Combined Cycle Sites and Single owner units | New Business Rule | Unit-Info-GEN,WIND | Angie Moy | Prafulla Nellutla
1.2 | 2009-08-26 | Resource Entity Name should not allow any special characters are allowed. Generate an error if there is any special character in the RE Name except spaces | New Business Rule | General Information-ALL, Unit Info-GEN,CC,Wind | Angie Moy | Prafulla Nellutla
1.2 | 2009-08-26 | At least one connected device is required on each side of the Breaker/Switch. Generate an error if at least one connected device is missing on both sides Generate a Warning when at least one connected device is missing on any one side. | New Business Rule | Breaker/Switch | Joe Weatherly | Prafulla Nellutla
1.3 | 2009-10-07 | High Side Manufactured Nominal Voltage should be > Voltage at Lowest Tap Position and < Voltage at Highest Tap Position | New Business Rule | Transformer | Joe Weatherly | Prafulla Nellutla
1.4 | 2009-10-08 | Remove rule#2 for Maximum Regulating voltage. Base kv in rule#6 refers to Voltage Level of Bus bar being regulated (applicable to desired,min,maximum regulating voltage fields) | Enhancement | Capacitor/Reactor | Joe Weatherly | Prafulla Nellutla
1.5 | 2009-10-22 | No two capacitors should have the same controlling breaker or switch. Every Device entry on the “Capacitor and Reactor Data” tab sheet needs to have a unique “Device Name(s) – that this reactive device is directly connected to”. | New Business Rule | Capacitor/Reactor | Joe Weatherly | Prafulla Nellutla
1.5 | 2009-10-22 | All tap information is required if it exists on either the LTC or Fixed side. | New Business Rule | Transformer | Joe Weatherly | Prafulla Nellutla
1.6 | 2009-11-13 | Update the Audit views to include/update the rules for the operational parameters. Min Onlinetime,Min Offline-> should be >0, Decimal positive number of hours should be submitted., Warning that downstream system will round UP the value if entered decimal Maximum Online Time -> should be >0. Decimal positive number of hours should be submitted. Should enter in decimal hours, Warning that downstream system will round DOWN the value if entered decimal Maxdaily starts-> Min value1, maximum value is 13. MMS can support maximally 13 starts because to start the unit must be OFF at least one hour (plus initial hour start). Maxweekly starts-> Min value1, maximum value is 85. MMS can support maximally 85 starts because to start the unit must be OFF at least one hour (plus initial hour start). Hotstart,ColdStart,Intermediate Start->should be >=0, Decimal non-negative number of hours should be submitted., Warning that downstream system will round DOWN when the value is entered decimal Hot to Intermediate, Intermediate to cold->Should be >=0, Decimal non-negative number of hours should be submitted, Warning that downstream system will round DOWN when the value is entered decimal | Enhancement | Operational Parameters-GEN,CC,Wind | Haso, Peljto | Prafulla Nellutla
1.7 | 2009-11-18 | Desired, Minimum, and Maximum voltage fields values should have a range within 10% of the Voltage level of the Bus Bar being Regulated. Anything beyond should be a Warning. Also, remove rule#2 for (Value may not exceed 345) for Desired,Min.Regulating voltage fields | Enhancement | Capacitor-Reactor | Joe Weatherly | Prafulla Nellutla
1.8 | 2009-12-03 | Generate a warning in RARF Audit Report when Resistance or Reactance values are rounded in Transformer Data Tab in RARF. it should be accurate to the 5th decimal. | Enhancement | Transformer | Angie Moy | Prafulla Nellutla
1.9 | 2009-12-18 | Connected Device that this load is directly connected to' Field in Load Data Tab should be defined either in the Breaker/Switch Tab(if the connected device is a switch Name) or in the Transformer Tab(if the connected device is a Transformer Name). Audit report should produce an error if the rule fails. | Enhancement | Load Data Tab | Angie Moy | Prafulla Nellutla
2.0 | 2009-12-17 | Connected Device' Field in Capacitor Reactor Tab should be defined either in the Breaker/Switch Tab(if the connected device is a switch Name) or in the Transformer Tab(if the connected device is a Transformer Name). Audit report should produce an error if the rule fails. | Enhancement | Capacitor Reactor Tab | Angie Moy | Prafulla Nellutla
2.1 | 2009-12-28 | Produce a Warning Only for MW4 Field when the rule fails (MW4 should be >= HRL) for wind units that have multiple groups of turbines. Currently, Audit report generates an Error when MW4 is <= HRL, this enhancement is to produce this error for Units that have single group of turbine and produce a warning for units that have multiple groups of turbines. | Enhancement | Reactive Capability-WIND | Angie Moy | Prafulla Nellutla
2.2 | 2009-12-29 | Unit Start Date should be >= Site Start Date ( Site-Information Tab). Generate an error if the rule fails | Enhancement | Unit Info-GEN,CC,Wind | Angie Moy | Prafulla Nellutla
2.3 | 2009-10-08 | Transformer High Side Manufactured Nominal Voltage should equal to Voltage at Highest Tap - Step Size voltage to reach Nominal Tap. | Enhancement | Transformer | Joe Weatherly | Prafulla Nellutla
2.4 | 2009-11-10 | CMZ Zone is Required field. Generate an error if the field is blank. | Enhancement | Site-Information Tab | Angela Moy | Prafulla Nellutla
2.5 | 2009-12-01 | RE Duns# should not be duplicated for different Owner RE's for a Jointly Owned Unit. Generate an error when RE Duns# is same for different Owner RE's for a Jointly Owned Unit | Enhancement | Unit Info-GEN,Wind | Angela Moy | Prafulla Nellutla
2.6 | 2009-12-02 | Validate HRL value against Real Power Rating and generate a warning if HRL (NET) is greater than Real Power Rating(Gross). | Enhancement | PARAMETERS-GEN,CC,WIND | Angela Moy | Prafulla Nellutla
2.7 | 2009-11-02 | Load Tap Changer should be 'Y' when AVR is 'Y'. Generate an error if Load Tap Changer is 'N' and AVR = 'Y'. | Enhancement | Transformer | Angela Moy | Prafulla Nellutla
2.8 | 2009-11-11 | Change the Error to Warning only when LAG values(MVARLAG1,MVARLAG2,MVARLAG3,MVARLAG4) are NEGATIVE and LEAD values(MVAR1LEAD,MVAR2LEAD, MVAR3LEAD,MVAR4LEAD)are POSITIVE. This is for Wind units only. | Enhancement | Reactive Capability-WIND | Angela Moy | Prafulla Nellutla
2.9 | 2009-11-02 | Change the High Reasonability Ramp Rate ERRORS for CCUNITs to be WARNINGS instead if they fall outside of the boundaries in the rules. | Enhancement | Parameters-CC,CFG | Angela Moy | Prafulla Nellutla
2.10 | 2009-11-10 | For every configuration there must be a Transition , Ex: CC1_1 needs a Transition from & to Offline, then if they have CC1_2 it needs to show in Transitions that CC1_2 goes from and to CC1_1.The rule is for every registered configuration, there must be a. Transition indicating that configuration as TO_CONFIG (provide transition from offline or other configurations within the same plant, i.e. provide path to transit INTO that configuration) b. Transition indicating that configuration as FROM_CONFIG (provide transition to offline or other configurations within the same plant, i.e. provide path to transit OUT OF that configuration). | New Requirement | CC1,CC2,CC3Transitions | Angela Moy | Prafulla Nellutla
2.11 | 2009-12-21 | 1) Produce an Error if the Transformer Resistance/Reactance value is less than 3 decimals.(('Error! Resistance/Reactance (x) may be rounding, it should be accurate to 5th decimal') 2) Produce a Warning if the Transformer Resistance/Reactance value is greater than 2 decimals and less than 5 decimals('Warning! Resistance/Reactance (x) may be rounding, it should be accurate to 5th decimal') | Enhancement | Transformer | Angela Moy | Prafulla Nellutla
2.12 | 2009-12-29 | If the Zero Impedance Lines are contained within a single substation, then they should be removed from the Line tab and the updated connections should be shown in the Breaker/Switch tab. If Zero Impedance Lines goes between two substations, produce an error if line ratings are entered as 9999. | Enhancement | Line Data tab | Joel Koepke | Prafulla Nellutla
2.12 | 2009-12-29 | Connected Device that this load is directly connected to' Field in Load Data Tab should be defined either in the Breaker/Switch Tab(if the connected device is a switch Name) or in the Transformer Tab(if the connected device is a Transformer Name). Produce a WARNING when this rule fails | Enhancement | Load Data Tab | Angie Moy | Prafulla Nellutla
2.12 | 2009-12-29 | For wind units that have multiple groups of turbines, Produce a Warning Only when the rule#2 fails (MW4 should be >= HRL) . For Units that have single group of turbine, produce an Error when the rule fails (MW4 should be >= HRL) | Enhancement | Reactive Capability-WIND | Angie Moy | Prafulla Nellutla
2.13 | 2010-01-13 | Transformer R/X Ratio validation check added. If “Low kV” <> 1 Then ERROR if R/X > 1 Else “no warning/error” Else if “Low kV” = 1 Then Warning if R/X > 3 Else “no warning/error” (Note: Low KV refers to Low side Voltage Level(no-load)' =1 | New Requirement | Transformer Tab | Joe Weatherly | Prafulla Nellutla
2.13 | 2010-01-14 | When Generation load Split is 'Y', sum of the Fixed Load Splitting % (for each ESIID's) should be 100 | New Requirement | Site Information | Angela Moy | Prafulla Nellutla
2.14 | 2010-01-25 | Add Wind Unit Latitude & Longitude Business Rules to RARF Audit: Latitude of center of Wind Farm: Must be <= 90 decimal degrees Longitude of center of Wind Farm: Must be <= 180 decimal degrees Latitude of Meteorological Tower: Must be <= 90 decimal degrees Longitude of Meteorological Tower: Must be <= 180 decimal degrees | New Requirement | Unit Info-WIND | Angela Moy | Prafulla Nellutla
2.14 | 2010-01-26 | Lagging MVAR must always be greater than the Leading MVAR - On Reactive Capability Tab | Enhancement | Reactive Capability-GEN,CC,Wind | Joe Weatherly | Prafulla Nellutla
2.14 | 2010-02-01 | Enhancement for Seasonal Rating Limits :Business Rules: 1.Seasonal Net Max Sustainable Rating - Spring > Seasonal Net Min Sustainable Rating - Spring (Also for Summer, Fall, Winter) 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring (Also for Summer, Fall, Winter) | Enhancement | Parameters-GEN,CC,WIND,CFG | Joe Weatherly | Prafulla Nellutla
2.15 | 2010-02-04 | Add the Resource Category 'Power Storage' to the existing Resource Category list in RARF | New Requirement | Unit Info-GEN & CC | Angela Moy | Prafulla Nellutla
2.16 | 2010-02-05 | Wind groups of turbines within a unit must be of the same type and size | New Requirement | Unit Info-WIND | Angela Moy/Art Deller | Prafulla Nellutla
2.17 | 2010-02-08 | 1. Add new rule to Generation& CC Resource Primary & Sec fuel type fields: Audit report should generate an error when Physical Unit type is 'ST' or 'CA' and Primary or Secondary Fuel type is 'STM' 2.Low Side Manufactured Nominal Voltage should equal (Voltage at Lowest Tap) + (Step size voltage to reach Nominal tap) | New Requirement | Unit Info-GEN & CC | Patrick Coon & Angie Moy, Joe Weatherly | Prafulla Nellutla
2.18 | 2010-02-10 | Primary Fuel Type & Secondary fue type rule defined above is applicable only for CC units. PUNS are excluded from this rule | Enhancement | Unit Info-GEN & CC | Patrick Coon & Angie Moy | Prafulla Nellutla
2.19 | 2010-02-15 | Add rule to step size voltage field in transformer Tab. The rule is applicable to both low & high tap sections. Size of each voltage step ('x') must not be > 69 KV. Generate an error if the rule fails. | Enhancement | Transformer | Angela Moy | Prafulla Nellutla
2.20 | 2010-02-22 | Unit Generating voltage can not be below 6.9 KV | Enhancement | Unit-Info-Wind/Unit-Info-Generation | Angela Moy | Prafulla Nellutla
2.21 | 2010-02-25 | Capacitor/Reactor Tab connected device rule need to be updated Details: Current Business rule validates that the Connected Device in the capacitor/reactor tab do exist in either breaker switch tab or Transformer tab and generates an error if the rule fails. Per Network Modeling the rule needs to be updated per below reasons: For all other equipment that is not a Capacitor/Reactor, they can have connectivity references to transformers, lines, etc. However, for the Capacitor/Reactors, the EMS needs to have a controlling switch modeled, else they would always be "On Business Rule: Connected Device in Capacitor Reactor should have a Controlling Breaker/Switch in Breaker/switch Tab. Audit report should generate an error if the rule fails. | Enhancement | Capacitor-Reactor | Joe Weatherly/Angela Moy | Prafulla Nellutla
2.21 | 2010-03-08 | Unit Name/Unit Code should not allow spaces | Enhancement | Unit-Info-Wind/Unit-Info-Generation/Unit-Info-CC | Angela Moy | Prafulla Nellutla
2.22 | 2010-03-09 | RARF Audit Enhancement: Substation Code invalid message should be warning only if the PUN flag is 'yes'. Details: If a substation is invalid , audit report should generate a Warning only if the Private Network Flag set to Yes. | Enhancement | Line, Transformer, Series Device, Capacitor Reactor, Breaker Switch, Load, Static Var Compensator | Angela Moy | Prafulla Nellutla
2.22 | 2010-03-09 | Rule that wind farms should split their units if the turbines are of different size/group should be Warning not an error | Enhancement | Unit-Info-Wind | Angela Moy | Prafulla Nellutla
2.23 | 2010-03-12 | RARF Audit Rule Enhancement: Add a new Rule to Breaker/Switch tab to generate a warning when the Normal Operating Status is 'OPEN' | Requirement | Breaker-Switch | Boyda Matthew | Prafulla Nellutla
2.24 | 2010-03-17 | RARF Audit rule Enhancement: Duplicate Series Device device Error need to change to Warning Details: On the series device tab ,audit report generates an ERROR if the connected devices are duplicated. But per Network Modeling, it needs to change to a WARNING because it is plausible have a by-pass switch duplicate on both sides | Enhancement | Series Device Data | Angie Moy | Prafulla Nellutla
2.24 | 2010-03-17 | RARF Audit Enhancement: Transformer Rating rules need adjustments Details: Per network modeling feedback on the Transformer Ratings, RARF Audit rules need to be adjusted according to this: Continuous must have valid mva rating (eg: will get an ERROR if 9999.00) 2hr (9999.00 mva will produce a WARNING) 15min (9999.00 mva will produce a WARNING), also if 2hr is 9999.00 then the only valid entry for 15min is 9999.00 or it will give an ERROR. | Enhancement | Transformer | Joel Koepke | Prafulla Nellutla
2.24 | 2010-03-17 | Generate a warning only when secondary fuel type is 'STM' for ST or CA units | Enhancement | Unit-Info-CC/Unit-Info-Wind | Angela Moy | Prafulla Nellutla
2.25 | 2010-04-05 | Unit Name can not exceed 8 characters | Requirement | Unit-Info-CC/Unit-Info-Wind/Unit-Info-Generation | Angela Moy | Prafulla Nellutla
2.26 | 2010-04-08 | Add a rule to generate an ERROR when Non GSU Transformers that have entered associated units. | Requirement | Transformer | Angela Moy | Prafulla Nellutla
2.27 | 2010-04-12 | RARF Audit Enhancement: Add a rule that Transformer MVA Rating should be >= Unit Seasonal Net Max sustainable rating Details: Generate a Warning when Transformer Continuous Rating is less than Unit Seasonal Net Max sustainable rating | Requirement | Transformer | Angela Moy | Prafulla Nellutla
2.28 | 2010-04-20 | Add a rule that Add new rule that Switch Name in Breaker_Switch Table can not be duplicated for a substation code ina sitecode | Requirement | Breaker_switch | Angela Moy | Prafulla Nellutla
2.29 | 2010-04-20 | Add a rule that CCTRAIN resouce category is determined by capacity of largest simple cycle combustion turbine in the train | Requirement | unitinfo-cc | art deller | Prafulla Nellutla
2.29 | 2010-04-20 | Add a rule: When AVR is 'Y' then Tap settings are required, they can not be blank | Requirement | Transformer | Network Modeling team | Prafulla Nellutla
2.30 | 2010-04-22 | Add a rule all Device names(in transmission tabs) must be unique for each Device code for a substation in a SITE | Requirement | Line, Transformer, Series Device, Capacitor Reactor, Breaker Switch, Load, Static Var Compensator | Network Modeling team/Angie Moy | Prafulla Nellutla
2.31 | 2010-04-30 | Add a rule to the Transformer Tab that any connected devices listed in transformer tab should exist in the breaker switch tab | Requirement | Transformer Tab | Network Modeling team/Angie Moy | Prafulla Nellutla
2.31 | 2010-04-30 | Audit report should generate an error when Physical Unit type selected is 'GT' | Requirement | Unit-Info-CC | Angie Moy | Prafulla Nellutla
2.31 | 2010-05-11 | Add a new rule to Transformer Impedances that generates a Warning when R/X ratio is >0.1 | Requirement | Transformer | Angie Moy/Network Modeling | Prafulla Nellutla
2.32 | 2010-05-17 | Add a rule to Reactive Capability-GEN,CC,Wind Tabs that Audit report generates an error when the rule ( MW1 should be >=0.1) fails. | Requirement | Reactive Capability-GEN,CC,Wind | Angie Moy/Network Modeling | Prafulla Nellutla
2.32 | 2010-05-17 | Update the business rule on the Line Susceptance. If Line Data - Line Voltage Level = 69kV, value must be >=.00001<=0.3 If Line Data - Line Voltage Level = 138kV, value must be >=.00001<=0.5 If Line Data - Line Voltage Level = 345kV, value must be >=.00001<=2.2. Generate a Warning if Rule fails | Requirement | Line Information | Angie Moy/Network Modeling | Prafulla Nellutla
2.33 | 2010-06-01 | Adjust the Error that Unique Switchable device is Required on Load data Adjust the Error on the Load tab to check ONLY the Breaker tab for devices and IF at least one connected device is not listed on the Breaker tab then it gets an ERROR? Otherwise, they get approved and sometimes only have a transformer listed, but a unique controlling device must also be listed. Error! Unique controlling device must also exist in the 'BREAKER_SWITCH Tab' | Requirement | Load Data Tab | Angie Moy | Prafulla Nellutla
2.34 | 2010-06-15 | Add a rule to RARF Audit "Transformer Rating should be >=HRL or unit will be curtailed down to transformer rating" | Requirement | Transformer | Ed geer/Angie Moy | Prafulla Nellutla
2.35 | 2010-06-16 | Add a rule to generate an Error message when WIND units LRL is greater than zero.The protocol definition for WGR and LRL supports setting the LRL for WGRs to zero. "ERROR: WGR LRL should =0 to reflect the full possible net output capability of LSL submitted in real-time" | Requirement | Parameters-WIND | Scott Midlleton/Patrick Coon/Ed Geer | Prafulla Nellutla
2.36 | 2010-08-12 | Add a rule: “Sum (HRL) of PRIMARY physical CCU component within the combined cycle configuration must be greater than or equal to the HRL of configuration itself.” Now, if the alternate unit has different HRL from the primary component, the validation is somewhat complicated since we need to find the worst case combination (sum physical CCU capacity with minimum value) to compare with registered configuration HRL --- need permutation through all primary/alternate combination | Requirement | Parameters-CFG | Matthew Boyda/Kittipong | Prafulla Nellutla
2.37 | 2010-08-12 | Lower the limit for Unit generating voltage (UNIT_KV) to 4.16 kv | Enhancement | Unit Info-GEN,CC,Wind | Keith Smith | Prafulla Nellutla

## Vaidation Rules
Field/Section Type: R- Required( Not null),O= Optional ,C =Conditional
Validation Type: B = Basic Validation , DVB = Data Validation based on Business Rules , DVE = Data Validation with the existing record in ERCOT
Format /Data type: Numeric, Integer , Character, Date, Dropdown List
Source--> Represents the source of the Validation Rules | [20 empty] | General Comments
RARF VALIDATION RULES | [20 empty] | The general layout of the form needs to be improved for useability, it is currently too difficult to align the flow of information on this form, with that of the glossary. It should match the glossary line-for-line. The edits that were made here are a good start, but it is doubtfull that all discrepancies were captured. ERCOT needs to audit this form using the glossary as the master document. The source references are also woefully out-of-date, and require work. Fields highlighted in red contains suggestions/issues concerning the glossary itself, those fields highlighted in yellow pertain solely to the validation rules.
RARF FORM TYPE | RARF DATA FIELD | Field Updates | Change Description | RARF Tab | Source Report Name | Label | TABLE | DB Field | Business Rules/Basic UI validations | Field/ Tab Type | Data type | Validation Type | Source | Destination Application | Comments | Required for Screening Study (SS) | Required for Full Interconnect Study (FIS) | Planning Model (R, C, O, A) | Full Registration (R, C O, A) | Required for Planning | Issue
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | General and Site Information |  |  | General and Site Information |  |  | Not in table | Not in table | This tab is Required for all Resource Entities (Load and Generation Resources) | R |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | This submittal is for | Updated 03/09/2012 validation rule to match view |  | General and Site Information |  |  | SITECODES | SUBMIT_REASON | Not null. Select from the list: New Site, Revision, Addition of Unit(s), Deletion of Unit(s)* | R | Dropdown List | B,DVB |  |  |  | N | N |  |  | N
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Submittal Information |  |  | General and Site Information |  |  | Not in table | Not in table | Not null. Select from the list: New Site, Revision, Addition of Units, Deletion of Units | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 4/RARF Guide version 4.0/ Angela Moy |  |  | N | N |  |  | N
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Date Form Completed: |  |  | General and Site Information |  |  | SITECODES | FORM_COMP_DT | Not null. Equal to the System Date. Date Format should be mm/dd/yyyy | R | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | Y | Y
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Resource Entity Submitting Form: | 03/09/2012 Updated Validation | ADDED 06/27/2012 | General and Site Information | GeneralInformation.View |  | RE_RARF | RE_NAME | 1.This field is not null. 2. All should be capital letters 3.No Special characters except spaces and dashes. | R | Character | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | Y | Y
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Resource Entity DUNS #: |  |  | General and Site Information |  |  | SITECODES & RE_RARF | RE_DUNS | Not null. Data type should be varchar (as sometimes the value contains # with a leading zero). Duns# is either 9 digit or 13 digit .Should match with RE Duns# IN Siebel | R | Character | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk |  |  | N | N
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Site Information |  |  | General and Site Information |  |  | Not in table | Not in table | This tab is Conditional: Required if the Generation Type is ' WIND or CC or GEN' , where GEN is non-cc non-wind generation resources. This tab is not required for Load Resources. | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,MMS,Lodestar
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Resource Site Name: |  |  | General and Site Information |  |  | SITECODES | SITE_NAME | 1.This field is not null. Validate with the existing record in ERCOT?? 2. All should be capital letters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | EMS,Lodestar |  | Y | Y
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Resource Site Code: | 05/02/2012 Updated Table that this field is mapped to, adding SITE_LOAD_SPLIT. |  | General and Site Information |  |  | SITECODES & SITE_LOAD_SPLIT | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk |  |  | N | N |  |  |  | What if this is a new site?
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Street Address: |  |  | General and Site Information |  |  | SITECODES | STREET_ADDRESS | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar |  | N | N
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | City: |  |  | General and Site Information |  |  | SITECODES | CITY | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar |  | N | N
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | State |  |  | General and Site Information |  |  | SITECODES | STATE | This is Required field (can not be null) Value must be at least two characters and alphabetic only. | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar |  | N | N
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Zip Code |  |  | General and Site Information |  |  | SITECODES | ZIPCODE | This is a Required field and can not be null. Value must be 5 digits. | R | Number | B |  | Siebel |  | N | N
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | County: |  |  | General and Site Information |  |  | SITECODES | COUNTY | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar |  | Y | Y
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Site In-Service Date: |  |  | General and Site Information |  |  | SITECODES | SITE_IN_SRVC_DT | Site-In Service Date is earlier than Site-Stop Service Date. Enter the date in mm/dd/yy format. This field is not null. | R | Date | B,DVB | Lin Xu | Lodestar,MMS |  | Y | Y
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Site Stop Service Date: |  |  | General and Site Information |  |  | SITECODES | SITE_STOP_SRVC_DT | Site Stop Service Date should be later than Site-In Service Date. Format is mm/dd/yyy. This field is optional. NA is not valid , Leave it blank if not applicable. | O | Date | B,DVB | Lin Xu | Lodestar,MMS |  | N | N
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Congestion Management Zone for 2003: |  |  | General and Site Information |  |  | SITECODES | CMZ_2003 | Select from the list: North,South,Houston,West. This field is Required | O | Dropdown List | B,DVB | RARF Glossary Version 4.0/ Angela Moy |  |  | N | N |  |  |  | Why is this necessary?
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Resource owned by NOIE? |  |  | General and Site Information |  |  | SITECODES | RE_OWNED_NOIE_FLG | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | Y | Y
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Is Resource behind a NOIE Settlement Meter Point? |  |  | General and Site Information |  |  | SITECODES | RE_BHND_NOIE_SMP_FLG | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N | N
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Number of EPS Primary meters: |  |  | General and Site Information |  |  | SITECODES | NUM_EPS_METERS | This field is required and it should be an integer | R | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N | N
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Is Resource claiming status as a Non-Modeled Generator as defined in ERCOT Protocol Section 2, Resource? | 05/23/2012 Updated validation Rule 04/12/2012 Updated RARF TAB | ADDED 06/27/2012 | General and Site Information | DG_SiteInfo.View | Y/N | SITECODES | RE_CLAIM_NONMOD_STATUS | 1. If Site_Code is in NON_MODELED then If RE_CLAIM_NONMOD_STATUS is null then Error Else if RE_CLAIM_NONMOD_STATUS not Y or N, Error If Site_Code is NOT in NON_MODELED then do not validate | C | Dropdown List | B,DVB |  |  |  | N | N |  |  |  | If Site_Code is in NON_MODELED, why are you even asking the question?
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Is Resource >10 MW? | 05/23/2012 Updated validation Rule 04/12/2012 Updated RARF TAB | ADDED 06/27/2012 | General and Site Information | DG_SiteInfo.View | Y/N | SITECODES | RES_GREAT_TEN_MW | 1.If Site_Code is in NON_MODELED then If RE_CLAIM_NONMOD_STATUS is null then Error Else if RE_CLAIM_NONMOD_STATUS not Y or N, Error If Site_Code is NOT in NON_MODELED then do not validate . | C | Dropdown List | B,DVB |  |  |  | N | N |  |  |  | If Site_Code is in NON_MODELED, why are you even asking the question?
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Primary Contact (name of person ERCOT can contact with questions regarding this form) |  |  | General and Site Information |  |  | Not in table | Not in table
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Printed Name: |  |  | General and Site Information |  |  | SITECODES | NAME_PC | Not null. Validate that the Authorized rep has valid digital certificate to access the User Interface | R | Character | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | Y | Y |  |  |  | What if the Authorized Rep doesn't have a valid digital cert? Who says it has to be submitted by the AR? It is doubtful that most ARs even know what goes into a RARF.
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Title: |  |  | General and Site Information |  |  | SITECODES | TITLE_PC | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | Y | Y |  |  |  | Do you really want me to continue making up titles? I'm more than happy to do so, you know.
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Phone Number: |  |  | General and Site Information |  |  | SITECODES | PHONE_PC | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | Y | Y
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | E-mail Address: |  |  | General and Site Information |  |  | SITECODES | EMAIL_PC | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | Y | Y
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Secondary Contact (if available) |  |  | General and Site Information |  |  | Not in table | Not in table | Optional
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Printed Name: |  |  | General and Site Information |  |  | Not in table | Not in table | Optional | [6 empty] | Y | Y
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Title: |  |  | General and Site Information |  |  | Not in table | Not in table | Optional | [6 empty] | Y | Y
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Phone Number: |  |  | General and Site Information |  |  | Not in table | Not in table | Optional | [6 empty] | Y | Y
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | E-mail Address: |  |  | General and Site Information |  |  | Not in table | Not in table | Optional | [6 empty] | Y | Y
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | GEN Load Split -ESIID |  |  | GEN Load Split - ESIID |  |  | Not in table | Not in table
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | GENERATION SITE LOAD DETAILS |  |  | GEN Load Split - ESIID |  |  | Not in table | Not in table
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | ESIID_NUMBER |  |  | GEN Load Split - ESIID |  |  | SITE_LOAD_SPLIT | ESIID_NUMBER | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Generate ESIID Number + 1 (ex. ESIID_1, ESIID_2, ESIID_3) | A | [5 empty] | N | N |  |  |  | This is filled automatically in the form, why is there any validation?
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | SITECODE_ESIID |  |  | GEN Load Split - ESIID |  |  | SITE_LOAD_SPLIT | SITECODE_ESIID | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Concantanate SITECODE_ESIID_Number | A | [5 empty] | N | N |  |  |  | This is filled automatically in the form, why is there any validation?
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Generation Load Split? | Corrected 02/29/2012 |  | GEN Load Split - ESIID |  | Y/N | SITECODES | GEN_LOAD_SPLIT_FLG | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar |  | N | N
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | ERCOT Read Meter? |  |  | GEN Load Split - ESIID |  | Y/N | SITECODES | ERCOT_READ_FLG | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar |  | N | N
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | ESI ID: | 08/17/2012 - Correction Step 2 validation Rule 05/02/2012 Updated Validation Rule | 08/17/2012 - Correction Step 2 validation Rule | GEN Load Split - ESIID |  |  | SITE_LOAD_SPLIT | ESI_ID | 1.Data type is character 2.If Generation Load Split is 'N' then If RE_BHND_NOIE_SMP_FLG is 'Y', then no ESIID is required. else ESIID is required 3. If Generation Load Split is 'Y' then If RE_BHND_NOIE_SMP_FLG is 'Y' and Site_Code is in NON_MODELED, then no ESIID is required else ESIID is required | C | Character | B | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | N | N
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | TDSP Providing Service To Resource: | Corrected |  | GEN Load Split - ESIID |  | List | SITE_LOAD_SPLIT | TDSP_PROVIDING_SVC | This field is conditional. Required only if If the Generation Load Split question is answered as 'N' . Validate with the existing record in ERCOT?? | C | Character | B,DVE | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar |  | N | N
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | TDSP DUNS Number: | 03/09/2012 Updated Validation |  | GEN Load Split - ESIID |  | Automatic | SITE_LOAD_SPLIT | TDSP_DUNS | 1. Not null 2. Must match with the data existing in Siebel 3. Data type: varchar (as sometimes the value contains # with a leading zero) 4. Either a 9 or 13 digit DUNS number | R A | Integer | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 | Lodestar |  | N | N |  |  |  | This is filled automatically in the form, why is there any validation?
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Fixed Load Splitting | 05/03/2012 removed percent from label on form |  | GEN Load Split - ESIID |  |  | SITE_LOAD_SPLIT | FIXED_LD_SPLIT | 1.This field is optional/conditional. Required only if Gen Site is split among multiple ESI Id's.If entered, cross check the data with Lodestar. 2. Sum of the Fixed Load Splitting % (corresponding to each ESIID) should be 100. Generate an error if the rule fails | C/O | Numeric | B | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 | Lodestar |  | N | N |  |  |  | Add direction that "1" = 100%
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Load Serving Entity |  |  | GEN Load Split - ESIID |  | List | SITE_LOAD_SPLIT | COMP_RETAILER | This field is optional/conditional. Required only if Gen Site is split among multiple ESI Id's. | C | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar |  | N | N
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Load Serving Entity Duns# |  |  | GEN Load Split - ESIID |  | Automatic | SITE_LOAD_SPLIT | COMP_RETAILER_DUNS | This field is optional/conditional. Required only if Gen Site is split among multiple ESI Id's. If entered it should be either 9 or 13 digit number AND should match with the existing record in Lodestar? | C A | Integer | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 | Lodestar |  | N | N |  |  |  | This is filled automatically in the form, why is there any validation?
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Private Network - Site |  |  | Private Network - Site |  |  | Not in table | Not in table
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | SITE DETAILS |  |  | Private Network - Site |  |  | Not in table | Not in table
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Private Network? | 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  | Y/N | SITECODES | PRIVATE_NTWK_SITE_FLG | Select from Y or N. Private Network Flag is not null | R | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms/Kittiepong | EMS |  |  |  | Y | Y
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | PRIVATE NETWORK - SITE INFORMATION |  |  | Private Network - Site |  |  | Not in table | Not in table | This tab is conditional : Required for all Private Use Networks |  | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Average Amount Of Self-serve Private Load | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  | MW | SITECODES | AVG_LD_MW_UNIT | This field is conditional. Required if Private Network flag is 'Y' | C | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms | EMS |  |  |  | Y | Y
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Average Amount Of Self-serve Private Reactive Load | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  | MVAR | SITECODES | AVG_LD_MVAR_UNIT | This field is conditional. Required if Private Network flag is 'Y' | C | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms |  |  |  |  | Y | Y
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Expected Typical Private Network Net Interchange | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  | MW | SITECODES | NET_INTERCHNG_MW_UNIT | This field is conditional. Required if Private Network flag is 'Y' | C | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms | EMS |  |  |  | Y | Y |  |  |  | Spreadsheet does not allow negative values to be entered, reformatting of cell is necessary.
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Expected Typical Private Network Net Reactive Interchange | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  | MVAR | SITECODES | NET_INTERCHNG_MVAR_UNIT | This field is conditional. Required if Private Network flag is 'Y' | C | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms |  |  |  |  | Y | Y |  |  |  | Spreadsheet does not allow negative values to be entered, reformatting of cell is necessary.
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Private Network Gross Unit Capability | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  | MW | SITECODES | GROSS_CAPBLTY_MW_UNIT | This field is conditional. Required if Private Network flag is 'Y' | C | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms |  |  |  |  | Y | Y |  |  |  | Should strike the word "Unit", as there may be multiple units, and the field is labeled as "Site" information, so you want the aggregate amount.
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Private Network Gross Unit Reactive Capability | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  | MVAR | SITECODES | GROSS_CAPBLTY_MVAR_UNIT | This field is conditional. Required if Private Network flag is 'Y' | C | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms |  |  |  |  | Y | Y |  |  |  | Should strike the word "Unit", as there may be multiple units, and the field is labeled as "Site" information, so you want the aggregate amount.
General_Site_ESIID Information (GEN, CC, Renewable, DG, Non-Modeled) | Load Characteristics For MW Load |  |  | Private Network - Site |  |  | Not in table | Not in table | This tab is conditional : Required for all Private Use Networks |  | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
General_Site_ESIID Information (GEN, CC, PV, Wind, DG, Non-Modeled) | Large Motor, Percent Of Total MW Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  |  | SITECODES | PUN_MW_LARGEMTR_PCT | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu | MMS |  |  |  | N | N |  |  |  | Add direction that "1" = 100%, or reformat cell in RARF to be in %
General_Site_ESIID Information (GEN, CC, PV, Wind, DG, Non-Modeled) | Small Motor, Percent Of Total OF MW Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  |  | SITECODES | PUN_MW_SMALLMTR_PCT | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu | MMS |  |  |  | N | N |  |  |  | Add direction that "1" = 100%, or reformat cell in RARF to be in %
General_Site_ESIID Information (GEN, CC, PV, Wind, DG, Non-Modeled) | Resistive (heating) Load, Percent Of Total MW Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  |  | SITECODES | PUN_MW_RESISTIVE_PCT | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu | MMS |  |  |  | N | N |  |  |  | Add direction that "1" = 100%, or reformat cell in RARF to be in %
General_Site_ESIID Information (GEN, CC, PV, Wind, DG, Non-Modeled) | Discharge Lighting, Percent Of Total Mw Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  |  | SITECODES | PUN_MW_DISCHARGE_PCT | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu | MMS |  |  |  | N | N |  |  |  | Add direction that "1" = 100%, or reformat cell in RARF to be in %
General_Site_ESIID Information (GEN, CC, PV, Wind, DG, Non-Modeled) | Other, Percent Of Total MW Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  |  | SITECODES | PUN_MW_OTHER_PCT | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu | MMS |  |  |  | N | N |  |  |  | Add direction that "1" = 100%, or reformat cell in RARF to be in %
General_Site_ESIID Information (GEN, CC, PV, Wind, DG, Non-Modeled) | Load Characteristics for MVAR Load |  |  | Private Network - Site |  |  | Not in table | Not in table | This tab is conditional : Required for all Private Use Networks
General_Site_ESIID Information (GEN, CC, PV, Wind, DG, Non-Modeled) | Large Motor, Percent Of Total MVAR Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  |  | SITECODES | PUN_MVAR_LARGEMTR_PCT | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu | MMS |  |  |  | N | N |  |  |  | Add direction that "1" = 100%, or reformat cell in RARF to be in %
General_Site_ESIID Information (GEN, CC, PV, Wind, DG, Non-Modeled) | Small Motor, Percent Of Total MVAR Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  |  | SITECODES | PUN_MVAR_SMALLMTR_PCT | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | R | Lin Xu | MMS |  |  |  | N | N |  |  |  | Add direction that "1" = 100%, or reformat cell in RARF to be in %
General_Site_ESIID Information (GEN, CC, PV, Wind, DG, Non-Modeled) | Discharge Lighting, Percent Of Total MVAR Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  |  | SITECODES | PUN_MVAR_DISCHARGE_PCT | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu | MMS |  |  |  | N | N |  |  |  | Add direction that "1" = 100%, or reformat cell in RARF to be in %
General_Site_ESIID Information (GEN, CC, PV, Wind, DG, Non-Modeled) | Other, Percent Of Total MVAR Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  |  | SITECODES | PUN_MVAR_OTHER_PCT | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu | MMS |  |  |  | N | N |  |  |  | Add direction that "1" = 100%, or reformat cell in RARF to be in %
Solar Photovoltaic (PV) | Parameters - RENEWABLE |  |  | Parameters - RENEWABLE |  |  | RENEWABLE
Solar Photovoltaic (PV) | GENERATOR DETAILS |  |  | Parameters - RENEWABLE |  |  | RENEWABLE
Solar Photovoltaic (PV) | Unit Name | Do not show Message on Audit or Delta | Added 5/1/2017 | Parameters - RENEWABLE |  | List | RENEWABLE | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N | N |  |  |  | It's a drop-down list, better to make that validation in the Unit Info - GEN tab
Solar Photovoltaic (PV) | Resource Name (Unit Code/Mnemonic) |  | Added 5/1/2017 | Parameters - RENEWABLE |  | Automatic | RENEWABLE | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk |  |  | N | N |  |  |  | This is filled automatically in the form, why is there any validation?
Solar Photovoltaic (PV) | REASONABILITY LIMITS |  |  | Parameters - RENEWABLE |  |  | RENEWABLE | Not in table
Solar Photovoltaic (PV) | High Reasonability Limit |  | Added 5/1/2017 | Parameters - RENEWABLE |  | MW | RENEWABLE | HR_LMT | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit | R | Numeric | B,DVB | KitteiPong/Jamil Daouk |  |  | N | N
Solar Photovoltaic (PV) | Low Reasonability Limit |  | Added 5/1/2017 | Parameters - RENEWABLE |  | MW | RENEWABLE | LR_LMT | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | Numeric | B,DVB | KitteiPong/Lin Xu/ Jamil Daouk, Kenneth Ragsdale |  |  | N | N
Solar Photovoltaic (PV) | High Reasonability Ramp Rate Limit |  | Added 5/1/2017 | Parameters - RENEWABLE |  | MW/min | RENEWABLE | HR_RAMPRATE_LMT | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk |  |  | N | N
Solar Photovoltaic (PV) | Low Reasonability Ramp Rate Limit |  | Added 5/1/2017 | Parameters - RENEWABLE |  | MW/min | RENEWABLE | LR_RAMP_RATE_LMT | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk |  |  | N | N
Solar Photovoltaic (PV) | SEASONAL RATINGS - SPRING |  |  | Parameters - RENEWABLE |  |  | RENEWABLE | Not in table
Solar Photovoltaic (PV) | Seasonal Net Max Sustainable Rating - Spring |  | Added 5/1/2017 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MAX_SUST_RTG_SP | 1.Seasonal Net Max Sustainable Rating - Spring >= Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui |  |  | N | N
Solar Photovoltaic (PV) | Seasonal Net Min Sustainable Rating - Spring |  | Added 5/1/2017 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MIN_SUST_RTG_SP | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui |  |  | N | N
Solar Photovoltaic (PV) | Seasonal Net Max Emergency Rating - Spring |  | Added 5/1/2017 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MAX_EMGY_RTG_SP | 1.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui |  |  | N | N
Solar Photovoltaic (PV) | Seasonal Net Min Emergency Rating - Spring |  | Added 5/1/2017 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MIN_EMGY_RTG_SP | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui |  |  | N | N
Solar Photovoltaic (PV) | SEASONAL RATINGS - SUMMER |  |  | Parameters - RENEWABLE |  |  | RENEWABLE | Not in table
Solar Photovoltaic (PV) | Seasonal Net Max Sustainable Rating - Summer |  | Added 5/1/2017 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MAX_SUST_RTG_SM | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui |  |  | N | N
Solar Photovoltaic (PV) | Seasonal Net Min Sustainable Rating - Summer |  | Added 5/1/2017 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MIN_SUST_RTG_SM | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui |  |  | N | N
Solar Photovoltaic (PV) | Seasonal Net Max Emergency Rating - Summer |  | Added 5/1/2017 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MAX_EMGY_RTG_SM | 1.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui |  |  | N | N
Solar Photovoltaic (PV) | Seasonal Net Min Emergency Rating - Summer |  | Added 5/1/2017 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MIN_EMGY_RTG_SM | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui |  |  | N | N
Solar Photovoltaic (PV) | SEASONAL RATINGS - FALL |  |  | Parameters - RENEWABLE |  |  | RENEWABLE | Not in table
Solar Photovoltaic (PV) | Seasonal Net Max Sustainable Rating - Fall |  | Added 5/1/2017 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MAX_SUST_RTG_FL | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui |  |  | N | N
Solar Photovoltaic (PV) | Seasonal Net Min Sustainable Rating - Fall |  | Added 5/1/2017 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MIN_SUST_RTG_FL | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Min Sustainable Rating - Fall. >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui |  |  | N | N
Solar Photovoltaic (PV) | Seasonal Net Max Emergency Rating - Fall |  | Added 5/1/2017 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MAX_EMGY_RTG_FL | 1.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui |  |  | N | N
Solar Photovoltaic (PV) | Seasonal Net Min Emergency Rating - Fall |  | Added 5/1/2017 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MIN_EMGY_RTG_FL | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui |  |  | N | N
Solar Photovoltaic (PV) | SEASONAL RATINGS - WINTER |  |  | Parameters - RENEWABLE |  |  | RENEWABLE | Not in table
Solar Photovoltaic (PV) | Seasonal Net Max Sustainable Rating - Winter |  | Added 5/1/2017 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MAX_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui |  |  | N | N
Solar Photovoltaic (PV) | Seasonal Net Min Sustainable Rating - Winter |  | Added 5/1/2017 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MIN_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Sustainable Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui |  |  | N | N
Solar Photovoltaic (PV) | Seasonal Net Max Emergency Rating - Winter |  | Added 5/1/2017 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MAX_EMGY_RTG_WT | 1.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui |  |  | N | N
Solar Photovoltaic (PV) | Seasonal Net Min Emergency Rating - Winter |  | Added 5/1/2017 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MIN_EMGY_RTG_WT | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui |  |  | N | N
NOT in Form or Tables used only for Validation Purposes | Collector System Data? | 06/11/2012 -Added for Validation Purposes for Collector System Data |  | NA |  |  | NA | NA | If SITECODE found in Wind Table then Collector System Data is required | C | [10 empty] | This field is not in the Parameters Renewable Tab, move to proper location
NOT in Form or Tables used only for Validation Purposes | Cable Segment Data? | 06/11/2012 -Added for Validation Purposes for Cable Segment Data |  | NA |  |  | NA | NA | If SITECODE found in Wind Table then Cable Segment Data is required | C | [10 empty] | This field is not in the Parameters Renewable Tab, move to proper location
Generation | Unit Info - GEN |  |  | Unit Info - GEN |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type Selected is 'GEN' where GEN is non-CC non-wind Generation Resources. | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,MMS,NMMS
Generation | GENERATOR DETAILS |  |  | Unit Info - GEN |  |  | Not in table | Not in table
Generation | Unit Name | Do not show Message on Audit or Delta |  | Unit Info - GEN |  | All Caps | GENERATION | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | Y | Y
Generation | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | Unit Info - GEN |  | Automatic | GENERATION | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | N |  |  |  | This is filled automatically in the form, why is there any validation?
Generation | Non_Modeled Generator |  | ADDED 06/27/2012 | Unit Info - GEN | Generation_UnitInfo.View | Y/N | GENERATION | NON_MOD_GEN | Select from the list: Y or N | R | Dropdown List | B,DVB | WCS |  |  | N | N
Generation | PUC Registration Number |  |  | Unit Info - GEN |  |  | GENERATION | PUC_NUM | This field is optional. Enter a Valid Number or leave it blank if not applicable | O | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N | N
Generation | ERCOT Interconnection Project Number - only new units |  |  | Unit Info - GEN |  |  | GENERATION | ERCOT_INTRCONN_PROJ_NUM | 1.This field is optional. Required only for new units. Enter a Valid Number or leave it blank if not applicable 2. Cross check with the data entered in the field 'This submittal is for' in General Information Tab. If the value is 'New Site' then only this field is required. | O | Character | B,DVE | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Angela Moy |  |  | N | Y |  |  |  | Not all new projects receive an Interconnection Project Number (Please reference TOSBATT facility). "If the value is 'New Site' then only this field is required" - Suggest re-wording this, as written, it makes no sense.
Generation | NERC Number |  |  | Unit Info - GEN |  |  | GENERATION | NERC_NUM | This field is optional. Enter a Valid Alphanumeric value or leave it blank if not applicable | O | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N | N |  |  |  | This doesn't even belong on the RARF, organizations get registered with NERC, not generating units.
Generation | Qualifying facility |  |  | Unit Info - GEN |  | Y/N | GENERATION | QUAL_FACILITY_FLG | QF flag is not null. Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/kittiepong | Lodestar |  | N | N
Generation | SITE AND UNIT DATES |  |  | Unit Info - GEN |  |  | Not in table | Not in table
Generation | Transmission Only MRD |  | ADDED 06/27/2012 | Unit Info - GEN | Generation_UnitInfo.View | mm/dd/yyyy | GENERATION | TRANS_ONLY_DT | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB | WCS |  |  | N | N |  |  |  | This confusing, and if not needed, (and since it's optional, it's not really needed), then it should be eliminated.
Generation | Standard Generation Interconnection Agreement (SGIA) Signature Date | 11/26/2012 Change Error message to Warning | ADDED 06/27/2012 | Unit Info - GEN | Generation_UnitInfo.View | mm/dd/yyyy | GENERATION | SGIA_SIGA_DT | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date. | R | Date | B/DVB | CDannunzio |  |  | N | N
Generation | Unit Start Date (Model Ready Date) | 03/13/2012 Updated Validation | ADDED 06/27/2012 | Unit Info - GEN | Generation_UnitInfo.View | mm/dd/yyyy | GENERATION | UNIT_MRD_ST_DT | This field is optional. Format should be: MM/DD/YYYY |  |  |  | WCS |  |  | N | N
Generation | Commercial Operations Date | Upated 2/10/2016 | Upated 2/10/2016 | Unit Info - GEN |  | mm/dd/yyyy | GENERATION | UNIT_START_DT | This field is not null. Format should be: MM/DD/YYYY Unit Start Date should be >= Site Start Date ( Site-Information Tab) | R | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,NMMS |  | Y | Y
Generation | Unit End Date |  |  | Unit Info - GEN |  | mm/dd/yyyy | GENERATION | UNIT_END_DT | This field is optional. Format should be: MM/DD/YYYY | O | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,NMMS |  | N | N
Generation | POINT OF INTERCONNECTION |  |  | Unit Info - GEN |  |  | Not in table | Not in table
Generation | SubStation Code/SubStation Mnemonic | 11/26/2012 Change Error message to Warning 11/06/2012 Remove validation #2 | ADDED 06/27/2012 | Unit Info - GEN | Generation_UnitInfo.View | All Caps | GENERATION | SUBSTAT_CODE_SUB_MNEMONIC | 1) This field is not null (required). Data type must be Character. 2) This field may not have any special characters, except an underscore "_" and a dash "-" . 3 Must be <= 8 characters. Warning! Substation Code should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 4) Substation code should be in Upper case letters. Generate an error if the rule fails. | R | Character | B/DVB | CDannunzio |  |  | Y | Y |  |  |  | What if there is no "Substation" at the POI?
Generation | Voltage Level |  | ADDED 06/27/2012 | Unit Info - GEN | Generation_UnitInfo.View | kV | GENERATION | VOL_LEV | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0. | R | Float | B/DVE | CDannunzio |  |  | Y | Y |  |  |  | What if project interconnects at distribution level?
Generation | PTI Bus Number | 10/10/2012 Change Error message to Warning CR 46847 06/14/2012 Updated Validation #2 to increase to 999,999 | ADDED 06/27/2012 | Unit Info - GEN | Generation_UnitInfo.View | # | GENERATION | PTI_BUS_NUM | 1) This field is not null (required). Data type must be Integer. 2) This field must be between 1 - 999,999 | R | Integer | B/DVB | CDannunzio |  |  | Y | Y |  |  |  | There are no PTI bus numbers for distribution elements
Generation | FUEL INFORMATION |  |  | Unit Info - GEN |  |  | Not in table | Not in table
Generation | Primary Fuel Type |  |  | Unit Info - GEN |  | List | GENERATION | PRIM_FUELTYPE | Select from the list: AB, BFG, BIT, BL, DFO, GEO, JF, KER, LFG, LIG, MSW, NA, NG, NUC, OBG, OBL, OBS, OG, OO, OTH, PC, PG, RFO, SLW, STM, SUB, SUN, T, TDF, WAT, WDL, WDS, WH, WOC, WND This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS |  | Y | Y
Generation | Secondary Fuel Type |  |  | Unit Info - GEN |  | List | GENERATION | SEC_FUELTYPE | Select from the list: AB, BFG, BIT, BL, DFO, GEO, JF, KER, LFG, LIG, MSW, NA, NG, NUC, OBG, OBL, OBS, OG, OO, OTH, PC, PG, RFO, SLW, STM, SUB, SUN, T, TDF, WAT, WDL, WDS, WH, WOC, WND. This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS |  | Y | Y
Generation | Fuel Transportation Type |  |  | Unit Info - GEN |  | List | GENERATION | FUEL_TRANSTYPE | Select from the list: CV, PL, RR, TK, NA. This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N | N
Generation | Resource Category | Updated Validation 03/28/2012 |  | Unit Info - GEN |  | List | GENERATION | RES_CATG | 1)Resource Category is not null. 2)Select from the list: Nuclear,Hydro,Coal and Lignite, Gas Steam- Super Critical Boiler, Gas Steam- Reheat Boiler, Gas Steam - Non Reheat or Boiler without air preheaterd, Simple Cycle <= 90 MW, Simple Cycle > 90 MW, Diesel, Reciprocating Engine, Solar, Power Storage, Other | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/kittiepong |  |  | N | N
Generation | RATINGS AND DESIGNS |  |  | Unit Info - GEN |  |  | Not in table | Not in table
Generation | Renewable |  |  | Unit Info - GEN |  | Y/N | GENERATION | RENEWABLE_FLG | Renewable Flag is not null. Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar |  | N | N
Generation | Renewable/Offset |  |  | Unit Info - GEN |  | List | GENERATION | RENEWABLE_OFFSET | Select from the list : RN, OS, NA. This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar |  | N | N
Generation | Physical Unit Type | Updated Validation 03/28/2012 |  | Unit Info - GEN |  | List | GENERATION | PHYS_UNIT_TYPE | Select from the list: CA, CE, CS, CT, FC, GT, HY, IC, NA, OT, PS, PV, ST. This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | Y | Y
Generation | Name Plate Rating |  |  | Unit Info - GEN |  | MVA | GENERATION | NAME_PLT_RTG | Name Plate Rating should be >= Real Power Rating | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS |  | Y | Y
Generation | Real Power Rating |  |  | Unit Info - GEN |  | MW | GENERATION | RTG_MW | 1) Real Power Rating should be > Reactive Power Rating 2) When RES_CATG = Power Storage or Energy Storage thean Real Power Rating should be >= Reactive Power Rating | R | Numeric | B,DVB | Lin Xu | MMS,NMMS |  | Y | Y
Generation | Reactive Power Rating |  |  | Unit Info - GEN |  | MVAR | GENERATION | RTG_MVAR | Name Plate Rating should be >= Reactive Power Rating | R | Numeric | B,DVB | Lin Xu | MMS,NMMS |  | Y | Y |  |  |  | This rule is redundant to the business rule for Real Power Rating, suggest eliminating it.
Generation | Turbine Rating |  |  | Unit Info - GEN |  | MW | GENERATION | TURBINE_RTG | This field is optional. Enter Numeric value or leave it blank if not applicable. | O | Numeric | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | Y | Y
Generation | Unit Generating Voltage |  |  | Unit Info - GEN |  | kV | GENERATION | UNIT_KV | 1. This field is not null and it should be a number 2. Unit Generating voltage can not be below 0.48 KV | R | Numeric | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS |  | Y | Y
Generation | Governor Droop Setting | 08/29/2012 Update #2 and #3 Business Rule 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Unit Info - GEN | Generation_UnitInfo.View |  | GENERATION | GOV_DROOP | 1) Data type must be Numeric, Positive value (>=0.0) 2) Generate an Error if it is <(less than).02 OR >(greater than).05) | O C | Numeric | B,DVB | Operation Analysis |  |  | N | N |  |  |  | The Operating Guide limit on droop settings are MAXIMUMS, and there is no prohibition against lower values. Glossary lists this field as conditional, but doesn't identify what it's conditional to. Does the validation rule still work, or is a statement that it can be left null required?
Generation | Governor Dead-band | 08/29/2012 Update #2 and #3 Business Rule 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Unit Info - GEN | Generation_UnitInfo.View | Hz | GENERATION | GOV_DEAD_BND | 1) This field is required 2) Data type must be Numeric, Positive value (>=0.0) 3) Generate an Error Warning if > 0.01734 | R | Numeric | B,DVB | Operation Analysis |  |  | N | N
Generation | Design Max Ambient Temperature | 10/11/2012 Updated validation rules CR 46863 | ADDED 06/27/2012 | Unit Info - GEN | Generation_UnitInfo.View | degree F | GENERATION | DESIGN_MAX_AMB_TEMP | 1) If a numeric value is entered, then the Value must >100 and <150 2) “NA” 3) “Unknown” | O |  |  | Operation Analysis |  |  | N | N
Generation | Design Min Ambient Temperature | 10/11/2012 Updated validation rules CR 46863 | ADDED 06/27/2012 | Unit Info - GEN | Generation_UnitInfo.View | degree F | GENERATION | DESIGN_MIN_AMB_TEMP | 1) If a numeric value is entered, then the Value must >-100 and <32 2) “NA” 3) “Unknown” | O |  |  | Operation Analysis |  |  | N | N
Generation | Unit Info - AGR | Added 04/02/2012 | ADDED 06/27/2012 | Unit Info - AGR | Generation_UnitInfo.View |  | Not in table | Not in table
Generation | GENERATOR DETAILS | Added 04/02/2012 | ADDED 06/27/2012 | Unit Info - AGR | Generation_UnitInfo.View |  | Not in table | Not in table
Generation | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code Added 04/02/2012 | ADDED 06/27/2012 | Unit Info - AGR | Generation_UnitInfo.View | Automatic | GENERATION | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | Y | Y |  |  |  | This is filled automatically in the form, why is there any validation?
Generation | AGR DETAILS | Added 04/02/2012 | ADDED 06/27/2012 | Unit Info - AGR | Generation_UnitInfo.View |  | Not in table | Not in table
Generation | Aggregated Generation Resource(Manufacturer/Model) | Added 04/02/2012 | ADDED 06/27/2012 | Unit Info - AGR | Generation_UnitInfo.View | all caps | GENERATION | AGR_TYPE | Data type should be character. | O | Character |  |  |  |  | N | N
Generation | MW Rating for this Aggregated Generation Resource | Added 04/02/2012 2/10/2016 Updated Valadation rule #2 - NPRR704 | ADDED 06/27/2012 Updated 2/10/2016 | Unit Info - AGR | Generation_UnitInfo.View | MW | GENERATION | AGR_MW_MDL_RTG | 1)Data type should be Numeric 2)Must be less than 20 | O | Numeric |  |  |  |  | Y | Y
Generation | Number of this type of Aggregated Generation Resource | Added 04/02/2012 | ADDED 06/27/2012 | Unit Info - AGR | Generation_UnitInfo.View | # | GENERATION | AGR_NUM | 1)Should be an integer | O | Integer |  |  |  |  | Y | Y
CC | Unit Info - Train |  |  | Unit Info - Train |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type selected is 'CC' | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,MMS,NMMS
CC | CC TRAIN DETAILS |  |  | Unit Info - Train |  |  | Not in table | Not in table
CC | Train Name | Corrected 02/23/2012 |  | Unit Info - Train |  | List | TRAIN | TRAIN_NAME | This field is not null. Data type: Character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | Y | Y
CC | Train Code | Corrected 02/23/2012 |  | Unit Info - Train |  | Automatic | TRAIN | TRAIN_CODE | 1. This field is not null. Data type is Character | R A | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS |  | Y | Y |  |  |  | This is filled automatically in the form, why is there any validation?
CC | Non_Moldeled Generator |  | ADDED 06/27/2012 | Unit Info - Train | CC_UnitInfo.View | Y/N | TRAIN | NON_MOD_GEN | Select from the list: Y or N | R | Dropdown List | B,DVB | WCS |  |  | N | N
CC | PUC Registration Number |  |  | Unit Info - Train |  |  | TRAIN | PUC_NUM | This field is optional. NA is not valid , Leave it blank if not applicable. | O | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N | N
CC | NERC Number |  |  | Unit Info - Train |  |  | TRAIN | NERC_NUM | This field is optional. Enter a Valid Alphanumeric value or leave it blank if not applicable | O | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N | N |  |  |  | This doesn't even belong on the RARF, organizations get registered with NERC, not generating units.
CC | Qualifying Facility? |  |  | Unit Info - Train |  | Y/N | TRAIN | TRN_QUAL_FACILITY_FLG | QF Flag is not null. Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/kittiepong | Lodestar |  | N | N
CC | SITE AND UNIT DATES |  |  | Unit Info - Train |  |  | Not in table | Not in table
CC | Train Commercial Operations Date |  | Updated field name 2/10/2016 | Unit Info - Train |  | mm/dd/yyyy | TRAIN | TRN_UNIT_START_DATE | This field is not null. Format should be: MM/DD/YYYY Unit Start Date should be >= Site Start Date ( Site-Information Tab) | R | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,NMMS |  | Y | Y
CC | Train Retirement Date |  | Updated field name 2/10/2016 | Unit Info - Train |  | mm/dd/yyyy | TRAIN | TRN_UNIT_END_DATE | This field is optional. Format should be MM/DD/YYYY.NA is not valid , Leave it blank if not applicable. | O | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,NMMS |  | N | N
CC | FUEL INFORMATION |  |  | Unit Info - Train |  |  | Not in table | Not in table
CC | Fuel Transportation Type |  |  | Unit Info - Train |  | List | TRAIN | FUEL_TRANSTYPE_TRN | Select from the list: CV, PL, RR, TK, NA. This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N | N
CC | Resource Category |  |  | Unit Info - Train |  | List | TRAIN | RES_CATG_TRN | 1.Resource type is not null. 2. Select from the list: Combined Cycle <= 90 MW, Combined Cycle >90 MW This field is not null 3. Resource Category for CCTrain is determined by the capacity of largest simple cycle combustion turbine in the train. Example if a CCTrain is combined cycle >90 MW, largest CT in the train should have real power rating>90. Audit report should generate an error if the CT's are <90 MW in this case. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/kittiepong |  |  | N | N
CC | POWER AUGMENTATION |  |  | Unit Info - Train |  |  | Not in table | Not in table
CC | Is Train Augmented With Duct Burner(s)? |  |  | Unit Info - Train |  | Y/N | TRAIN | TRN_AUG_DUCTBRNRS_FLG | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N | N
CC | Is Train Augmented with Evap Cooler(s)? |  |  | Unit Info - Train |  | Y/N | TRAIN | TRN_AUG_EVAP_CLRS_FLG | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N | N
CC | Is Train augmented with Chiller(s)? |  |  | Unit Info - Train |  | Y/N | TRAIN | TRN_AUG_CHILLERS_FLG | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N | N
CC | Other Augmentation? |  |  | Unit Info - Train |  | Y/N | TRAIN | TRN_OTHER_AUG | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N | N
CC | Unit Info - CC |  |  | Unit Info - CC |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type selected is 'CC' | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,MMS,NMMS
CC | GENERATOR DETAILS |  |  | Unit Info - CC |  |  | Not in table | Not in table
CC | Unit Name | Do not show Message on Audit or Delta |  | Unit Info - CC |  | All Caps | CCUNIT | UNIT_NAME | 1.This field is not null. Data type: Character. | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | Y | Y
CC | SITE_CODE |  |  | UNIT Info - CC |  | Automatic | CCUNIT | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | A | Character |  |  |  |  | N | N |  |  |  | This is filled automatically in the form, why is there any validation?
CC | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | Unit Info - CC |  | Automatic | CCUNIT | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | Y | Y |  |  |  | This is filled automatically in the form, why is there any validation?
CC | ERCOT Interconnection Project Number - Only New Units |  |  | Unit Info - CC |  |  | CCUNIT | ERCOT_INTRCONN_PROJ_NUM | 1.This field is optional. Required only for new units. NA is not valid , Leave it blank if not applicable. 2. Cross check with the data entered in the field 'This submittal is for' in General Information Tab. If the value is 'New Site' then only this field is required. | O | Character | B,DVE | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Angela Moy |  |  | N | N
CC | SITE AND UNIT DATES |  |  | Unit Info - CC |  |  | Not in table | Not in table
CC | Transmission Only MRD |  | ADDED 06/27/2012 | Unit Info - CC | CC_UnitDetails.View | mm/dd/yyyy | CCUNIT | TRANS_ONLY_DT | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB | WCS |  |  | N | N
CC | Standard Generation Interconnection Agreement (SGIA) Signature Date | 11/26/2012 Change Error message to Warning | ADDED 06/27/2012 | Unit Info - CC | CC_UnitDetails.View | mm/dd/yyyy | CCUNIT | SGIA_SIG_DT | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date. | R | Date | B/DVB | CDannunzio |  |  | N | N
CC | Unit Start Date (Model Ready Date) | 03/13/2012 Updated Validation | ADDED 06/27/2012 | Unit Info - CC | CC_UnitDetails.View | mm/dd/yyyy | CCUNIT | UNIT_MRD_ST_DT | This field is optional. Format should be: MM/DD/YYYY |  |  |  | WCS |  |  | N | N
CC | Commercial Operations Date | Updated 2/10/2016 | Updated 2/10/2016 | Unit Info - CC |  | mm/dd/yyyy | CCUNIT | UNIT_START_DT | This field is not null. Format should be: MM/DD/YYYY Unit Start Date should be >= Site Start Date ( Site-Information Tab) | R | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,NMMS |  | Y | Y
CC | Unit End Date |  |  | Unit Info - CC |  | mm/dd/yyyy | CCUNIT | UNIT_END_DT | This field is optional. Format should be: MM/DD/YYYY | O | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,NMMS |  | N | N
CC | POINT OF INTERCONNECTION |  |  | Unit Info - CC |  |  | Not in table | Not in table
CC | SubStation Code/SubStation Mnemonic | 11/26/2012 Change Error message to Warning 11/06/2012 Remove validation #2 | ADDED 06/27/2012 | Unit Info - CC | CC_UnitDetails.View | All Caps | CCUNIT | SUBSTAT_CODE_SUB_MNEMONIC | 1) This field is not null (required). Data type must be Character. 2) This field may not have any special characters, except an underscore "_" and a dash "-" . 3 Must be <= 8 characters. Warning! Substation Code should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 4) Substation code should be in Upper case letters. Generate an error if the rule fails. | R | Character | B/DVB | CDannunzio |  |  | Y | Y
CC | Voltage Level |  | ADDED 06/27/2012 | Unit Info - CC | CC_UnitDetails.View | kV | CCUNIT | VOL_LEV | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | R | Float | B/DVE | CDannunzio |  |  | Y | Y
CC | PTI Bus Number | 10/10/2012 Change Error message to Warning CR 46847 06/14/2012 Updated Validation #2 to increase to 999,999 | ADDED 06/27/2012 | Unit Info - CC | CC_UnitDetails.View | # | CCUNIT | PTI_BUS_NUM | 1) This field isnot null (required). Data type must be Integer. 2) This field must be between 1 - 999,999 | R | Integer | B/DVB | CDannunzio |  |  | Y | Y
CC | FUEL INFORMATION |  |  | Unit Info - CC |  |  | Not in table | Not in table
CC | Primary Fuel Type |  |  | Unit Info - CC |  | List | CCUNIT | PRIM_FUELTYPE | 1. Select from the list: DFO, JF, KER, NA, NG, OBG, OO, OG, TDF, WDL, WH, STM 2. Audit report should generate an error when Physical Unit type is 'ST' or 'CA' and Primary or Secondary Fuel type is 'STM'. The rule is not applicable for PUN sites | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS |  | Y | Y
CC | Secondary Fuel Type |  |  | Unit Info - CC |  | List | CCUNIT | SEC_FUELTYPE | 1. Select from the list: DFO, JF, KER, NA, NG, OBG, OO, OG, TDF, WDL, WH, STM 2.Audit report should generate an error when Physical Unit type is 'ST' or 'CA' and Primary or Secondary Fuel type is 'STM'. The rule is not applicable for PUN sites | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS |  | Y | Y
CC | RATINGS AND DESIGNS |  |  | Unit Info - CC |  |  | Not in table | Not in table
CC | Physical Unit Type |  |  | Unit Info - CC |  | List | CCUNIT | PHYS_UNIT_TYPE | Select from the list:CA, CC, CS, CT, ST, OT This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS |  | Y | Y
CC | Name Plate Rating |  |  | Unit Info - CC |  | MVA | CCUNIT | NAME_PLT_RTG | Name Plate Rating should be >= Real Power Rating | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS |  | Y | Y
CC | Real Power Rating |  |  | Unit Info - CC |  | MW | CCUNIT | RTG_MW | Real Power Rating should be > Reactive Power Rating | R | Numeric | B,DVB | Lin Xu | MMS,NMMS |  | Y | Y
CC | Reactive Power Rating |  |  | Unit Info - CC |  | MVAR | CCUNIT | RTG_MVAR | Name Plate Rating should be >= Reactive Power Rating | R | Numeric | B,DVB | Lin Xu | MMS,NMMS |  | Y | Y
CC | Turbine Rating |  |  | Unit Info - CC |  | MW | CCUNIT | TURBINE_RTG | This field is optional. NA is not valid , Leave it blank if not applicable. | O | Numeric | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | Y | Y
CC | Unit Generating Voltage |  |  | Unit Info - CC |  | kV | CCUNIT | UNIT_KV | 1. This field is not null and it should be a number 2. Unit Generating voltage can not be below 4.16 KV | R | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS |  | Y | Y
CC | Governor Droop Setting | 08/29/2012 Update #2 and #3 Business Rule 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Unit Info - CC | CC_UnitDetails.View |  | CCUNIT | GOV_DROOP | 1) This field is required 2) Data type must be Numeric, Positive value (>=0.0) 3) Generate a Warning if it is <(less than).04 OR >(greater than).05) 3) Audit report should generate an error warning when Physical Unit type is ‘CT’ and value is <>(not) 0.04. 4) Audit report should generate an error warning when Physical Unit type is ‘CA’ and value is <>(not) 0.05. | R | Numeric | B,DVB | Operations Analysis |  |  | N | N |  |  |  | Droop setting limits are maximums, there is no prohibition from having them set lower.
CC | Governor Dead-band | 08/29/2012 Update #2 and #3 Business Rule 05/03/2012 removed percent from label on form | Updated 05/21/2013 ADDED 06/27/2012 | Unit Info - CC | CC_UnitDetails.View | Hz | CCUNIT | GOV_DEAD_BND | 1) This field is required 2) Data type must be Numeric, Positive value (>=0.0) 3) Generate an Error if > 0.036. >0.034 3) Generate a Warning if > 0.017 | R | Numeric | B,DVB | Operations Analysis |  |  | N | N
CC | Design Max Ambient Temperature | 10/11/2012 Updated validation rules CR 46863 | ADDED 06/27/2012 | Unit Info - CC | CC_UnitDetails.View | degree F | CCUNIT | DESIGN_MAX_AMB_TEMP | 1) If a numeric value is entered, then the Value must >100 and <150 2) “NA” 3) “Unknown” | O |  |  | Operations Analysis |  |  | N | N |  |  |  | Instead of NA or Unknown, how about letting the preparer just leave it blank?
CC | Design Min Ambient Temperature | 10/11/2012 Updated validation rules CR 46863 | ADDED 06/27/2012 | Unit Info - CC | CC_UnitDetails.View | degree F | CCUNIT | DESIGN_MIN_AMB_TEMP | 1) If a numeric value is entered, then the Value must >-100 and <32 2) “NA” 3) “Unknown” | O |  |  | Operations Analysis |  |  | N | N |  |  |  | Instead of NA or Unknown, how about letting the preparer just leave it blank?
Wind | Unit Info - Wind |  |  | Unit Info - RENEWABLE |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type selected is 'WIND ' | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,MMS,NMMS
Wind | GENERATOR DETAILS |  |  | Unit Info - RENEWABLE |  |  | Not in table | Not in table
Wind | Unit Name | Do not show Message on Audit or Delta |  | Unit Info - RENEWABLE |  | All Caps | RENEWABLE | UNIT_NAME | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | Y | Y
Wind | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code 05/17/2012 Update #3 validation |  | Unit Info - RENEWABLE |  | Automatic | RENEWABLE | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | Y | Y |  |  |  | This is filled automatically in the form, why is there any validation?
Wind | Site Code |  |  | Unit Info - RENEWABLE |  | Automatic | RENEWABLE | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R A | Character |  |  |  |  | N | N |  |  |  | This is filled automatically in the form, why is there any validation?
Wind | Non_Modeled Generator |  | ADDED 06/27/2012 | Unit Info - RENEWABLE | Wind_UnitInfo.View | Y/N | RENEWABLE | NON_MOD_GEN | Select from the list: Y or N | R | Dropdown List | B,DVB | WCS |  |  | N | N
Wind | PUC Registration Number |  |  | Unit Info - RENEWABLE |  |  | RENEWABLE | PUC_NUM | This field is optional and it should be a number. NA is not valid , Leave it blank if not applicable. | O | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N | N
Wind | ERCOT Interconnection Project Number - only new units |  |  | Unit Info - RENEWABLE |  |  | RENEWABLE | ERCOT_INTRCONN_PROJ_NUM | 1.This field is optional. Required only for new units. NA is not valid , Leave it blank if not applicable. 2. Cross check with the data entered in the field 'This submittal is for' in General Information Tab. If the value is 'New Site' then only this field is required. | O | Character | B,DVE | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Angela Moy |  |  | N | N
Wind | NERC Number |  |  | Unit Info - RENEWABLE |  |  | RENEWABLE | NERC_NUM | This field is optional. Enter a Valid Alphanumeric value or leave it blank if not applicable | O | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N | N |  |  |  | This doesn't even belong on the RARF, organizations get registered with NERC, not generating units.
Wind | Qualifying Facility |  |  | Unit Info - RENEWABLE |  | Y/N | RENEWABLE | QUAL_FACILITY_FLG | Select from the list: Y or N. QF Flag is not null | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/kittiepong | Lodestar |  | N | N
Wind | SITE AND UNIT DATES |  |  | Unit Info - RENEWABLE |  |  | Not in table | Not in table
Wind | Transmission Only Date (POI) |  | ADDED 06/27/2012 | Unit Info - RENEWABLE | Wind_UnitInfo.View | mm/dd/yyyy | RENEWABLE | TRANS_ONLY_DT | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB |  |  |  | N | N
Wind | Standard Generation Interconnection Agreement (SGIA) Signature Date | 11/26/2012 Change Error message to Warning | ADDED 06/27/2012 | Unit Info - RENEWABLE | Wind_UnitInfo.View | mm/dd/yyyy | RENEWABLE | SGIA_SIG_DT | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date. | R | Date | B/DVB | CDannunzio |  |  | N | N
Wind | Unit Start Date (Model Ready Date) | 03/13/2012 Updated Validation | ADDED 06/27/2012 | Unit Info - RENEWABLE | Wind_UnitInfo.View | mm/dd/yyyy | RENEWABLE | UNIT_MRD_ST_DT | This field is optional. Format should be: MM/DD/YYYY | R |  |  | WCS |  |  | N | N
Wind | Commercial Operations Date | Updated 2/10/2016 | Updated 2/10/2016 | Unit Info - RENEWABLE |  | mm/dd/yyyy | RENEWABLE | UNIT_START_DT | This field is not null. Format should be: MM/DD/YYYY Unit Start Date should be >= Site Start Date ( Site-Information Tab) | R | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar |  | Y | Y
Wind | Unit End Date |  |  | Unit Info - RENEWABLE |  | mm/dd/yyyy | RENEWABLE | UNIT_END_DT | This field is optional. Format Should be: MM/DD/YYYY. NA is not valid , Leave it blank if not applicable. | O | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar |  | N | N
Wind | POINT OF INTERCONNECTION |  |  | Unit Info - RENEWABLE |  |  | Not in table | Not in table
Wind | SubStation Code/SubStation Mnemonic | 11/26/2012 Change Error message to Warning 11/06/2012 Remove validation #2 | ADDED 06/27/2012 | Unit Info - RENEWABLE | Wind_UnitInfo.View | All caps | RENEWABLE | SUBSTAT_CODE_SUB_MNEMONIC | 1) This field is not null (required). Data type must be Character. 2) This field may not have any special characters, except an underscore "_" and a dash "-" . 3 Must be <= 8 characters. Warning! Substation Code should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 4) Substation code should be in Upper case letters. Generate an error if the rule fails. | R | Character | B/DVB | CDannunzio |  |  | Y | Y
Wind | Voltage Level | 03/13/12 Updated | ADDED 06/27/2012 | Unit Info - RENEWABLE | Wind_UnitInfo.View | kV | RENEWABLE | VOL_LEV | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0. | R | Float | B/DVE | CDannunzio |  |  | Y | Y
Wind | PTI Bus Number | 10/10/2012 Change Error message to Warning CR 46847 06/14/2012 Updated Validation #2 to increase to 999,999 | ADDED 06/27/2012 | Unit Info - RENEWABLE | Wind_UnitInfo.View | # | RENEWABLE | PTI_BUS_NUM | 1) This field is not null (required). Data type must be Integer. 2) This field must be between 1 - 999,999 | R | Integer | B/DVB | CDannunzio |  |  | Y | Y
Wind | FUEL INFORMATION |  |  | Unit Info - RENEWABLE |  |  | Not in table | Not in table
Wind | Renewable |  |  | Unit Info - RENEWABLE |  | Y/N | RENEWABLE | RENEWABLE_FLG | Select from the list: Y or N. This field is not null | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar |  | N | N
Wind | Renewable/Offset |  |  | Unit Info - RENEWABLE |  | List | RENEWABLE | RENEWABLE_OFFSET | Select from the list : RN, OS, NA. This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar |  | N | N
Wind | Resource Category |  |  | Unit Info - RENEWABLE |  | List | RENEWABLE | RES_CATG | 1.Resource Category is not null. 2.Select from the list: Wind Generation Resource, Solar and OT Other | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/kittiepong |  |  | Y | Y
Wind | RATINGS AND DESIGNS |  |  | Unit Info - RENEWABLE |  |  | Not in table | Not in table
Wind | Physical Unit Type | Updated Validation 03/28/2012 |  | Unit Info - RENEWABLE |  | List | RENEWABLE | PHYS_UNIT_TYPE | Select from the list: WT, PV OT | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | Y | Y
Wind | Name Plate Rating |  |  | Unit Info - RENEWABLE |  | MVA | RENEWABLE | NAME_PLT_RTG | Name Plate Rating should be >= Real Power Rating | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS |  | Y | Y
Wind | Real Power Rating |  |  | Unit Info - RENEWABLE |  | MW | RENEWABLE | RTG_MW | Real Power Rating should be > Reactive Power Rating | R | Numeric | B,DVB | Lin Xu | MMS,NMMS |  | Y | Y
Wind | Reactive Power Rating |  |  | Unit Info - RENEWABLE |  | MVAR | RENEWABLE | RTG_MVAR | Name Plate Rating should be >= Reactive Power Rating | R | Numeric | B,DVB | Lin Xu | MMS,NMMS |  | Y | Y
Wind | Unit Generating Voltage |  |  | Unit Info - RENEWABLE |  | kV | RENEWABLE | UNIT_KV | Data type is Numeric. Unit Generating voltage can not be below 4.16 KV | R | Numeric | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS |  | Y | Y
Wind | Governor Droop Setting | 08/29/2012 Update #2 and #3 Business Rule 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Unit Info - RENEWABLE | Wind_UnitInfo.View |  | RENEWABLE | GOV_DROOP | 1) Data type must be Numeric, Positive value (>=0.0) 2) Generate an Error if it is <(less than).02 OR >(greater than).05) | R | Numeric | B,DVB | Operations Analysis |  |  | N | N |  |  |  | Droop setting limits are maximums, there is no prohibition from having them set lower.
Wind | Governor Dead-Band | 08/29/2012 Update #2 and #3 Business Rule 05/03/2012 removed percent from label on form | Updated: 05/21/2013 added rule #4 ADDED 06/27/2012 | Unit Info - RENEWABLE | Wind_UnitInfo.View | Hz | RENEWABLE | GOV_DEAD_BND | 1) This field is required 2) Data type must be Numeric, Positive value (>=0.0) 3) Generate an Error Warning if > 0.017 | R | Numeric | B,DVB | Operations Analysis |  |  | N | N
Wind | Design Max Ambient Temperature | 10/11/2012 Updated validation rules CR 46863 | ADDED 06/27/2012 | Unit Info - RENEWABLE | Wind_UnitInfo.View | Degree F | RENEWABLE | DESIGN_MAX_AMB_TEMP | 1) If a numeric value is entered, then the Value must >100 and <150 2) “NA” 3) “Unknown” | O |  |  | Operations Analysis |  |  | N | N |  |  |  | Instead of NA or Unknown, how about letting the preparer just leave it blank?
Wind | Design Min Ambient Temperature | 10/11/2012 Updated validation rules CR 46863 | ADDED 06/27/2012 | Unit Info - RENEWABLE | Wind_UnitInfo.View | Degree F | RENEWABLE | DESIGN_MIN_AMB_TEMP | 1) If a numeric value is entered, then the Value must >-100 and <32 2) “NA” 3) “Unknown” | O |  |  | Operations Analysis |  |  | N | N |  |  |  | Instead of NA or Unknown, how about letting the preparer just leave it blank?
Wind | Maximum Operating Temperature |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | degree F | RENEWABLE | MAX_OPR_TEMP | 1) This field is required 2) Data type must be Numeric, Positive value (>=0.0) | R | [6 empty] | R
Wind | Minimum Operating Temperature |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | degree F | RENEWABLE | MIN_OPR_TEMP | 1) This field is required 2) Data type must be Numeric | R | [6 empty] | R
Wind | METEOROLOGICAL TOWER AND INSTRUMENTATION INFORMATION |  |  | Unit Info - RENEWABLE |  |  | Not in table | Not in table
Wind | Average Height Above Ground Of Turbine Hub |  |  | Unit Info - RENEWABLE | Wind_UnitInfo.View | Meters | RENEWABLE | AVG_HGHT_ABV_GRND | This field is not null and it should be a number | R | Numeric
Wind | Latitude of Meteorological Tower |  |  | Unit Info - RENEWABLE |  | decimal degrees(N) | RENEWABLE | LAT_METG_TOWER | 1. This field is not null. Data type must be Float 2. Latitude of Meteorological Tower : Must be <= 90 decimal degrees | R | Numeric | B | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | N | N
Wind | Longitude of Meteorological Tower |  |  | Unit Info - RENEWABLE |  | decimal degrees(W) | RENEWABLE | LONG_METG_TOWER | 1. This field is not null. Data type must be Float 2.Longitude of Meteorological Tower: Must be <= 180 decimal degrees | R | Numeric | B | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | N | N
Wind | Height of Meteorological Instrumentation - Wind Speed |  | ADDED 06/27/2012 | Unit Info - RENEWABLE | Wind_UnitInfo.View | Meters | RENEWABLE | HGT_MET_TWR_WND_SPD | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Float | B/DVB | CDannunzio |  |  | N | N
Wind | Height of Meteorological Instrumentation - Wind Direction |  | ADDED 06/27/2012 | Unit Info - RENEWABLE | Wind_UnitInfo.View | Meters | RENEWABLE | HGT_MET_TWR_WND_DIRT | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Float | B/DVB | CDannunzio |  |  | N | N
Wind | Height of Meteorological Instrumentation - Barometric Pressure |  | ADDED 06/27/2012 | Unit Info - RENEWABLE | Wind_UnitInfo.View | Meters | RENEWABLE | HGT_MET_TWR_BAR_PRES | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Float | B/DVB | CDannunzio |  |  | N | N
Wind | Height of Meteorological Instrumentation - Temperature |  | ADDED 06/27/2012 | Unit Info - RENEWABLE | Wind_UnitInfo.View | Meters | RENEWABLE | HGT_MET_TWR_TEMP | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Float | B/DVB | CDannunzio |  |  | N | N
Wind | WEATHER LIMITATIONS - WIND ONLY |  |  | Unit Info - RENEWABLE
Wind | High Wind Speed Cut-Out |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | m/s | RENEWABLE | HIGH_WND_SPD_CO | 1) This field is required 2) Data type must be Numeric, Positive value (>=0.0) | R | [6 empty] | R
Wind | High Wind Speed Cut-Out time |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | minutes | RENEWABLE | HIGH_WND_SPD_CO_TIME | 1) This field is required 2) Data type must be a time, Positive value (>=0.0) | R | [6 empty] | R
Wind | High Wind Speed Cut-Out Reset |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | m/s | RENEWABLE | HIGH_WND_SPD_CO_RESET | 1) This field is required 2) Data type must be Numeric, Positive value (>=0.0) | R | [6 empty] | R
Wind | High Wind Speed Cut-Out Reset Time |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | minutes | RENEWABLE | HIGH_WND_SPD_CO_RESET_TIME | 1) This field is required 2) Data type must be a time, Positive value (>=0.0) | R | [6 empty] | R
Solar Photovoltaic (PV) | Unit Info - RENEWABLE |  |  | Unit Info - RENEWABLE |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type selected is 'WIND ' | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,MMS,NMMS
Solar Photovoltaic (PV) | GENERATOR DETAILS |  |  | Unit Info - RENEWABLE |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | UNIT NAME | Do not show Message on Audit or Delta | Added 5/1/2017 | Unit Info - RENEWABLE |  | All Caps | RENEWABLE | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | Y | Y
Solar Photovoltaic (PV) | Resource Name (Unit Code/Mnemonic) |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | Automatic | RENEWABLE | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | N |  |  |  | This is filled automatically in the form, why is there any validation?
Solar Photovoltaic (PV) | Site Code |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | Automatic | RENEWABLE | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | A | Character |  |  |  |  | N | N |  |  |  | This is filled automatically in the form, why is there any validation?
Solar Photovoltaic (PV) | Non_Modeled Generator |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | Y/N | RENEWABLE | NON_MOD_GEN | Select from the list: Y or N | R | Dropdown List | B,DVB | WCS |  |  | N | N
Solar Photovoltaic (PV) | PUC Registration Number |  | Added 5/1/2017 | Unit Info - RENEWABLE |  |  | RENEWABLE | PUC_NUM | This field is optional. Enter a Valid Number or leave it blank if not applicable | O | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N | N
Solar Photovoltaic (PV) | ERCOT Interconnection Project Number - Only New Units |  | Added 5/1/2017 | Unit Info - RENEWABLE |  |  | RENEWABLE | ERCOT_INTRCONN_PROJ_NUM | 1.This field is optional. Required only for new units. Enter a Valid Number or leave it blank if not applicable 2. Cross check with the data entered in the field 'This submittal is for' in General Information Tab. If the value is 'New Site' then only this field is required. | O C | Character | B,DVE | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Angela Moy |  |  | N | Y
Solar Photovoltaic (PV) | NERC Number |  | Added 5/1/2017 | Unit Info - RENEWABLE |  |  | RENEWABLE | NERC_NUM | This field is optional. Enter a Valid Alphanumeric value or leave it blank if not applicable | O | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N | N |  |  |  | This doesn't even belong on the RARF, organizations get registered with NERC, not generating units.
Solar Photovoltaic (PV) | Qualifying Facility |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | Y/N | RENEWABLE | QUAL_FACILITY_FLG | QF flag is not null. Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/kittiepong | Lodestar |  | N | N
Solar Photovoltaic (PV) | SITE AND UNIT DATES |  |  | Unit Info - RENEWABLE |  |  | RENEWABLE
Solar Photovoltaic (PV) | Transmission Only MRD |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | mm/dd/yyyy | RENEWABLE | TRANS_ONLY_DT | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB | WCS |  |  | N | N
Solar Photovoltaic (PV) | Standard Generation Interconnection Agreement (SGIA) Signature Date |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | mm/dd/yyyy | RENEWABLE | SGIA_SIGA_DT | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date. | R | Date | B/DVB | CDannunzio |  |  | N | N
Solar Photovoltaic (PV) | Unit Start Date (Model Ready Date) |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | mm/dd/yyyy | RENEWABLE | UNIT_MRD_ST_DT | This field is optional. Format should be: MM/DD/YYYY | O |  |  | WCS |  |  | N | N
Solar Photovoltaic (PV) | Commercial Operations Date |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | mm/dd/yyyy | RENEWABLE | UNIT_START_DT | This field is not null. Format should be: MM/DD/YYYY Unit Start Date should be >= Site Start Date ( Site-Information Tab) | R | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,NMMS |  | Y | Y
Solar Photovoltaic (PV) | Unit End Date |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | mm/dd/yyyy | RENEWABLE | UNIT_END_DT | This field is optional. Format should be: MM/DD/YYYY | O | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,NMMS |  | N | N
Solar Photovoltaic (PV) | POINT OF INTERCONNECTION |  |  | Unit Info - RENEWABLE |  |  | RENEWABLE
Solar Photovoltaic (PV) | SubStation Code/SubStation Mnemonic |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | All Caps | RENEWABLE | SUBSTAT_CODE_SUB_MNEMONIC | 1) This field is not null (required). Data type must be Character. 2) This field may not have any special characters, except an underscore "_" and a dash "-" . 3 Must be <= 8 characters. Warning! Substation Code should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 4) Substation code should be in Upper case letters. Generate an error if the rule fails. | R | Character | B/DVB | CDannunzio |  |  | Y | Y
Solar Photovoltaic (PV) | Voltage Level |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | kV | RENEWABLE | VOL_LEV | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, 230 or 345 3) The value must be > 0. | R | Float | B/DVE | CDannunzio |  |  | Y | Y
Solar Photovoltaic (PV) | PTI Bus Number |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | # | RENEWABLE | PTI_BUS_NUM | 1) This field is not null (required). Data type must be Integer. 2) This field must be between 1 - 999,999 | R | Integer | B/DVB | CDannunzio |  |  | Y | Y
Solar Photovoltaic (PV) | FUEL INFORMATION |  |  | Unit Info - RENEWABLE |  |  | RENEWABLE
Solar Photovoltaic (PV) | Resource Category |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | List | RENEWABLE | RES_CATG | 1)Resource Category is not null. 2)Select from the list: Solar, Wind Generation Resource or Other | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/kittiepong |  |  | N | N
Solar Photovoltaic (PV) | Renewable |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | Y/N | RENEWABLE | RENEWABLE_FLG | Renewable Flag is not null. Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar |  | N | N
Solar Photovoltaic (PV) | Renewable/Offset |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | Y/N | RENEWABLE | RENEWABLE_OFFSET | Select from the list : RN, OS, NA. This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar |  | N | N
Solar Photovoltaic (PV) | RATINGS AND DESIGNS |  |  | Unit Info - RENEWABLE |  |  | RENEWABLE
Solar Photovoltaic (PV) | Physical Unit Type |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | List | RENEWABLE | PHYS_UNIT_TYPE | Select from the list: WT or PV,. This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | Y | Y
Solar Photovoltaic (PV) | Name Plate Rating |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | MVA | RENEWABLE | NAME_PLT_RTG | Name Plate Rating should be >= Real Power Rating | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS |  | Y | Y
Solar Photovoltaic (PV) | Real Power Rating |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | MW | RENEWABLE | RTG_MW | Real Power Rating should be > Reactive Power Rating | R | Numeric | B,DVB | Lin Xu | MMS,NMMS |  | Y | Y |  |  |  | Either the Real power rating should br greater than or equal to the Reactive power rating, or the Name Plate rating should just be greater than the Reactive power, (no, or equal to).
Solar Photovoltaic (PV) | Reactive Power Rating |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | MVAR | RENEWABLE | RTG_MVAR | Name Plate Rating should be >= Reactive Power Rating | R | Numeric | B,DVB | Lin Xu | MMS,NMMS |  | Y | Y
Solar Photovoltaic (PV) | Turbine Rating |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | MW | RENEWABLE | TURBINE_RTG | This field is optional. Enter Numeric value or leave it blank if not applicable. | O C | Numeric | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | Y | Y
Solar Photovoltaic (PV) | Unit Generating Voltage |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | kV | RENEWABLE | UNIT_KV | 1. This field is not null and it should be a number 2. Unit Generating voltage can not be below 4.16 KV | R | Numeric | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS |  | Y | Y
Solar Photovoltaic (PV) | Governor Droop Setting |  | Added 5/1/2017 | Unit Info - RENEWABLE |  |  | RENEWABLE | GOV_DROOP | 1) Data type must be Numeric, Positive value (>=0.0) 2) Generate an Error if it is <(less than).02 OR >(greater than).05) | O C | Numeric | B,DVB | Operation Analysis |  |  | N | N |  |  |  | Droop setting limits are maximums, there is no prohibition from having them set lower.
Solar Photovoltaic (PV) | Governor Dead-band |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | Hz | RENEWABLE | GOV_DEAD_BND | 1) This field is required 2) Data type must be Numeric, Positive value (>=0.0) 3) Generate a Warning if > 0.017 | R | Numeric | B,DVB | Operation Analysis |  |  | N | N
Solar Photovoltaic (PV) | Design Max Ambient Temperature |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | degree F | RENEWABLE | DESIGN_MAX_AMB_TEMP | 1) If a numeric value is entered, then the Value must >100 and <150 2) “NA” 3) “Unknown” | O |  |  | Operation Analysis |  |  | N | N
Solar Photovoltaic (PV) | Design Min Ambient Temperature |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | degree F | RENEWABLE | DESIGN_MIN_AMB_TEMP | 1) If a numeric value is entered, then the Value must >-100 and <32 2) “NA” 3) “Unknown” | O |  |  | Operation Analysis |  |  | N | N
Solar Photovoltaic (PV) | Maximum Operating Temperature |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | degree F | RENEWABLE | MAX_OPR_TEMP | 1) This field is required 2) Data type must be Numeric, Positive value (>=0.0) | R
Solar Photovoltaic (PV) | Minimum Operating Temperature |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | degree F | RENEWABLE | MIN_OPR_TEMP | 1) This field is required 2) Data type must be Numeric | R
Solar Photovoltaic (PV) | Height of Meteorological Instrumentation - Wind speed |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | meters | RENEWABLE | HGT_MET_TWR_WND_SPD | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Float | B/DVB | CDannunzio |  |  | N | N |  |  |  | Why is wind speed required for a PV unit?
Solar Photovoltaic (PV) | Height of Meteorological Instrumentation - Wind direction |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | meters | RENEWABLE | HGT_MET_TWR_WND_DIRT | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Float | B/DVB | CDannunzio |  |  | N | N |  |  |  | Why is wind direction required for a PV unit?
Solar Photovoltaic (PV) | Height of Meteorological Instrumentation - Barometric pressure |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | meters | RENEWABLE | HGT_MET_TWR_BAR_PRES | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Float | B/DVB | CDannunzio |  |  | N | N |  |  |  | Why is barometric pressure required for a PV unit?
Solar Photovoltaic (PV) | Height of Meteorological Instrumentation - Temperature |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | meters | RENEWABLE | HGT_MET_TWR_TEMP | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Float | B/DVB | CDannunzio |  |  | N | N |  |  |  | Why is temperature required for a PV unit?
Solar Photovoltaic (PV) | Height of Meteorological Instrumentation - Irradiance (PV Only) |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | meters | RENEWABLE | HGT_MET_TWR_IRRD | 1) This field is required 2) Data type must be Numeric, Positive value (>=0.0) | R
Solar Photovoltaic (PV) | Average Height above ground of Panel Center (PV Only) |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | meters | RENEWABLE | AVG_HGT_PNL_CNTR | 1) This field is required 2) Data type must be Numeric, Positive value (>=0.0) | R
Solar Photovoltaic (PV) | Site Elevation above Sea Level (PV Only) |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | meters | RENEWABLE | SITE_ELV | 1) This field is required 2) Data type must be Numeric | R
Solar Photovoltaic (PV) | PV Unit Capacity |  |  | Unit Info - RENEWABLE |  |  | RENEWABLE
Solar Photovoltaic (PV) | Nameplate DC Capacity |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | MW | RENEWABLE | NAME_PLT_DC_CAP | 1) This field is required 2) Data type must be Numeric, Positive value (>=0.0) | R
Solar Photovoltaic (PV) | Nameplate AC Capacity |  | Added 5/1/2017 | Unit Info - RENEWABLE |  | MW | RENEWABLE | NAME_PLT_AC_CAP | 1) This field is required 2) Data type must be Numeric, Positive value (>=0.0) | R
Wind | Turbine Details | 12/10/2013 Tab name changed to TURBINE DETAILS | 12/10/2013 Tab name changed to TURBINE DETAILS | Wind Turbine Details |  |  | Not in table | Not in table
Wind | WIND GENERATION GROUP DETAILS | 12/10/2013 Tab name changed to TURBINE DETAILS | 12/10/2013 Tab name changed to TURBINE DETAILS | Wind Turbine Details |  |  | Not in table | Not in table
Wind | Resoure Name (Unit Code/Mnemonic) | 12/10/13 Moved from Planning - Wind tab. 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code | Added 12/10/13 Moved from Planning - Wind tab and Wind Table - Duplicate Data on Turbine Table | Wind Turbine Details |  | Automatic | TURBINE | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | Y | Y |  |  |  | This is filled automatically in the form, why is there any validation?
Wind | WGR Group | Added 12/10/13 | Added 12/10/13 | Wind Turbine Details |  |  | TURBINE | WGR_GRP | Numeric Value | O | Numeric |  | NPRR425
Wind | Group Code (Hidden Field on Form) | Added 12/10/13 | Added 12/10/13 | Wind Turbine Details |  | Automatic | TURBINE | GRP_CODE | Concantante UNIT_CODE_TUR_MFG_MOD_WGR_GRP | R A |  |  | NPRR425
Wind | SITE_GROUP | Added 12/10/13 | Added 12/10/13 | Wind Turbine Details |  | Automatic | TURBINE | SITE_GRP | Concantante SITE_CODE_SITE_GRP if WGR_GRP | R A |  |  | NPRR425
Wind | TURBINE DETAILS | Added 12/10/13 | Added 12/10/13 | Wind Turbine Details |  |  | Not in table | Not in table
Wind | Turbine Manufacturer/Model | 12/10/13 Name change and moved from Unit Info - Turbine | 12/10/13 Moved fields from Unit Info - Turbine tab and duplicate values from Wind Table. (WIND.TUR_TYPE) | Wind Turbine Details |  |  | TURBINE | TUR_MFG_MOD | This field is not null and the Data type should be character. | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | Y | Y
Wind | MW Rating for this model of Turbine | 12/10/13 Moved from Unit Info - Turbine and Wind Table | 12/10/13 Moved fields from Unit Info - Turbine tab and duplicate values from Wind Table. | Wind Turbine Details |  | MW | TURBINE | TUR_MW_MDL_RTG | This field is not null and the Data type should be Numeric | R | Numeric | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | Y | Y
Wind | Number of Turbine Manufacturer/Model | 12/10/13 Name change and moved from Unit Info - Turbine | 12/10/13 Moved fields from Unit Info - Turbine tab and duplicate values from Wind Table. (Audit and Delta Report) | Wind Turbine Details |  | # | TURBINE | TUR_NUM | This field is not null and it should be an integer | R | Numeric | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | Y | Y
Wind | Turbine Type | Added 12/10/13 | Added 12/10/13 (NULL VALUES) | Wind Turbine Details |  | 1,2,3,4,5 | TURBINE | TUR_TYPE | Select from List | R | List |  |  |  |  | Y | Y
Wind | PLANNING DETAILS | Added 12/10/13 | Added 12/10/13 | Wind Turbine Details |  |  | Not in table | Not in table
Wind | What is the Mva Base That the Following Data Is Based On? | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table | Wind Turbine Details |  | MVA | TURBINE | MVABASE | 1) This field is required 2) Value must be Float 3) Value must be >0 "ERROR! MVABASE ( ) must be greater than 0 MVA" 4) Generate a Warning if MVABASE greater than 12.0; "Warning! MVABASE ( ) is greater than 12.0 MVA, please enter the data on the WTG Rated MVA base” | R | Float | B | Planning Team |  |  | N | Y
Wind | What Is The Kv Base That The Following Data Is Based On? | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table | Wind Turbine Details |  | KV | TURBINE | KVBASE | 1) This field is required 2) Value must be >0 and <= 18 "ERROR! KVBASE ( ) is greater than 18 KV or less than or equal to 0 KV" 3) Generate a Warning if KVBASE> 12 "Warning! KVBASE is greater than 12 KV" | R | Float | B,DVB | Planning Team |  |  | N | Y
Wind | Subtransient Reactance X'',(Instantaneous Fault Current Period) (unsaturated) | 12/10/13 Moved from Planning - Wind tab and name change | 12/10/13 Moved from Planning - Wind tab and Wind Table. (Audit and Delta Report) | Wind Turbine Details |  | p.u. | TURBINE | DIRECT_AXIS_SUBSTNT_REACTANCE | 1) This field is required and Data type is float 2) Value must be between 0.0 and 10.0 3) Generate a Warning if X"di (unsaturated) < X"dv (saturated) | R | Float | B | Planning Team |  |  | N | N
Wind | Transient Reactance, X' (First 2-3 cycles of the Fault) (unsaturated) | 12/10/13 Moved from Planning - Wind tab and name change | 12/10/13 Moved from Planning - Wind tab and Wind Table | Wind Turbine Details |  | p.u. | TURBINE | DIRECT_AXIS_TRANSNT_REACTANCE | 1) This field is required and Data type is float 2) Value must be between 0.0 and 10.0 3) Generate a Warning if X’di (unsaturated) < X’dv (saturated) | R | Float | B | Planning Team |  |  | N | N
Wind | Positive Sequence Resistance (unsaturated) | 12/10/2013 Moved from Planning - Wind tab | 12/10/2013 Moved from Planning - Wind tab and Wind Table. (Audit and Delta Report) | Wind Turbine Details |  | R in p.u. | TURBINE | POSITIVE_SEQ_Z_R_UNSATURATED_PU | 1) This field is required and Data type is float 2) Value must be between 0.0 and 10.0 | R | Float |  | Planning Team |  |  | N | N
Wind | Synchronous Reactance X (After 4 cycles of the fault) (unsaturated) | 12/10/2013 Moved from Planning - Wind tab | 12/10/2013 Moved from Planning - Wind tab and Wind Table. (Audit and Delta Report) | Wind Turbine Details |  | X in p.u. | TURBINE | POSITIVE_SEQ_Z_X_UNSATURATED_PU | 1) This field is required and Data type is numeric 2) Value must be between 0.0 and 10.0 | R | Float |  | Planning Team |  |  | N | N
Wind | Negative Sequence Z (unsaturated) | 12/10/2013 Moved from Planning - Wind tab | 12/10/2013 Moved from Planning - Wind tab and Wind Table | Wind Turbine Details |  | R in p.u. | TURBINE | NEGATIVE_SEQ_Z_R_UNSATURATED_PU | 1) This field is required and Data type is float 2) Value must be between 0.0 and 10.0 | R | Float |  | Planning Team |  |  | N | N
Wind | Negative Sequence Z (unsaturated) | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table | Wind Turbine Details |  | X in p.u. | TURBINE | NEGATIVE_SEQ_Z_X-UNSATURATED_PU | 1) This field is required and Data type is float 2) Value must be between 0.0 and 10.0 | R | Float |  | Planning Team |  |  | N | N
Wind | Zero Sequence Z (unsaturated) | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table | Wind Turbine Details |  | R in p.u. | TURBINE | ZERO_SEQ_Z_R_UNSATURATED_PU | 1) This field is required and Data type is float 2) Value must be >= 0.0 and <= 99999.0 [for ungrounded turbines] | R | Float |  | Planning Team |  |  | N | N
Wind | Zero Sequence Z (unsaturated) | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table | Wind Turbine Details |  | X in p.u. | TURBINE | ZERO_SEQ_Z_X_UNSATURATED_PU | 1) This field is required and Data type is float 2) Value must be >= 0.0 and <= 99999.0 [for ungrounded turbines] | R | Float |  | Planning Team |  |  | N | N
Wind | Subtransient Reactance X'',(Instantaneous Fault Current Period) (saturated) | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table. (Audit and Delta Report) | Wind Turbine Details |  | p.u. | TURBINE | DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED | 1) This field is required and Data type is float 2) Value must be between 0.0 and 10.0 | R | Float | B | Planning Team |  |  | N | N
Wind | Transient Reactance, X' (First 2-3 cycles of the Fault) (saturated) | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table. (Audit and Delta Report) | Wind Turbine Details |  | p.u. | TURBINE | DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED | 1) This field is required and Data type is float 2) Value must be between 0.0 and 10.0 | R | Float | B | Planning Team |  |  | N | N
Wind | Positive Sequence Resistance (saturated) | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table. (Audit and Delta Report) | Wind Turbine Details |  | R in p.u. | TURBINE | POSITIVE_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be between 0.0 and 10.0 | R | Float | B | Planning Team | NMMS |  | N | N
Wind | Synchronous Reactance X (After 4 cycles of the fault) (saturated) | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table(Audit and Delta Report) | Wind Turbine Details |  | X in p.u. | TURBINE | POSITIVE_SEQ_Z_X_PU | 1) This field is required and Data type is numeric 2) Value must be between 0.0 and 10.0 | R | Float | B | Planning Team | NMMS |  | N | N
Wind | Negative Sequence Z (saturated) | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table | Wind Turbine Details |  | R in p.u. | TURBINE | NEGATIVE_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be between 0.0 and 10.0 | R | Float | B | Planning Team |  |  | N | N
Wind | Negative Sequence Z (saturated) | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table | Wind Turbine Details |  | X in p.u. | TURBINE | NEGATIVE_SEQ_Z_X_PU | 1) This field is required and Data type is float 2) Value must be between 0.0 and 10.0 | R | Float | B | Planning Team |  |  | N | N
Wind | Zero Sequence Z (saturated) | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table | Wind Turbine Details |  | R in p.u. | TURBINE | ZERO_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be >= 0.0 and <= 99999.0 [for ungrounded turbines] | R | Float | B | Planning Team | NMMS |  | N | N
Wind | Zero Sequence Z (saturated) | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table | Wind Turbine Details |  | X in p.u. | TURBINE | ZERO_SEQ_Z_X_PU | 1) This field is required and Data type is float 2) Value must be >= 0.0 and <= 99999.0 [for ungrounded turbines] | R | Float | B | Planning Team | NMMS |  | N | N
Wind | Grounding Resistance For An Impedance Grounded Generator In P.U. (100 Mva Base) | 12/10/2013 Moved from Planning - Wind tab and name change | 12/10/13 Moved from Planning - Wind tab and Wind Table (Audit and Delta Report) | Wind Turbine Details |  | p.u. | TURBINE | ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU | 1) This field is required and Data type is numeric 2 Value must be greater than or equal to 0.0 and less than or equal to 99999.0 | R | Float |  | Model Adminstration |  |  | N | N
Wind | Grounding Reactance For An Impedance Grounded Generator In P.U. (100 Mva Base) | 12/10/2013 Moved from Planning - Wind tab and name change | 12/10/13 Moved from Planning - Wind tab and Wind Table (Audit and Delta Report) | Wind Turbine Details |  | p.u. | TURBINE | ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU | 1) This field is required and Data type is numeric 2) Value must be greater than or equal to 0.0 and less than or equal to 99999.0 | R | Float |  | Model Adminstration |  |  | N | N
Wind | Instantaneous Controlled Fault Current Magnitude (Multiple of full load current) for Turbine Types 3 & 4 | Updated 08/15/14 rule 2 and 3 Added 12/10/13 | Added 12/10/13 | Wind Turbine Details |  | p.u. | TURBINE | INST_CTRL_FAULT_CUR_MAG | 1) This field is conditional. Required for Turbine Types 3 and 4.(ONLY) 2) Value must be greater than or egual to 1 AND less than or equal to 5.8 3) Generate a warning if greater than or equal 3.5 | C | Numeric
Wind | Controlled Fault Current Magnitude At 2 to 3 cycles after fault (Multiple of full load current) for Turbine Types 3 & 4 | Updated 08/15/14 rule 2 and 3 Added 12/10/13 | Added 12/10/13 | Wind Turbine Details |  | p.u. | TURBINE | CTRL_FAULT_CUR_MAG_TWO_THREE_CYCLES | 1) This field is conditional. Required for Turbine Types 3 and 4.(ONLY) 2) Value must be greater than or egual to 0.8 AND less than or equal to 3 3) Generate a warning if greater than or equal 1.8 or less than 1.0 | C | Numeric
Wind | Controlled Fault Current Magnitude At 4 plus cycles after fault (Multiple of full load current) for Turbine Types 3 & 4 | Updated 08/15/14 rule 2 and 3 Updated Validation rule #3 01/31/2014 | Added 12/10/13 | Wind Turbine Details |  | p.u. | TURBINE | CTRL_CTRL_FAULT_CUR_MAG_FOUR_PLUS_CYCLES | 1) This field is conditional. Required for Turbine Types 3 and 4.(ONLY) 2) Value must be greater than or egual to .45 AND less than or equal to 3 3) Generate a warning greater than or equal to 1.5 or less than 1.0 | C | Numeric
Wind | TURBINE STEP-UP TRANSFORMER DATA | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab | Wind Turbine Details |  |  | Not in table | Not in table
Wind | Continuous Rating |  | Added 5/1/2017 | Wind Turbine Details |  | MVA | TURBINE | PAD_XF_CONTINUOS | 1) This field is required 2) Data type must be Numeric, Positive value (>=0.0) | R
Wind | High Side Voltage Level (nominal) | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table | Wind Turbine Details |  | Kv | TURBINE | HIGH_SIDE_VT_LEVL | 1) This field is required 2) Data type must be real 3) Generate an Error if not between 1 and 69 | R | Real | B,DVB | Planning Team/Model Adminstration |  |  | N | Y
Wind | Low Side Voltage Level (nominal) | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table | Wind Turbine Details |  | KV | TURBINE | LOW_SIDE_VT_LEVL | 1) This field is required 2) Data type must be real 3) Generate an Error if not < 69 | R | Real | B,DVB | Planning Team/Model Adminstration |  |  | N | Y
Wind | High Side Voltage Connection | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table | Wind Turbine Details |  | List | TURBINE | HIGH_SIDE_VT_CONNT | 1) This field is required 2) Data type must be from list (Wye, Wye - Grounded or Delta) 3) Generate an Error if blank | R | Real | B,DVB | Planning Team/Model Adminstration |  |  | N | Y
Wind | Low Side Voltage Connection | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table | Wind Turbine Details |  | List | TURBINE | LOW_SIDE_VT_CONNT | 1) This field is required 2) Data type must be from list (Wye, Wye - Grounded or Delta) 3) Generate an Error if blank | R | Real | B,DVB | Planning Team/Model Adminstration |  |  | N | Y
Wind | Impedance Z | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table | Wind Turbine Details |  | p.u. | TURBINE | IMPEDANCE_Z | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0 | R | Real | B,DVB | Planning Team/Model Adminstration |  |  | N | Y
Wind | X/R Ratio | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table | Wind Turbine Details |  |  | TURBINE | X_R_RATIO | 1) This field is required 2) Data type must be real 3) Generate an Error if < 1 | R | Real | B,DVB | Planning Team/Model Adminstration |  |  | N | Y
Wind | Zero Sequence Z | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table | Wind Turbine Details |  | p.u. | TURBINE | ZERO_SEQ_Z | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0 | R | Real | B,DVB | Planning Team/Model Adminstration |  |  | N | Y
Wind | Zero Sequence X/R Ratio | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table | Wind Turbine Details |  |  | TURBINE | ZERO_SEQ_X_R_RATIO | 1) This field is required 2) Data type must be real 3) Generate an Error if < 1 | R | Real | B,DVB | Planning Team/Model Adminstration |  |  | N | Y
Wind | Base Mva For Transformer Data | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab and Wind Table | Wind Turbine Details |  | MVA | TURBINE | BASE_MVA_TRANSFORMER_DATA | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. 4) Value must be >0 "ERROR! MVABASE ( ) must be greater than 0 MVA" 5) Generate Warning if greater than 12 MVA "Warning! MVABASE ( ) is greater than 12.0 MVA, please enter the data on the Transformer Rated MVA base” | R | Real | B,DVB | Planning Team/Model Adminstration |  |  | N | Y
Wind | PSSE MODELS : THE FOLLOWING FILES ARE REQUIRED TO BE SUBMITTED. PLEASE INCLUDE ALL PSSE FILES IN A ZIP OR COMPRESSED FOLDER IN THE DYNAMIC DATA TAB. | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab | Wind Turbine Details |  |  | TURBINE | Not in table
Wind | PSSE Compatible Wind Generator Models | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab | Wind Turbine Details |  |  | Not in table | Not in table | [7 empty] | N | Y
Wind | Dynamic Reactive Device Form | 12/10/13 Moved from Planning - Wind tab | 12/10/13 Moved from Planning - Wind tab | Wind Turbine Details |  |  | Not in table | Not in table | [7 empty] | N | Y
Solar Photovoltaic (PV) | Inverter Details - SOLAR |  |  | Inverter Details - SOLAR |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | INVERTER DETAILS |  |  | Inverter Details - SOLAR
Solar Photovoltaic (PV) | Skid/Array Configuration Identifier |  | Added 5/1/2017 | Inverter Details - SOLAR |  | All Caps | INVERTER | SKD_ARY_CONFIG_ID | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | [10 empty] | Glossary lists this an automatic field
Solar Photovoltaic (PV) | Inverter Manufacturer |  | Added 5/1/2017 | Inverter Details - SOLAR |  | All Caps | INVERTER | INVRT_MFG | This field is not null and the Data type should be character. | R
Solar Photovoltaic (PV) | Inverter Model |  | Added 5/1/2017 | Inverter Details - SOLAR |  | Numeric | INVERTER | INVRT_MDL | This field is not null and the Data type should be Numeric | R
Solar Photovoltaic (PV) | MW Rating for this Model of Inverter |  | Added 5/1/2017 | Inverter Details - SOLAR |  | MW | INVERTER | INVRT_MW__MDL_RTG | This field is not null and it should be an integer | R
Solar Photovoltaic (PV) | Number of Inverters per Skid/Array Transformer |  | Added 5/1/2017 | Inverter Details - SOLAR |  | # | INVERTER | NUM_INVRT_TRANS | 1) This field is required 2) Data type must be Numeric, Positive value (>=0.0) | R
Solar Photovoltaic (PV) | PLANNING DETAILS |  |  | Inverter Details - SOLAR
Solar Photovoltaic (PV) | What is the MVA base that the following data is based on? |  | Added 5/1/2017 | Inverter Details - SOLAR |  | MVA | INVERTER | MVABASE | 1) This field is required 2) Value must be Float 3) Value must be >0 "ERROR! MVABASE ( ) must be greater than 0 MVA" 4) Generate a Warning if MVABASE greater than 12.0; "Warning! MVABASE ( ) is greater than 12.0 MVA, please enter the data on the Inverter Rated MVA base” | R
Solar Photovoltaic (PV) | What is the kV base that the following data is based on? |  | Added 5/1/2017 | Inverter Details - SOLAR |  | KV | INVERTER | KVBASE | 1) This field is required 2) Value must be >0 and <= 1.0 "ERROR! KVBASE ( ) is greater than 1 KV or less than or equal to 0 KV" 3) Generate a Warning if KVBASE < 0.3 or KVBASE> 0.70 "Warning! KVBASE ( ) is less than 0.3 KV or greater than 0.7 KV" | R
Solar Photovoltaic (PV) | Subtransient Reactance X''d,(Instantaneous Fault Current Period) (unsaturated) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | p.u. | INVERTER | DIRECT_AXIS_SUBSTNT_REACTANCE | 1) This field is required and Data type is float 2) Value must be between 0.0 and 10.0 3) Generate a Warning if X"di (unsaturated) < X"dv (saturated) | R
Solar Photovoltaic (PV) | Transient Reactance, X' (First 2-3 cycles of the Fault) (unsaturated) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | p.u. | INVERTER | DIRECT_AXIS_TRANSNT_REACTANCE | 1) This field is required and Data type is float 2) Value must be between 0.0 and 10.0 3) Generate a Warning if X’di (unsaturated) < X’dv (saturated) | R
Solar Photovoltaic (PV) | Positive Sequence Resistance (unsaturated) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | R in p.u. | INVERTER | POSITIVE_SEQ_Z_R_UNSATURATED_PU | 1) This field is required and Data type is float 2) Value must be between 0.0 and 10.0 | R
Solar Photovoltaic (PV) | Synchronous Reactance X (After 4 cycles of the fault) (unsaturated) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | X in p.u. | INVERTER | POSITIVE_SEQ_Z_X_UNSATURATED_PU | 1) This field is required and Data type is numeric 2) Value must be between 0.0 and 10.0 | R
Solar Photovoltaic (PV) | Negative Sequence Z (unsaturated) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | R in p.u. | INVERTER | NEGATIVE_SEQ_Z_R_UNSATURATED_PU | 1) This field is required and Data type is float 2) Value must be between 0.0 and 10.0 | R
Solar Photovoltaic (PV) | Negative Sequence Z (unsaturated) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | X in p.u. | INVERTER | NEGATIVE_SEQ_Z_X-UNSATURATED_PU | 1) This field is required and Data type is float 2) Value must be >= 0.0 and <= 99999.0 | R
Solar Photovoltaic (PV) | Zero Sequence Z (unsaturated) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | R in p.u. | INVERTER | ZERO_SEQ_Z_R_UNSATURATED_PU | 1) This field is required and Data type is float 2) Value must be between 0.0 and 10.0 | R
Solar Photovoltaic (PV) | Zero Sequence Z (unsaturated) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | X in p.u. | INVERTER | ZERO_SEQ_Z_X_UNSATURATED_PU | 1) This field is required and Data type is float 2) Value must be >= 0.0 and <= 99999.0 | R
Solar Photovoltaic (PV) | Subtransient Reactance X'',(Instantaneous Fault Current Period) (saturated) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | p.u. | INVERTER | DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED | 1) This field is required and Data type is float 2) Value must be between 0.0 and 10.0 | R
Solar Photovoltaic (PV) | Transient Reactance, X' (First 2-3 cycles of the Fault) (saturated) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | p.u. | INVERTER | DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED | 1) This field is required and Data type is float 2) Value must be between 0.0 and 10.0 | R
Solar Photovoltaic (PV) | Positive Sequence Resistance (saturated) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | R in p.u. | INVERTER | POSITIVE_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be between 0.0 and 10.0 | R
Solar Photovoltaic (PV) | Synchronous Reactance X (After 4 cycles of the fault) (saturated) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | X in p.u. | INVERTER | POSITIVE_SEQ_Z_X_PU | 1) This field is required and Data type is numeric 2) Value must be between 0.0 and 10.0 | R
Solar Photovoltaic (PV) | Negative Sequence Z (saturated) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | R in p.u. | INVERTER | NEGATIVE_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be between 0.0 and 10.0 | R
Solar Photovoltaic (PV) | Negative Sequence Z (saturated) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | X in p.u. | INVERTER | NEGATIVE_SEQ_Z_X_PU | 1) This field is required and Data type is float 2) Value must be >= 0.0 and <= 99999.0 | R
Solar Photovoltaic (PV) | Zero Sequence Z (saturated) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | R in p.u. | INVERTER | ZERO_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be between 0.0 and 10.0 | R
Solar Photovoltaic (PV) | Zero Sequence Z (saturated) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | X in p.u. | INVERTER | ZERO_SEQ_Z_X_PU | 1) This field is required and Data type is float 2) Value must be >= 0.0 and <= 99999.0 | R
Solar Photovoltaic (PV) | Zero Sequence Grounding Resistance For An Impedance Grounded Inverter in p.u. (100 MVA Base) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | p.u. | INVERTER | ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU | 1) This field is required and Data type is numeric 2 Value must be greater than or equal to 0.0 and less than or equal to 99999.0 | R
Solar Photovoltaic (PV) | Grounding Reactance For An Impedance Grounded Inverter in p.u. (100 MVA Base) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | p.u. | INVERTER | ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU | 1) This field is required and Data type is numeric 2) Value must be greater than or equal to 0.0 and less than or equal to 99999.0 | R
Solar Photovoltaic (PV) | Instantaneous Controlled Fault Current Magnitude (Multiple of full Load current) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | p.u. | INVERTER | INST_CTRL_FAULT_CUR_MAG | 1) Value must be greater than or egual to 1 AND less than or equal to 5.8 2) Generate a warning if greater than or equal 3.5 | R
Solar Photovoltaic (PV) | Controlled Fault Current Magnitude At 2 to 3 cycles after fault (Multiple of full Load current) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | p.u. | INVERTER | CTRL_FAULT_CUR_MAG_TWO_THREE_CYCLES | 1) Value must be greater than or egual to 0.8 AND less than or equal to 3 2) Generate a warning if greater than or equal 1.8 or less than 1.0 | R
Solar Photovoltaic (PV) | Controlled Fault Current Magnitude At 4 plus cycles after fault (Multiple of full Load current) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | p.u. | INVERTER | CTRL_CTRL_FAULT_CUR_MAG_FOUR_PLUS_CYCLES | 1) Value must be greater than or egual to .45 AND less than or equal to 3 2) Generate a warning greater than or equal to 1.5 or less than 1.0 | R
Solar Photovoltaic (PV) | Skid/Array Transformer Rating |  | Added 5/1/2017 | Inverter Details - SOLAR |  | MVA | INVERTER | SKID_ARY_TRNS_RTG | 1) This field is required 2) Data type must be Numeric, Positive value (>=0.0) | R
Solar Photovoltaic (PV) | SKID/ARRAY TRANSFORMER DETAILS |  | Added 5/1/2017 | Inverter Details - SOLAR
Solar Photovoltaic (PV) | High Side Voltage Level (nominal) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | kV | INVERTER | HIGH_SIDE_VT_LEVL | 1) This field is required 2) Data type must be real 3) Generate an Error if not between 1 and 69 | R
Solar Photovoltaic (PV) | Low Side Voltage Level (nominal) |  | Added 5/1/2017 | Inverter Details - SOLAR |  | kV | INVERTER | LOW_SIDE_VT_LEVL | 1) This field is required 2) Data type must be real 3) Generate an Error if not > 0.0 and <= 1 kV | R
Solar Photovoltaic (PV) | High Side Voltage Connection |  | Added 5/1/2017 | Inverter Details - SOLAR |  | List | INVERTER | HIGH_SIDE_VT_CONNT | 1) This field is required 2) Data type must be from list (Wye, Wye - Grounded or Delta) 3) Generate an Error if blank | R
Solar Photovoltaic (PV) | Low Side Voltage Connection |  | Added 5/1/2017 | Inverter Details - SOLAR |  | List | INVERTER | LOW_SIDE_VT_CONNT | 1) This field is required 2) Data type must be from list (Wye, Wye - Grounded or Delta) 3) Generate an Error if blank | R
Solar Photovoltaic (PV) | Positive Sequence Impedance Z |  | Added 5/1/2017 | Inverter Details - SOLAR |  | p.u. | INVERTER | IMPEDANCE_Z | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0 | R
Solar Photovoltaic (PV) | Positive Sequence X/R Ratio |  | Added 5/1/2017 | Inverter Details - SOLAR |  |  | INVERTER | X_R_RATIO | 1) This field is required 2) Data type must be real 3) Generate an Error if < 1 | R
Solar Photovoltaic (PV) | Zero Sequence Impedance Z |  | Added 5/1/2017 | Inverter Details - SOLAR |  | p.u. | INVERTER | ZERO_SEQ_Z | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0 | R
Solar Photovoltaic (PV) | Zero Sequence X/R Ratio |  | Added 5/1/2017 | Inverter Details - SOLAR |  |  | INVERTER | ZERO_SEQ_X_R_RATIO | 1) This field is required 2) Data type must be real 3) Generate an Error if <= 1 | R
Solar Photovoltaic (PV) | Base MVA for Skid/Array Transformer Data |  | Added 5/1/2017 | Inverter Details - SOLAR |  | MVA | INVERTER | BASE_KV_SKID_ARY_TRANS | 1) This field is required 3) Generate an Error if blank. 4) Value must be greater than 0 "ERROR! MVABASE ( ) must be greater than 0 MVA" 5) Generate Warning if greater than 24 MVA "Warning! MVABASE ( ) is greater than 24.0 MVA, please enter the data on the Transformer Rated MVA base” | R
Solar Photovoltaic (PV) | PSSE MODELS : THE FOLLOWING FILES ARE REQUIRED TO BE SUBMITTED. PLEASE INCLUDE ALL PSSE FILES IN A ZIP OR COMPRESSED FOLDER IN THE DYNAMIC DATA TAB. |  | Added 5/1/2017 | Inverter Details - SOLAR |  |  | TURBINE | Not in table
Solar Photovoltaic (PV) | PSSE Compatible Wind Generator Models |  | Added 5/1/2017 | Inverter Details - SOLAR |  |  | Not in table | Not in table | [7 empty] | N | Y
Solar Photovoltaic (PV) | Dynamic Reactive Device Form |  | Added 5/1/2017 | Inverter Details - SOLAR |  |  | Not in table | Not in table | [7 empty] | N | Y
Solar Photovoltaic (PV) | Inverter Efficiency Curve |  | Added 5/1/2017 | Inverter Details - SOLAR |  |  | Not in table |  | Attach Inverter Efficiency Curve | R
Solar Photovoltaic (PV) | Panel Details - SOLAR |  |  | Panel Details - SOLAR |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | PANEL DETAILS |  |  | Panel Details - SOLAR |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | Panel Configuration Identifier |  | Added 5/1/2017 | Panel Details - SOLAR |  | List | Panel | PNL_CONFIG_ID | 1) This field is required 2. Should not allow spaces | R
Solar Photovoltaic (PV) | Tracking Type |  | Added 5/1/2017 | Panel Details - SOLAR |  | List | Panel | TRACKING_TYPE | 1) This field is required 2) Choice between "single axis" or "double axis" None, Azimuth only, Tilt Only, Azimuth and Tilt | R
Solar Photovoltaic (PV) | Plane of Array - Azimuth |  | Added 5/1/2017 | Panel Details - SOLAR |  | degrees | Panel | PLANE_ARY_AZIMUTH | 1) This field is required 2) Data type must be Numeric | R
Solar Photovoltaic (PV) | Plane of Array - Tilt |  | Added 5/1/2017 | Panel Details - SOLAR |  | degrees | Panel | PLANE_ARY_TILT | 1) This field is required 2) Data type must be Numeric | R
Solar Photovoltaic (PV) | Panel Manufacturer |  | Added 5/1/2017 | Panel Details - SOLAR |  | All Caps | Panel | PNL_MFG | 1) This field is required | R
Solar Photovoltaic (PV) | Panel Model |  | Added 5/1/2017 | Panel Details - SOLAR |  | All Caps | Panel | PNL_MDL | 1) This field is required | R
Solar Photovoltaic (PV) | Panel Area |  | Added 5/1/2017 | Panel Details - SOLAR |  | meters squared | Panel | PNL_AREA | 1) This field is required | R
Solar Photovoltaic (PV) | Panel Efficiency |  | Added 5/1/2017 | Panel Details - SOLAR |  | % | Panel | PNL_EFF | 1) This field is required 2) Data type must be Numeric | R
Solar Photovoltaic (PV) | Panel temperature Coefficient of power |  | Added 5/1/2017 | Panel Details - SOLAR |  | % / degrees C | Panel | PNL_TEMP_CO_PWR | 1) This field is required 2) Data type must be Numeric | R
Solar Photovoltaic (PV) | Nominal Operating Cell Temperature |  | Added 5/1/2017 | Panel Details - SOLAR |  | Degrees C | Panel | MPM_OPR_CELL_TEMP | 1) This field is required 2) Data type must be Numeric | R
Solar Photovoltaic (PV) | MW Rating for this Model of Panel |  | Added 5/1/2017 | Panel Details - SOLAR |  | MW | Panel | IPNL_MW_MDL_RTG | 1) This field is required 2) Data type must be Numeric, | R
Solar Photovoltaic (PV) | PVGR - Connectivity |  |  | PVGR Connectivity |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | Solar Generation Group Details |  |  | PVGR Connectivity |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | Resoure Name (Unit Code/Mnemonic) |  | Added 5/1/2017 | PVGR Connectivity |  |  | PVGR_CONNECTIVITY | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R
Solar Photovoltaic (PV) | PVGR Group |  | Added 5/1/2017 | PVGR Connectivity |  | # | PVGR_CONNECTIVITY | PVGR_GRP | 1) This field is optional. 2. Whole Number | R
Solar Photovoltaic (PV) | Group Code |  | Added 5/1/2017 | PVGR Connectivity |  | Automatic | PVGR_CONNECTIVITY | GRP_CODE | If PVGR_GRP is populated then Concantante UNIT_CODE_SKD_ARY_CONFIG_ID_PNL_CONFIG_ID_PVGR_GRP. | R
Solar Photovoltaic (PV) | Site_Group |  | Added 5/1/2017 | PVGR Connectivity |  | Automatic | PVGR_CONNECTIVITY | SITE_GRP | 1) This field is required only if PVGR_GRP is populated. | R
Solar Photovoltaic (PV) | Skid/Array Configuration Identifier |  | Added 5/1/2017 | PVGR Connectivity |  | List | PVGR_CONNECTIVITY | SKD_ARY_CONFIG_ID | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R
Solar Photovoltaic (PV) | Number of Skid/Arrays per skid/Array Configuration Identifier |  | Added 5/1/2017 | PVGR Connectivity |  | # | PVGR_CONNECTIVITY | NUM_SKID_ARY_PER_CONFIG | 1) This field is required 2. Whole Number | R
Solar Photovoltaic (PV) | Panel Configuration Identifier |  | Added 5/1/2017 | PVGR Connectivity |  | List | PVGR_CONNECTIVITY | PNL_CONFIG_ID | 1) This field is required | R
Solar Photovoltaic (PV) | Number of Panels per Panel Configuration |  | Added 5/1/2017 | PVGR Connectivity |  | # | PVGR_CONNECTIVITY | NUM_PNL_PER_CONFIG | 1) This field is required 2. Whole Number | R
Generation | Ownership-GEN |  |  | Ownership - GEN |  |  | Not in table | Not in table | This tab is conditional. Required if single entity represents the Resource. | C
Generation | GENERATOR DETAILS |  |  | Ownership - GEN |  |  | Not in table | Not in table
Generation | Unit Name | Do not show Message on Audit or Delta |  | Ownership - GEN |  | List | GENERATION | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | N
Generation | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code 05/17/2012 Update #3 validation |  | Ownership - GEN |  | List | OWNERSHIP | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | N
Generation | Ownership Percentages |  |  | Ownership - GEN |  |  | Not in table | Not in table
Generation | Joint Ownership? |  | ADDED 06/27/2012 | Ownership - GEN | Delta - GEN_Ownership.View Audit - Generation_Ownership.View | Y/N | OWNERSHIP | J0CODE | 1. Select from the list: Y or N 2. If N then Fixed Ownership 100% | R | Dropdown List |  |  |  |  | N | N
Generation | Resource Entity Name |  |  | Ownership - GEN |  |  | OWNERSHIP | MKT_PRTCPT | This field is conditional: Required if single entity represents the Resource. Data type: Character. Resource Entity Name should not allow any special characters except spaces. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | C | Character | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0 | EMS,Lodestar,NMMS |  | N | N
Generation | Resource Duns Number |  |  | Ownership - GEN |  | 9-13 digits | OWNERSHIP | MKT_PRTCPT_DUNS | This field is Conditional : Required if single entity represents the Resource. This should be either 9 or 13 digit number | C | Integer | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0 | EMS,Lodestar,NMMS |  | N | N
Generation | Fixed Ownership | 05/03/2012 removed percent from label on form |  | Ownership - GEN |  |  | OWNERSHIP | FIX_OWNRSHP_PCT | Sum of the Ownership percentage should be 0.0 to 1.. Up to 4 decimal places only are valid (limit submission to 4 places after the point) | C | Numeric | B,DVB | Lin Xu/Art Deller | EMS,Lodestar,MMS,NMMS |  | N | N
Generation | Master Owner |  |  | Ownership - GEN |  | Y/N | OWNERSHIP | MASTR_OWNR_FLG | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 | EMS,Lodestar,NMMS |  | N | N
Generation | Ownership Start Date | 04/09/2012 Changed Validation to be an Optional | ADDED 06/27/2012 | Ownership - GEN | Delta - GEN_Ownership.View Audit - Generation_Ownership.View | mm/dd/yyyy | OWNERSHIP | OWNR_START_DT | Format should be: MM/DD/YYYY | R | Date | B/DVB | Data Ag |  |  | N | N
Generation | Ownership Stop Date |  | ADDED 06/27/2012 | Ownership - GEN | Delta - GEN_Ownership.View Audit - Generation_Ownership.View | mm/dd/yyyy | OWNERSHIP | OWNR_END_DT | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB | Data Ag |  |  | N | N
CC | Ownership-CC |  |  | Ownership - CC |  |  | Not in table | Not in table | This Section is conditional. Required for only Combined Cycle generation resources. Required if Resource Entity represents 100% of all units. | C
CC | GENERATOR DETAILS |  |  | Ownership - CC |  |  | Not in table | Not in table | This Section is conditional. Required for only Combined Cycle generation resources. Required if Resource Entity represents 100% of all units. | C
CC | Train Name |  |  | Ownership - CC |  | List | TRAIN | TRAIN_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | N
CC | Train Code | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code 05/18/2012 Corrected Validation Code Corrected 02/23/2012 |  | Ownership - CC |  | Automatic | OWNERSHIP | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | N |  |  |  | This is filled automatically in the form, why is there any validation?
CC | Resource Entity Name |  |  | Ownership - CC | CC_Ownership.View |  | OWNERSHIP | MKT_PRTCPT | This field is conditional. Required if Resource Entity represents 100% of all units. Resource Entity Name should not allow any special characters except spaces | C | Character | B | RARF Guide Version 4.0 | Lodestar,NMMS |  | N | N
CC | Resource Duns Number |  |  | Ownership - CC | CC_Ownership.View | 9-13 digits | OWNERSHIP | MKT_PRTCPT_DUNS | This field is conditional. Required if Resource Entity represents 100% of all units. | C | Numeric | B,DVE | RARF Guide Version 4.0 | Lodestar,NMMS |  | N | N
CC | Fixed Ownership | 05/03/2012 removed percent from label on form |  | Ownership - CC |  |  | OWNERSHIP | FIX_OWNRSHP_PCT | This field is conditional. Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. Data type: character. | C | Character | B,DVB | RARF Guide Version 4.0 | EMS,Lodestar,NMMS |  | N | N
CC | Master Owner | 05/18/2012 Corrected Validation |  | Ownership - CC |  | Y/N | OWNERSHIP | MASTR_OWNR_FLG | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | C | Integer | B,DVB | RARF Guide Version 4.0/Angela Moy | EMS,Lodestar,NMMS |  | N | N
CC | Ownership Start Date | 04/09/2012 Changed Validation to be an Optional | ADDED 06/27/2012 | Ownership - CC | CC_Ownership.View | mm/dd/yyyy | OWNERSHIP | OWNR_START_DT | Format should be: MM/DD/YYYY | R | Date | B/DVB | Data Ag |  |  | N | N
CC | Ownership Stop Date |  | ADDED 06/27/2012 | Ownership - CC | CC_Ownership.View | mm/dd/yyyy | OWNERSHIP | OWNR_END_DT | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB | Data Ag |  |  | N | N
RENEWABLE | Ownership - RENEWABLE ENERGY |  |  | Ownership - RENEWABLE |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type selected is 'WIND ' | C |  |  | RARF Guide Version 4.0
RENEWABLE | GENERATOR DETAILS |  |  | Ownership - RENEWABLE |  |  | Not in table | Not in table
RENEWABLE | Unit Name | Do not show Message on Audit or Delta | Added 5/1/2017 | Ownership - RENEWABLE |  | List | RENEWABLE | UNIT_NAME | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | N
RENEWABLE | Resource Name (Unit Code/Mnemonic) |  | Added 5/1/2017 | Ownership - RENEWABLE |  | Automatic | OWNERSHIP & SITECODES | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | N
RENEWABLE | OWNERSHIP PERCENTAGES |  |  | Ownership - RENEWABLE |  |  | Not in table | Not in table
RENEWABLE | Joint Ownership? |  | ADDED 06/27/2012 | Ownership - RENEWABLE | WIND_Ownership.View | Y/N | OWNERSHIP | J0CODE | 1. Select from the list: Y or N 2. If N then Fixed Ownership 100% | R | Dropdown List |  |  |  |  | N | N
RENEWABLE | Resource Entity Name |  | Added 5/1/2017 | Ownership - RENEWABLE |  |  | OWNERSHIP | MKT_PRTCPT | This field is conditional: Required if single entity represents the Resource. Data type: Character. Resource Entity Name should not allow any special characters except spaces. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | C | Character | B,DVB | RARF Guide Version 4.0 | Lodestar,NMMS |  | N | N
RENEWABLE | Resource Duns Number |  | Added 5/1/2017 | Ownership - RENEWABLE |  | 9-13 digits | OWNERSHIP | MKT_PRTCPT_DUNS | This field is Conditional : Required if single entity represents the Resource. This should be either 9 or 13 digit number | C | Integer | B,DVE | RARF Guide Version 4.0 | Lodestar,NMMS |  | N | N
RENEWABLE | Fixed Ownership |  | Added 5/1/2017 | Ownership - RENEWABLE |  |  | OWNERSHIP | FIX_OWNRSHP_PCT | Sum of the Ownership percentage should be 0.0 to 1. Up to 4 decimal places are valid (limit submission to 4 places after the point) | C | Numeric | B,DVB | RARF Guide Version 4.0 | EMS,Lodestar,MMS,NMMS |  | N | N
RENEWABLE | Master Owner |  | Added 5/1/2017 | Ownership - RENEWABLE |  | Y/N | OWNERSHIP | MASTR_OWNR_FLG | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | R | Dropdown List | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0 | EMS,Lodestar,NMMS |  | N | N
RENEWABLE | Ownership Start Date |  | ADDED 06/27/2012 | Ownership - RENEWABLE | WIND_Ownership.View | mm/dd/yyyy | OWNERSHIP | OWNR_START_DT | Format should be: MM/DD/YYYY | O | Date | B/DVB | Data Ag |  |  | N | N
RENEWABLE | Ownership Stop Date |  | ADDED 06/27/2012 | Ownership - RENEWABLE | WIND_Ownership.View | mm/dd/yyyy | OWNERSHIP | OWNR_END_DT | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB | Data Ag |  |  | N | N
Generation | Parameters - GEN |  |  | Parameters - GEN |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type Selected is 'GEN' where GEN is non-CC non-wind Generation Resources. | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,MMS,NMMS
Generation | GENERATOR DETAILS |  |  | Parameters - GEN |  |  | Not in table | Not in table
Generation | Unit Name | Do not show Message on Audit or Delta |  | Parameters - GEN |  | List | Generation | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | N
Generation | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code 05/17/2012 Update #3 validation 04/23/2012 Updated Table to DERATING_GEN | ADDED 06/27/2012 | Parameters - GEN | Parameters_GEN.View | Automatic | GENERATION & DERATING_GEN | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | N
Generation | REASONABILITY LIMITS |  |  | Parameters - GEN |  |  | Not in table | Not in table
Generation | High Reasonability Limit |  | UPDATED 03/2012 | Parameters - GEN |  | MW | Generation | HR_LMT | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Generation | Low Reasonability Limit |  | UPDATED 03/2012 | Parameters - GEN |  | MW | Generation | LR_LMT | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Generation | High Reasonability Ramp Rate Limit |  | UPDATED 03/2012 | Parameters - GEN |  | MW/min | Generation | HR_RAMPRATE_LMT | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS |  | N | N
Generation | Low Reasonability Ramp Rate Limit |  | UPDATED 03/2012 | Parameters - GEN |  | MW/min | Generation | LR_RAMP_RATE_LMT | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS |  | N | N
Generation | SEASONAL RATINGS - SPRING |  |  | Parameters - GEN |  |  | Not in table | Not in table
Generation | Seasonal Net Max Sustainable Rating - Spring |  | UPDATED 03/2012 | Parameters - GEN |  | MW | Generation | SEASON_NET_MAX_SUST_RTG_SP | 1.Seasonal Net Max Sustainable Rating - Spring >= Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS |  | N | N
Generation | Seasonal Net Min Sustainable Rating - Spring |  | UPDATED 03/2012 | Parameters - GEN |  | MW | Generation | SEASON_NET_MIN_SUST_RTG_SP | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS |  | N | N
Generation | Seasonal Net Max Emergency Rating - Spring |  | UPDATED 03/2012 | Parameters - GEN |  | MW | Generation | SEASON_NET_MAX_EMGY_RTG_SP | 1.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS |  | N | N
Generation | Seasonal Net Min Emergency Rating - Spring |  | UPDATED 03/2012 | Parameters - GEN |  | MW | Generation | SEASON_NET_MIN_EMGY_RTG_SP | 1.Seasonal Net Min Emergency Rating - Spring < = Seasonal Net Min Sustainable Rating - Spring. 2.Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS |  | N | N
Generation | SEASONAL RATINGS - SUMMER |  |  | Parameters - GEN |  |  | Not in table | Not in table
Generation | Seasonal Net Max Sustainable Rating - Summer |  | UPDATED 03/2012 | Parameters - GEN |  | MW | Generation | SEASON_NET_MAX_SUST_RTG_SM | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS |  | N | N
Generation | Seasonal Net Min Sustainable Rating - Summer |  | UPDATED 03/2012 | Parameters - GEN |  | MW | Generation | SEASON_NET_MIN_SUST_RTG_SM | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu | MMS |  | N | N
Generation | Seasonal Net Max Emergency Rating - Summer |  | UPDATED 03/2012 | Parameters - GEN |  | MW | Generation | SEASON_NET_MAX_EMGY_RTG_SM | 1.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS |  | N | N
Generation | Seasonal Net Min Emergency Rating - Summer |  | UPDATED 03/2012 | Parameters - GEN |  | MW | Generation | SEASON_NET_MIN_EMGY_RTG_SM | 1.Seasonal Net Min Emergency Rating - Summer < = Seasonal Net Min Sustainable Rating - Summer. 2.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS |  | N | N
Generation | SEASONAL RATINGS - FALL |  |  | Parameters - GEN |  |  | Not in table | Not in table
Generation | Seasonal Net Max Sustainable Rating - Fall |  | UPDATED 03/2012 | Parameters - GEN |  | MW | Generation | SEASON_NET_MAX_SUST_RTG_FL | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS |  | N | N
Generation | Seasonal Net Min Sustainable Rating - Fall |  | UPDATED 03/2012 | Parameters - GEN |  | MW | Generation | SEASON_NET_MIN_SUST_RTG_FL | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Min Sustainable Rating - Fall. >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS |  | N | N
Generation | Seasonal Net Max Emergency Rating - Fall |  | UPDATED 03/2012 | Parameters - GEN |  | MW | Generation | SEASON_NET_MAX_EMGY_RTG_FL | 1.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS |  | N | N
Generation | Seasonal Net Min Emergency Rating - Fall |  | UPDATED 03/2012 | Parameters - GEN |  | MW | Generation | SEASON_NET_MIN_EMGY_RTG_FL | 1.Seasonal Net Min Emergency Rating - Fall < = Seasonal Net Min Sustainable Rating - Fall. 12.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS |  | N | N
Generation | SEASONAL RATINGS - WINTER |  |  | Parameters - GEN |  |  | Not in table | Not in table
Generation | Seasonal Net Max Sustainable Rating - Winter |  | UPDATED 03/2012 | Parameters - GEN |  | MW | Generation | SEASON_NET_MAX_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS |  | N | N
Generation | Seasonal Net Min Sustainable Rating - Winter |  | UPDATED 03/2012 | Parameters - GEN |  | MW | Generation | SEASON_NET_MIN_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Sustainable Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS |  | N | N
Generation | Seasonal Net Max Emergency Rating - Winter |  | UPDATED 03/2012 | Parameters - GEN |  | MW | Generation | SEASON_NET_MAX_EMGY_RTG_WT | 1.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS |  | N | N
Generation | Seasonal Net Min Emergency Rating - Winter |  | UPDATED 03/2012 | Parameters - GEN |  | MW | Generation | SEASON_NET_MIN_EMGY_RTG_WT | 1.Seasonal Net Min Emergency Rating - Winter< = Seasonal Net Min Sustainable Rating - Winter. 12.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS |  | N | N
Generation | STEAM TURBINE PRESSURE CURVE | Updated RARF for NERC-BAL-TRE 001 Regional Standard | 12/1/2014 Added new Field | Parameters - GEN |  |  | Not in table | Not in table | This is conditional. Required if the Generation Type Selected is 'GEN' where Physical Unit Type is 'ST' and Resource Category is 'Gas Steam - Non-reheat or Boiler without air-preheater, Gas Steam - Reheat Boiler, Gas Steam - Supercritical Boiler or Coal and Lignite. | C | [5 empty] | N | N
Generation | MW1 | Updated RARF for NERC-BAL-TRE 001 Regional Standard | 12/1/2014 Added new Field | Parameters - GEN | Parameters_GEN.View | MW | Generation | STPC_MW1 | 1. MW1 Must Not be Null if Physical Unit is 'ST' and Resource Category is 'Gas Steam - Non-reheat or Boiler without air-preheater, Gas Steam - Reheat Boiler, Gas Steam - Supercritical Boiler or Coal and Lignite' . 2. MW1 must be a floating point. 3. MWH => MW1 => MWL where, MWH = HRL MWL = Max(MW2*, MW3*, MW4*, MW5*, MW6, LRL) ( (* do not include in computation if null) ) | C | Numeric | B,DVB | OPS PLANNING | EMS, NMMS |  | N | N
Generation | PSI1 | Updated RARF for NERC-BAL-TRE 001 Regional Standard | 12/1/2014 Added new Field | Parameters - GEN | Parameters_GEN.View | PSI | Generation | PSI1 | 1. PSI1 must be a floating point. 2. If MW1 is non-null then PSI1 must be non-null. | C | Numeric | B,DVB | OPS PLANNING | EMS, NMMS |  | N | N
Generation | MW2 | 11/13/2014 Added validation rule #2. Updated RARF for NERC-BAL-TRE 001 Regional Standard | 12/1/2014 Added new Field | Parameters - GEN | Parameters_GEN.View | MW | Generation | STPC_MW2 | 1. MW2 must be a floating point. 2. If PSI2 is non-null then MW2 must be non-null. 3. If MW2 is non-null, MWH => MW2 => MWL where, MWH = Min (HRL, MW1) MWL = Max(MW3*, MW4*, MW5*, MW6, LRL) ( (* do not include in computation if null) ) | C/O | Numeric | B,DVB | OPS PLANNING | EMS, NMMS |  | N | N
Generation | PSI2 | Updated RARF for NERC-BAL-TRE 001 Regional Standard | 12/1/2014 Added new Field | Parameters - GEN | Parameters_GEN.View | PSI | Generation | PSI2 | 1. PSI2 must be a floating point. 2. If PSI2 is non-null then MW2 must be non-null. | C/O | Numeric | B,DVB | OPS PLANNING | EMS, NMMS |  | N | N
Generation | MW3 | 11/13/2014 Added validation rule #2. Updated RARF for NERC-BAL-TRE 001 Regional Standard | 12/1/2014 Added new Field | Parameters - GEN | Parameters_GEN.View | MW | Generation | STPC_MW3 | 1. MW3 must be a floating point. 2. If PSI3 is non-null then MW3 must be non-null. 3. If MW3 is non-null, MWH => MW3 => MWL where, MWH = Min (HRL, MW1, MW2*) ( (* do not include in computation if null) ) MWL = Max(MW4*, MW5*, MW6, LRL) ( (* do not include in computation if null) ) | C/O | Numeric | B,DVB | OPS PLANNING | EMS, NMMS |  | N | N
Generation | PSI3 | Updated RARF for NERC-BAL-TRE 001 Regional Standard | 12/1/2014 Added new Field | Parameters - GEN | Parameters_GEN.View | PSI | Generation | PSI3 | 1. PSI3 must be a floating point. 2. If MW3 is non-null then PSI3 must be non-null. | C/O | Numeric | B,DVB | OPS PLANNING | EMS, NMMS |  | N | N
Generation | MW4 | 11/13/2014 Added validation rule #2. Updated RARF for NERC-BAL-TRE 001 Regional Standard | 12/1/2014 Added new Field | Parameters - GEN | Parameters_GEN.View | MW | Generation | STPC_MW4 | 1. MW4 must be a floating point. 2. If PSI4 is non-null then MW4 must be non-null. 3. If MW4 is non-null, MWH => MW4 => MWL where, MWH = Min (HRL, MW1, MW2*, MW3*) ( (* do not include in computation if null) ) MWL = Max(MW5*, MW6, LRL) ( (* do not include in computation if null) ) | C/O | Numeric | B,DVB | OPS PLANNING | EMS, NMMS |  | N | N
Generation | PSI4 | Updated RARF for NERC-BAL-TRE 001 Regional Standard | 12/1/2014 Added new Field | Parameters - GEN | Parameters_GEN.View | PSI | Generation | PSI4 | 1. PSI4 must be a floating point. 2. If MW4 is non-null then PSI4 must be non-null. | C/O | Numeric | B,DVB | OPS PLANNING | EMS, NMMS |  | N | N
Generation | MW5 | 11/13/2014 Added validation rule #2. Updated RARF for NERC-BAL-TRE 001 Regional Standard | 12/1/2014 Added new Field | Parameters - GEN | Parameters_GEN.View | MW | Generation | STPC_MW5 | 1. MW5 must be a floating point. 2. If PSI5 is non-null then MW5 must be non-null. 3. If MW5 is non-null, MWH => MW5 => MWL where, MWH = Min (HRL, MW1, MW2*, MW3*, MW4*) ( (* do not include in computation if null) ) MWL = Max(MW6, LRL) | C/O | Numeric | B,DVB | OPS PLANNING | EMS, NMMS |  | N | N
Generation | PSI5 | Updated RARF for NERC-BAL-TRE 001 Regional Standard | 12/1/2014 Added new Field | Parameters - GEN | Parameters_GEN.View | PSI | Generation | PSI5 | 1. PSI5 must be a floating point. 2. If MW5 is non-null then PSI5 must be non-null. | C/O | Numeric | B,DVB | OPS PLANNING | EMS, NMMS |  | N | N
Generation | MW6 | Updated RARF for NERC-BAL-TRE 001 Regional Standard | 12/1/2014 Added new Field | Parameters - GEN | Parameters_GEN.View | MW | Generation | STPC_MW6 | 1. MW6 Must Not Be Null if Physical Unit is 'ST' and Resource Category is 'Gas Steam - Non-reheat or Boiler without air-preheater, Gas Steam - Reheat Boiler, Gas Steam - Supercritical Boiler or Coal and Lignite' . 2. MW6 must be a floating point. 3. MWH => MW6 => MWL where, MWH = Min (HRL, MW1, MW2*, MW3*, MW4*, MW5*) ( (* do not include in computation if null) ) MWL = LRL | C | Numeric | B,DVB | OPS PLANNING | EMS, NMMS |  | N | N
Generation | PSI6 | Updated RARF for NERC-BAL-TRE 001 Regional Standard | 12/1/2014 Added new Field | Parameters - GEN | Parameters_GEN.View | PSI | Generation | PSI6 | 1. PSI6 must be a floating point. 2. If MW6 is non-null then PSI6 must be non-null. | C | Numeric | B,DVB | OPS PLANNING | EMS, NMMS |  | N | N
Generation | Limiting K Factor | Updated RARF for NERC-BAL-TRE 001 Regional Standard | 12/1/2014 Added new Field | Parameters - GEN | Parameters_GEN.View | PSIG/MW | Generation | K_FACTOR | 1.K_FACTOR Must Not be Null if Physical Unit is 'ST' and Resource Category is 'Gas Steam - Non-reheat or Boiler without air-preheater, Gas Steam - Reheat Boiler, Gas Steam - Supercritical Boiler or Coal and Lignite' . 2. K Factor must be a floating point with default 0.0 3. 0.0 =< K =< 0.6 | C | Numeric | B,DVB | OPS PLANNING | EMS, NMMS |  | N | N
CC | Parameters - CC |  |  | Parameters - CC |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type selected is 'CC'. Can register up to 3 trains at one site. | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | MMS,NMMS
CC | GENERATOR DETAILS |  |  | Parameters - CC |  |  | Not in table | Not in table
CC | Unit Name | Do not show Message on Audit or Delta |  | Parameters - CC |  | List | CCUNIT | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | N
CC | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code 05/17/2012 Update #3 validation |  | Parameters - CC |  | List | CCUNIT & DERATING_CC | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | N
CC | REASONABILITY LIMITS |  |  | Parameters - CC |  |  | Not in table | Not in table
CC | High Reasonability Limit | 05/04/2012 added Validation (4. Generate a warning if HRL (NET) is greater than Real Power Rating(Gross)). 04/23/2012 Updated Table to DERATING_GEN |  | Parameters - CC |  | MW | CCUNIT | HR_LMT | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit 4. Generate a warning if HRL (NET) is greater than Real Power Rating(Gross). | R | Numeric | B,DVB | KitteiPong/Jamil Daouk | EMS,MMS,NMMS |  | N | N
CC | Low Reasonability Limit |  | UPDATED 03/2012 | Parameters - CC |  | MW | CCUNIT | LR_LMT | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | Numeric | B,DVB | KitteiPong/Lin Xu/ Jamil Daouk, Kenneth Ragsdale | EMS,MMS,NMMS |  | N | N
CC | High Reasonability Ramp Rate Limit |  | UPDATED 03/2012 | Parameters - CC |  | MW/min | CCUNIT | HR_RAMPRATE_LMT | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS |  | N | N
CC | Low Reasonability Ramp Rate Limit |  | UPDATED 03/2012 | Parameters - CC |  | MW/min | CCUNIT | LR_RAMP_RATE_LMT | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS |  | N | N
CC | SEASONAL RATINGS - SPRING |  |  | Parameters - CC |  |  | Not in table | Not in table
CC | Seasonal Net Max Sustainable Rating - Spring |  | UPDATED 03/2012 | Parameters - CC |  | MW | CCUNIT | SEASON_NET_MAX_SUST_RTG_SP | 1.Seasonal Net Max Sustainable Rating - Spring >= Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS |  | N | N
CC | Seasonal Net Min Sustainable Rating - Spring |  | UPDATED 03/2012 | Parameters - CC |  | MW | CCUNIT | SEASON_NET_MIN_SUST_RTG_SP | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS |  | N | N
CC | Seasonal Net Max Emergency Rating - Spring |  | UPDATED 03/2012 | Parameters - CC |  | MW | CCUNIT | SEASON_NET_MAX_EMGY_RTG_SP | 1.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS |  | N | N
CC | Seasonal Net Min Emergency Rating - Spring |  | UPDATED 03/2012 | Parameters - CC |  | MW | CCUNIT | SEASON_NET_MIN_EMGY_RTG_SP | 1.Seasonal Net Min Emergency Rating - Spring < = Seasonal Net Min Sustainable Rating - Spring. 2.Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS |  | N | N
CC | SEASONAL RATINGS - SUMMER |  |  | Parameters - CC |  |  | Not in table | Not in table
CC | Seasonal Net Max Sustainable Rating - Summer |  | UPDATED 03/2012 | Parameters - CC |  | MW | CCUNIT | SEASON_NET_MAX_SUST_RTG_SM | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS |  | N | N
CC | Seasonal Net Min Sustainable Rating - Summer |  | UPDATED 03/2012 | Parameters - CC |  | MW | CCUNIT | SEASON_NET_MIN_SUST_RTG_SM | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS |  | N | N
CC | Seasonal Net Max Emergency Rating - Summer |  | UPDATED 03/2012 | Parameters - CC |  | MW | CCUNIT | SEASON_NET_MAX_EMGY_RTG_SM | 1.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS |  | N | N
CC | Seasonal Net Min Emergency Rating - Summer |  | UPDATED 03/2012 | Parameters - CC |  | MW | CCUNIT | SEASON_NET_MIN_EMGY_RTG_SM | 1.Seasonal Net Min Emergency Rating - Summer < = Seasonal Net Min Sustainable Rating - Summer. 2.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS |  | N | N
CC | SEASONAL RATINGS - FALL |  |  | Parameters - CC |  |  | Not in table | Not in table
CC | Seasonal Net Max Sustainable Rating - Fall |  | UPDATED 03/2012 | Parameters - CC |  | MW | CCUNIT | SEASON_NET_MAX_SUST_RTG_FL | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS |  | N | N
CC | Seasonal Net Min Sustainable Rating - Fall |  | UPDATED 03/2012 | Parameters - CC |  | MW | CCUNIT | SEASON_NET_MIN_SUST_RTG_FL | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Min Sustainable Rating - Fall. >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS |  | N | N
CC | Seasonal Net Max Emergency Rating - Fall |  | UPDATED 03/2012 | Parameters - CC |  | MW | CCUNIT | SEASON_NET_MAX_EMGY_RTG_FL | 1.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS |  | N | N
CC | Seasonal Net Min Emergency Rating - Fall |  | UPDATED 03/2012 | Parameters - CC |  | MW | CCUNIT | SEASON_NET_MIN_EMGY_RTG_FL | 1.Seasonal Net Min Emergency Rating - Fall < = Seasonal Net Min Sustainable Rating - Fall. 12.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS |  | N | N
CC | SEASONAL RATINGS - WINTER |  |  | Parameters - CC |  |  | Not in table | Not in table
CC | Seasonal Net Max Sustainable Rating - Winter |  | UPDATED 03/2012 | Parameters - CC |  | MW | CCUNIT | SEASON_NET_MAX_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS |  | N | N
CC | Seasonal Net Min Sustainable Rating - Winter |  | UPDATED 03/2012 | Parameters - CC |  | MW | CCUNIT | SEASON_NET_MIN_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Sustainable Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS |  | N | N
CC | Seasonal Net Max Emergency Rating - Winter |  | UPDATED 03/2012 | Parameters - CC |  | MW | CCUNIT | SEASON_NET_MAX_EMGY_RTG_WT | 1.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS |  | N | N
CC | Seasonal Net Min Emergency Rating - Winter |  | UPDATED 03/2012 | Parameters - CC |  | MW | CCUNIT | SEASON_NET_MIN_EMGY_RTG_WT | 1.Seasonal Net Min Emergency Rating - Winter< = Seasonal Net Min Sustainable Rating - Winter. 12.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS |  | N | N
CC | Parameters - GEN |  |  | Parameters - CFG |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type selected is 'CC'. This tab is required for Configurations. | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,MMS,NMMS
CC | GENERATOR DETAILS |  |  | Parameters - CFG |  |  | Not in table | Not in table
CC | SITECODE |  |  | Parameters - CFG |  | List | CONFIGURATIONS | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R | [5 empty] | N | N
CC | Train Code | Corrected 02/23/2012 |  | Parameters - CFG |  | List | TRAIN | TRAIN_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N | N
CC | Configuration Code | 04/23/2012 Updated Table to DERATING_CFG |  | Parameters - CFG |  | List | CONFIGURATIONS & DERATING_CFG | CONFIG_CODE | Required | R | [5 empty] | N | N
CC | REASONABILITY LIMITS |  |  | Parameters - CFG |  |  | Not in table | Not in table
CC | High Reasonability Limit | 05/04/2012 removed Validation (4. Generate a warning if HRL (NET) is greater than Real Power Rating(Gross)). PHASE II Updated 03/06/2012 Added Step 4 and 5 | UPDATED 03/2012 | Parameters - CFG |  | MW | CONFIGURATIONS | HR_LMT | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit 4. Sum (HRL) of PRIMARY physical CCU component within the combined cycle configuration must be greater than or equal to the HRL of configuration itself. | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS |  | N | N
CC | Low Reasonability Limit |  | UPDATED 03/2012 | Parameters - CFG |  | MW | CONFIGURATIONS | LR_LMT | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS |  | N | N
CC | High Reasonability Ramp Rate Limit |  | UPDATED 03/2012 | Parameters - CFG |  | MW/min | CONFIGURATIONS | HR_RAMPRATE_LMT | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | EMS,MMS,NMMS |  | N | N
CC | Low Reasonability Ramp Rate Limit |  | UPDATED 03/2012 | Parameters - CFG |  | MW/min | CONFIGURATIONS | LR_RAMP_RATE_LMT | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | EMS,MMS,NMMS |  | N | N
CC | SEASONAL RATINGS - SPRING |  |  | Parameters - CFG |  |  | Not in table | Not in table
CC | Seasonal Net Max Sustainable Rating - Spring |  | UPDATED 03/2012 | Parameters - CFG |  | MW | CONFIGURATIONS | SEASON_NET_MAX_SUST_RTG_SP | 1.Seasonal Net Max Sustainable Rating - Spring >= Seasonal Net Min Sustainable Rating - Spring. 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS,NMMS |  | N | N
CC | Seasonal Net Min Sustainable Rating - Spring |  | UPDATED 03/2012 | Parameters - CFG |  | MW | CONFIGURATIONS | SEASON_NET_MIN_SUST_RTG_SP | 1.Seasonal Net Max Sustainable Rating - Spring > Seasonal Net Min Sustainable Rating - Spring 21.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 32.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS,NMMS |  | N | N
CC | Seasonal Net Max Emergency Rating - Spring |  | UPDATED 03/2012 | Parameters - CFG |  | MW | CONFIGURATIONS | SEASON_NET_MAX_EMGY_RTG_SP | 1.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS,NMMS |  | N | N
CC | Seasonal Net Min Emergency Rating - Spring |  | UPDATED 03/2012 | Parameters - CFG |  | MW | CONFIGURATIONS | SEASON_NET_MIN_EMGY_RTG_SP | 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring. 21.Seasonal Net Min Emergency Rating - Spring < = Seasonal Net Min Sustainable Rating - Spring. 32.Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS,NMMS |  | N | N
CC | SEASONAL RATINGS - SUMMER |  |  | Parameters - CFG |  |  | Not in table | Not in table
CC | Seasonal Net Max Sustainable Rating - Summer |  | UPDATED 03/2012 | Parameters - CFG |  | MW | CONFIGURATIONS | SEASON_NET_MAX_SUST_RTG_SM | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer. 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS |  | N | N
CC | Seasonal Net Min Sustainable Rating - Summer |  | UPDATED 03/2012 | Parameters - CFG |  | MW | CONFIGURATIONS | SEASON_NET_MIN_SUST_RTG_SM | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS |  | N | N
CC | Seasonal Net Max Emergency Rating - Summer |  | UPDATED 03/2012 | Parameters - CFG |  | MW | CONFIGURATIONS | SEASON_NET_MAX_EMGY_RTG_SM | 1.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3.Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS |  | N | N
CC | Seasonal Net Min Emergency Rating - Summer |  | UPDATED 03/2012 | Parameters - CFG |  | MW | CONFIGURATIONS | SEASON_NET_MIN_EMGY_RTG_SM | 1.Seasonal Net Max Emergency Rating - Summer > Seasonal Net Min Emergency Rating - Summer 21.Seasonal Net Min Emergency Rating - Summer < = Seasonal Net Min Sustainable Rating - Summer. 32.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS |  | N | N
CC | SEASONAL RATINGS - FALL |  |  | Parameters - CFG |  |  | Not in table | Not in table
CC | Seasonal Net Max Sustainable Rating - Fall |  | UPDATED 03/2012 | Parameters - CFG |  | MW | CONFIGURATIONS | SEASON_NET_MAX_SUST_RTG_FL | 1.Seasonal Net Max Sustainable Rating - Fall > =Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS |  | N | N
CC | Seasonal Net Min Sustainable Rating - Fall |  | UPDATED 03/2012 | Parameters - CFG |  | MW | CONFIGURATIONS | SEASON_NET_MIN_SUST_RTG_FL | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall | R | Numeric | B,DVB | Lin Xu | MMS |  | N | N
CC | Seasonal Net Max Emergency Rating - Fall |  | UPDATED 03/2012 | Parameters - CFG |  | MW | CONFIGURATIONS | SEASON_NET_MAX_EMGY_RTG_FL | 1.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Min Emergency Rating - Fall. 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS |  | N | N
CC | Seasonal Net Min Emergency Rating - Fall |  | UPDATED 03/2012 | Parameters - CFG |  | MW | CONFIGURATIONS | SEASON_NET_MIN_EMGY_RTG_FL | 1.Seasonal Net Max Emergency Rating - Fall > Seasonal Net Min Emergency Rating - Fall. 21.Seasonal Net Min Emergency Rating - Fall < = Seasonal Net Min Sustainable Rating - Fall. 32.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS |  | N | N
CC | SEASONAL RATINGS - WINTER |  |  | Parameters - CFG |  |  | Not in table | Not in table
CC | Seasonal Net Max Sustainable Rating - Winter |  | UPDATED 03/2012 | Parameters - CFG |  | MW | CONFIGURATIONS | SEASON_NET_MAX_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS |  | N | N
CC | Seasonal Net Min Sustainable Rating - Winter |  | UPDATED 03/2012 | Parameters - CFG |  | MW | CONFIGURATIONS | SEASON_NET_MIN_SUST_RTG_WT | 1.Seasonal Net Max Emergency Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall. 2.Seasonal Net Min Emergency Suatainable Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS |  | N | N
CC | Seasonal Net Max Emergency Rating - Winter |  | UPDATED 03/2012 | Parameters - CFG |  | MW | CONFIGURATIONS | SEASON_NET_MAX_EMGY_RTG_WT | 1.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Min Emergency Rating - Winter. 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS |  | N | N
CC | Seasonal Net Min Emergency Rating - Winter |  | UPDATED 03/2012 | Parameters - CFG |  | MW | CONFIGURATIONS | SEASON_NET_MIN_EMGY_RTG_WT | 1.Seasonal Net Max Emergency Rating - Winter > Seasonal Net Min Emergency Rating - Winter. 21.Seasonal Net Min Emergency Rating - Winter < = Seasonal Net Min Sustainable Rating - Winter. 32.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS |  | N | N
Wind | Parameters - RENEWABLE |  |  | Parameters - RENEWABLE |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type selected is 'WIND ' | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,MMS,NMMS
Wind | GENERATOR DETAILS |  |  | Parameters - RENEWABLE |  |  | Not in table | Not in table
Wind | Unit Name | Do not show Message on Audit or Delta |  | Parameters - RENEWABLE |  | List | RENEWABLE | UNIT_NAME | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | N
Wind | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code 04/23/2012 Updated Table to DERATING_WIND |  | Parameters - RENEWABLE |  | Automatic | Renewable & DERATING_Renewable | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | N
Wind | REASONABILITY LIMITS |  |  | Parameters - RENEWABLE |  |  | Not in table | Not in table
Wind | High Reasonability Limit |  | UPDATED 03/2012 | Parameters - RENEWABLE |  | MW | RENEWABLE | HR_LMT | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS |  | N | N
Wind | Low Reasonability Limit |  | UPDATED 03/2012 | Parameters - RENEWABLE |  | MW | RENEWABLE | LR_LMT | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS |  | N | N
Wind | High Reasonability Ramp Rate Limit |  | UPDATED 03/2012 | Parameters - RENEWABLE |  | MW/min | RENEWABLE | HR_RAMPRATE_LMT | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | EMS,MMS,NMMS |  | N | N
Wind | Low Reasonability Ramp Rate Limit |  | UPDATED 03/2012 | Parameters - RENEWABLE |  | MW/min | RENEWABLE | LR_RAMP_RATE_LMT | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | EMS,MMS,NMMS |  | N | N
Wind | SEASONAL RATINGS - SPRING |  |  | Parameters - RENEWABLE |  |  | Not in table | Not in table
Wind | Seasonal Net Max Sustainable Rating - Spring |  | UPDATED 03/2012 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MAX_SUST_RTG_SP | 1.Seasonal Net Max Sustainable Rating - Spring >= Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS |  | N | N
Wind | Seasonal Net Min Sustainable Rating - Spring |  | UPDATED 03/2012 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MIN_SUST_RTG_SP | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS |  | N | N
Wind | Seasonal Net Max Emergency Rating - Spring |  | UPDATED 03/2012 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MAX_EMGY_RTG_SP | 1.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS |  | N | N
Wind | Seasonal Net Min Emergency Rating - Spring |  | UPDATED 03/2012 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MIN_EMGY_RTG_SP | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS |  | N | N
Wind | SEASONAL RATINGS - SUMMER |  |  | Parameters - RENEWABLE |  |  | Not in table | Not in table
Wind | Seasonal Net Max Sustainable Rating - Summer |  | UPDATED 03/2012 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MAX_SUST_RTG_SM | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS |  | N | N
Wind | Seasonal Net Min Sustainable Rating - Summer |  | UPDATED 03/2012 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MIN_SUST_RTG_SM | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS |  | N | N
Wind | Seasonal Net Max Emergency Rating - Summer |  | UPDATED 03/2012 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MAX_EMGY_RTG_SM | 1.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS |  | N | N
Wind | Seasonal Net Min Emergency Rating - Summer |  | UPDATED 03/2012 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MIN_EMGY_RTG_SM | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS |  | N | N
Wind | SEASONAL RATINGS - FALL |  |  | Parameters - RENEWABLE |  |  | Not in table | Not in table
Wind | Seasonal Net Max Sustainable Rating - Fall |  | UPDATED 03/2012 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MAX_SUST_RTG_FL | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS |  | N | N
Wind | Seasonal Net Min Sustainable Rating - Fall |  | UPDATED 03/2012 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MIN_SUST_RTG_FL | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Min Sustainable Rating - Fall. >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS |  | N | N
Wind | Seasonal Net Max Emergency Rating - Fall |  | UPDATED 03/2012 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MAX_EMGY_RTG_FL | 1.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS |  | N | N
Wind | Seasonal Net Min Emergency Rating - Fall |  | UPDATED 03/2012 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MIN_EMGY_RTG_FL | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS |  | N | N
Wind | SEASONAL RATINGS - WINTER |  |  | Parameters - RENEWABLE |  |  | Not in table | Not in table
Wind | Seasonal Net Max Sustainable Rating - Winter |  | UPDATED 03/2012 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MAX_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS |  | N | N
Wind | Seasonal Net Min Sustainable Rating - Winter |  | UPDATED 03/2012 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MIN_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Sustainable Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS |  | N | N
Wind | Seasonal Net Max Emergency Rating - Winter |  | UPDATED 03/2012 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MAX_EMGY_RTG_WT | 1.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS |  | N | N
Wind | Seasonal Net Min Emergency Rating - Winter |  | UPDATED 03/2012 | Parameters - RENEWABLE |  | MW | RENEWABLE | SEASON_NET_MIN_EMGY_RTG_WT | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS |  | N | N
Generation | Operational Parameters - GEN |  |  | Operational Parameters - GEN |  |  | Not in table | Not in table |  | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | MMS,NMMS
Generation | GENERATOR DETAILS |  |  | Operational Parameters - GEN |  |  | Not in table | Not in table
Generation | Unit Name | Do not show Message on Audit or Delta |  | Operational Parameters - GEN |  | List | GENERATION | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | N
Generation | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code 05/17/2012 Update #3 validation |  | Operational Parameters - GEN |  | Automatic | GENERATION | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | N
Generation | RESOURCE PARAMETERS |  |  | Operational Parameters - GEN |  |  | Not in table | Not in table
Generation | Minimum On Line Time |  | UPDATED 03/2012 | Operational Parameters - GEN |  | hours | GENERATION | MIN_ONLINE_TIME | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum On Line Time >= 0 | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Generation | Minimum Off Line Time |  | UPDATED 03/2012 | Operational Parameters - GEN |  | hours | GENERATION | MIN_OFFLINE_TIME | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum Off Line Time >= 0 | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Generation | Hot Start Time |  | UPDATED 03/2012 | Operational Parameters - GEN |  | hours | GENERATION | HOTSTART | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot Start Time >= 0 3. Hot Start Time <= Intermediate Start Time | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Generation | Intermediate Start Time |  | UPDATED 03/2012 | Operational Parameters - GEN |  | hours | GENERATION | INTERMSTART | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate Start Time >= 0 3. Cold Start Time >= Intermediate Start Time >= Hot Start Time | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Generation | Cold Start Time |  | UPDATED 03/2012 | Operational Parameters - GEN |  | hours | GENERATION | COLDSTART | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Cold Start Time >= 0 3. Cold Start Time >= Intermediate Start Time | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Generation | Max Weekly Starts |  | UPDATED 03/2012 | Operational Parameters - GEN |  |  | GENERATION | MAXWKLYSTARTS | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Generation | Max On Line Time |  | UPDATED 03/2012 | Operational Parameters - GEN |  | hours | GENERATION | MAX_ONLINE_TIME | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Max OnLine Time > 0 | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Generation | Max Daily Starts |  | UPDATED 03/2012 | Operational Parameters - GEN |  |  | GENERATION | MAXDLYSTARTS | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Daily Start >= 0 3. Max Daily Start <= 999 | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Generation | Max Weekly Energy |  | UPDATED 03/2012 | Operational Parameters - GEN |  | MWh | GENERATION | MAXWKLYENRGY | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Energy >= 0 3. Max Weekly Energy < 1e10 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Generation | Hot-to-intermediate Time |  | UPDATED 03/2012 | Operational Parameters - GEN |  | hours | GENERATION | HOT_TO_INTMDT_TIME | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot-to-Intermediate Time >= 0 | R | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | NMMS |  | N | N
Generation | Intermediate-to-cold Time |  | UPDATED 03/2012 | Operational Parameters - GEN |  | hours | GENERATION | INTMDT_TO_COLD_TIME | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate-to-Cold Time >= 0 | R | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | NMMS |  | N | N
Generation | Operational Parameters - GEN - NRRC |  |  | Operational Parameters - GEN - NRRC |  |  | Not in table | Not in table
Generation | GENERATOR DETAILS |  |  | Operational Parameters - GEN - NRRC |  |  | Not in table | Not in table
Generation | Unit Name | Do not show Message on Audit or Delta |  | Operational Parameters - GEN - NRRC |  | List | GENERATION | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | N
Generation | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | Operational Parameters - GEN - NRRC |  | List | RAMP_RATES_NRRC | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | N
Generation | NORMAL RAMP RATE CURVE |  |  | Operational Parameters - GEN - NRRC |  |  | Not in table | Not in table | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit. |  |  |  |  | NMMS
Generation | MW Number |  |  | Operational Parameters - GEN - NRRC |  | List | RAMP_RATES_NRRC | MW_NUMBER_NRRC | Select from List | [6 empty] | N | N
Generation | NRRC Code |  | UPDATED 03/2012 | Operational Parameters - GEN - NRRC |  | Automatic | RAMP_RATES_NRRC | UNIT_MW_NRRC | Capture Unit Code and UNIT MW Number and NRRC, prepopulate this field with UNIT_CODE_UNIT_MW_NUMBER_NRRC. | R | Character |  |  |  |  | N | N
Generation | NRRC MW |  | UPDATED 03/2012 | Operational Parameters - GEN - NRRC |  | MW | RAMP_RATES_NRRC | MW_RATING_NRRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric | B | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS |  | N | N
Generation | Upward Ramprate |  | UPDATED 03/2012 | Operational Parameters - GEN - NRRC |  | MW/min | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2.. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Generation | Downward Ramprate |  | UPDATED 03/2012 | Operational Parameters - GEN - NRRC |  | MW/min | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Generation | Operational Parameters - GEN - ERRC |  |  | Operational Parameters - GEN - ERRC |  |  | Not in table | Not in table
Generation | GENERATOR DETAILS |  |  | Operational Parameters - GEN - ERRC |  |  | Not in table | Not in table
Generation | Unit Name | Do not show Message on Audit or Delta |  | Operational Parameters - GEN - ERRC |  | List | GENERATION | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | N
Generation | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | Operational Parameters - GEN - ERRC |  | List | RAMP_RATES_ERRC | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | N
Generation | EMERGENCY RAMP RATE CURVE |  |  | Operational Parameters - GEN - ERRC |  |  | Not in table | Not in table | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit. |  |  |  | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS
Generation | MW Number |  |  | Operational Parameters - GEN - ERRC |  | List | RAMP_RATES_ERRC | MW_NUMBER_ERRC | Select from List | [6 empty] | N | N
Generation | ERRC Code |  | UPDATED 03/2012 | Operational Parameters - GEN - ERRC |  | Automatic | RAMP_RATES_ERRC | UNIT_MW_ERRC | Capture Unit Code and UNIT MW Number and ERRC, prepopulate this field with UNIT_CODE_UNIT_MW_NUMBER_ERRC. | R | Character |  |  |  |  | N | N
Generation | ERRC MW |  | UPDATED 03/2012 | Operational Parameters - GEN - ERRC |  | MW | RAMP_RATES_NRRC | MW_RATING_ERRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric | B | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS |  | N | N
Generation | Upward Ramprate |  | UPDATED 03/2012 | Operational Parameters - GEN - ERRC |  | MW/min | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Generation | Downward Ramprate |  | UPDATED 03/2012 | Operational Parameters - GEN - ERRC |  | MW/min | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
CC | Operational Parameters - CFG |  |  | Operational Parameters - CFG |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type selected is 'CC'. Can register up to 3 trains at one site. This tab is required for Configurations. | C |  |  | RARF Guide Version 4.0 | MMS,NMMS
CC | GENERATOR DETAILS |  |  | Operational Parameters - CFG |  |  | Not in table | Not in table
CC | SITECODE |  |  | Operational Parameters - CFG |  | List | CONFIGURATIONS | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R | [5 empty] | N | N
CC | Train Code |  |  | Operational Parameters - CFG |  | List | TRAIN | TRAIN_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N | N
CC | Configuration Code |  |  | Operational Parameters - CFG |  | List | CONFIGURATIONS | CONFIG_CODE | Required | R | [5 empty] | N | N
CC | RESOURCE PARAMETERS |  |  | Operational Parameters - CFG |  |  | Not in table | Not in table
CC | Minimum On Line Time |  | UPDATED 03/2012 | Operational Parameters - CFG |  | hours | CONFIGURATIONS | MIN_ONLINE_TIME | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum On Line Time >= 0 | R | Integer | B,DVB | KittiPong/Jamil Daouk | MMS,NMMS |  | N | N
CC | Minimum Off Line Time |  | UPDATED 03/2012 | Operational Parameters - CFG |  | hours | CONFIGURATIONS | MIN_OFFLINE_TIME | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum Off Line Time >= 0 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS |  | N | N
CC | Hot Start Time |  | UPDATED 03/2012 | Operational Parameters - CFG |  | hours | CONFIGURATIONS | HOTSTART | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot Start Time >= 0 3. Hot Start Time <= Intermediate Start Time | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS |  | N | N
CC | Intermediate Start Time |  | UPDATED 03/2012 | Operational Parameters - CFG |  | hours | CONFIGURATIONS | INTERMSTART | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate Start Time >= 0 3. Cold Start Time >= Intermediate Start Time >= Hot Start Time | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS |  | N | N
CC | Cold Start Time |  | UPDATED 03/2012 | Operational Parameters - CFG |  | hours | CONFIGURATIONS | COLDSTART | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Cold Start Time >= 0 3. Cold Start Time >= Intermediate Start Time | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS |  | N | N
CC | Max Weekly Starts |  | UPDATED 03/2012 | Operational Parameters - CFG |  |  | CONFIGURATIONS | MAXWKLYSTARTS | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS |  | N | N
CC | Max On Line Time |  | UPDATED 03/2012 | Operational Parameters - CFG |  |  | CONFIGURATIONS | MAX_ONLINE_TIME | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Max OnLine Time > 0 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS |  | N | N
CC | Max Daily Starts |  | UPDATED 03/2012 | Operational Parameters - CFG |  |  | CONFIGURATIONS | MAXDLYSTARTS | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Daily Start >= 0 3. Max Daily Start <= 999 | R | Numeric | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS |  | N | N
CC | Max Weekly Energy |  | UPDATED 03/2012 | Operational Parameters - CFG |  | MWh | CONFIGURATIONS | MAXWKLYENRGY | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Energy >= 0 3. Max Weekly Energy < 1e10 | R | Integer | B,DVB | Lin Xu/Kittipong | MMS,NMMS |  | N | N
CC | Hot-to-intermediate Time |  | UPDATED 03/2012 | Operational Parameters - CFG |  | hours | CONFIGURATIONS | HOT_TO_INTMDT_TIME | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot-to-Intermediate Time >= 0 | R | Integer | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS |  | N | N
CC | Intermediate-to-cold Time |  | UPDATED 03/2012 | Operational Parameters - CFG |  | hours | CONFIGURATIONS | INTMDT_TO_COLD_TIME | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate-to-Cold Time >= 0 | R | Integer | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS |  | N | N
CC | Operational Parameters - NRRC |  |  | Operational Parameters - CFG - NRRC |  |  | Not in table | Not in table
CC | Train Code | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | Operational Parameters - CFG - NRRC |  | List | RAMP_RATES_NRRC | UNIT_CODE | 1.This field is Not null: Capture UNIT Code and Configuration Code and prepopulate this field with TRAIN _Config_Code. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | N
CC | Configuration Code |  |  | Operational Parameters - CFG - NRRC |  | List | CONFIGURATIONS | CONFIG_CODE | Required Field | R | Character | B,DVB |  |  |  | N | N
CC | NORMAL RAMP RATE CURVE |  |  | Operational Parameters - CFG - NRRC |  |  | Not in table | Not in table | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit. |  | Numeric | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS
CC | MW Number |  |  | Operational Parameters - CFG - NRRC |  | List | RAMP_RATES_NRRC | MW_NUMBER_NRRC | Select from List | R | [5 empty] | N | N
CC | NRRC Code |  | UPDATED 03/2012 | Operational Parameters - CFG - NRRC |  | Automatic | RAMP_RATES_NRRC | UNIT_MW_NRRC | This Field is Not in the RARF: Capture Unit Code and UNIT MW Number and NRRC, prepopulate this field with UNIT_CODE_UNIT_MW_NUMBER_NRRC. | R A | Character |  |  |  |  | N | N |  |  |  | This is filled automatically in the form, why is there any validation?
CC | NRRC MW |  | UPDATED 03/2012 | Operational Parameters - CFG - NRRC |  | MW | RAMP_RATES_NRRC | MW_RATING_NRRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in de ascending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric | B | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS |  | N | N
CC | Upward Ramprate | Updated 03/06/2012 | UPDATED 03/2012 | Operational Parameters - CFG - NRRC |  | MW/min | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
CC | Downward Ramprate |  | UPDATED 03/2012 | Operational Parameters - CFG - NRRC |  | MW/min | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
CC | Operational Parameters - ERRC |  |  | Operational Parameters - CFG - ERRC |  |  | Not in table | Not in table
CC | Train Code | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | Operational Parameters - CFG - ERRC |  | List | RAMP_RATES_ERRC | UNIT_CODE | 1.This field is Not null: Capture Train Code and Configuration Code and prepopulate this field with Train_Code _Config_Code. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | N
CC | Configuration Code |  |  | Operational Parameters - CFG - ERRC |  | List | CONFIGURATIONS | CONFIG_CODE | ` | R | Character | B,DVB |  |  |  | N | N
CC | EMERGENCY RAMP RATE CURVE |  |  | Operational Parameters - CFG - ERRC |  |  | Not in table | Not in table | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit. |  |  |  | RARF Guide Version 4.0 | NMMS
CC | MW Number |  |  | Operational Parameters - CFG - ERRC |  | List | RAMP_RATES_ERRC | MW_NUMBER_ERRC | Select from List | R | [5 empty] | N | N
CC | ERRC Code |  | UPDATED 03/2012 | Operational Parameters - CFG - ERRC |  | Automatic | RAMP_RATES_ERRC | UNIT_MW_ERRC | Capture Unit Code and UNIT MW Number and ERRC, prepopulate this field with UNIT_CODE_UNIT_MW_NUMBER_ERRC. | R A | Character |  |  |  |  | N | N |  |  |  | This is filled automatically in the form, why is there any validation?
CC | ERRC MW |  | UPDATED 03/2012 | Operational Parameters - CFG - ERRC |  | MW | RAMP_RATES_NRRC | MW_RATING_ERRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in de ascending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric | B | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS |  | N | N
CC | Upward Ramprate | Updated 03/06/2012 | UPDATED 03/2012 | Operational Parameters - CFG - ERRC |  | MW/min | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
CC | Downward Ramprate |  | UPDATED 03/2012 | Operational Parameters - CFG - ERRC |  | MW/min | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Wind | Operational Parameters - RENEW |  |  | Operational Parameters - RENEW |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Resource Type Selected is 'WIND units' | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | MMS,NMMS
Wind | GENERATOR DETAILS |  |  | Operational Parameters - RENEW |  |  | Not in table | Not in table
Wind | Unit Name | Do not show Message on Audit or Delta |  | Operational Parameters - RENEW |  | List | RENEWABLE | UNIT_NAME | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | N
Wind | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | Operational Parameters - RENEW |  | Automatic | RENEWABLE | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | N |  |  |  | This is filled automatically in the form, why is there any validation?
Wind | RESOURCE PARAMETERS |  |  | Operational Parameters - RENEW |  |  | Not in table | Not in table
Wind | Minimum On Line Time |  | UPDATED 03/2012 | Operational Parameters - RENEW |  | hours | RENEWABLE | MIN_ONLINE_TIME | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum On Line Time >= 0 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS |  | N | N
Wind | Minimum Off Line Time |  | UPDATED 03/2012 | Operational Parameters - RENEW |  | hours | RENEWABLE | MIN_OFFLINE_TIME | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum Off Line Time >= 0 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS |  | N | N
Wind | Hot Start Time |  | UPDATED 03/2012 | Operational Parameters - RENEW |  | hours | RENEWABLE | HOTSTART | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot Start Time >= 0 3. Hot Start Time <= Intermediate Start Time | O | Integer | B,DVB | Angela Moy/Jamil Daouk | NMMS |  | N | N
Wind | Intermediate Start Time |  | UPDATED 03/2012 | Operational Parameters - RENEW |  | hours | RENEWABLE | INTERMSTART | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate Start Time >= 0 3. Cold Start Time >= Intermediate Start Time >= Hot Start Time | O | Integer | B,DVB | Angela Moy/Jamil Daouk | NMMS |  | N | N
Wind | Cold Start Time |  | UPDATED 03/2012 | Operational Parameters - RENEW |  | hours | RENEWABLE | COLDSTART | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Cold Start Time >= 0 3. Cold Start Time >= Intermediate Start Time | O | Integer | B,DVB | Angela Moy/Jamil Daouk | NMMS |  | N | N
Wind | Max Weekly Starts |  | UPDATED 03/2012 | Operational Parameters - RENEW |  |  | RENEWABLE | MAXWKLYSTARTS | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Integer | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS |  | N | N
Wind | Max On Line Time |  | UPDATED 03/2012 | Operational Parameters - RENEW |  | hours | RENEWABLE | MAX_ONLINE_TIME | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Max OnLine Time > 0 | R | Integer | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS |  | N | N
Wind | Max Daily Starts |  | UPDATED 03/2012 | Operational Parameters - RENEW |  |  | RENEWABLE | MAXDLYSTARTS | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Daily Start >= 0 3. Max Daily Start <= 999 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS |  | N | N
Wind | Max Weekly Energy |  | UPDATED 03/2012 | Operational Parameters - RENEW |  | MWh | RENEWABLE | MAXWKLYENRGY | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Energy >= 0 3. Max Weekly Energy < 1e10 | R | Numeric | B,DVB | Lin Xu | MMS,NMMS |  | N | N
Wind | Hot-to-Intermediate Time |  | UPDATED 03/2012 | Operational Parameters - RENEW |  | hours | RENEWABLE | HOT_TO_INTMDT_TIME | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot-to-Intermediate Time >= 0 | R | Integer | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS |  | N | N
Wind | Intermediate-to-Cold Time |  | UPDATED 03/2012 | Operational Parameters - RENEW |  | hours | RENEWABLE | INTMDT_TO_COLD_TIME | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate-to-Cold Time >= 0 | R | Integer | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS |  | N | N
Wind | Operational Parameters - NRRC |  |  | Operational Parameters - NRRC |  |  | Not in table | Not in table
Wind | GENERATOR DETAILS |  |  | Operational Parameters - NRRC |  |  | Not in table | Not in table
Wind | Unit Name | Do not show Message on Audit or Delta |  | Operational Parameters - NRRC |  | List | RENEWABLE | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | N
Wind | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | Operational Parameters - NRRC |  | List | RAMP_RATES_NRRC | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | N
Wind | NORMAL RAMP RATE CURVE |  |  | Operational Parameters - NRRC |  |  | Not in table | Not in table | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit.
Wind | MW Number |  |  | Operational Parameters - NRRC |  | List | RAMP_RATES_NRRC | MW_NUMBER_NRRC | Select from List | [6 empty] | N | N
Wind | NRRC Code |  | UPDATED 03/2012 | Operational Parameters - NRRC |  | Automatic | RAMP_RATES_NRRC | UNIT_MW_NRRC | Capture Unit Code and UNIT MW Number and NRRC, prepopulate this field with UNIT_CODE_UNIT_MW_NUMBER_NRRC. | R A | Character |  |  |  |  | N | N |  |  |  | This is filled automatically in the form, why is there any validation?
Wind | NRRC MW |  | UPDATED 03/2012 | Operational Parameters - NRRC |  | MW | RAMP_RATES_NRRC | MW_RATING_NRRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in de ascending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric | B | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS |  | N | N
Wind | Upward Ramprate |  | UPDATED 03/2012 | Operational Parameters - NRRC |  | MW/min | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Wind | Downward Ramprate |  | UPDATED 03/2012 | Operational Parameters - NRRC |  | MW/min | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Wind | Operational Parameters - ERRC |  |  | Operational Parameters - ERRC |  |  | Not in table | Not in table
Wind | GENERATOR DETAILS |  |  | Operational Parameters - ERRC |  |  | Not in table | Not in table
Wind | Unit Name | Do not show Message on Audit or Delta | UPDATED 03/2012 | Operational Parameters - ERRC |  | List | RENEWABLE | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | N
Wind | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | Operational Parameters - ERRC |  | List | RAMP_RATES_ERRC | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | N
Wind | EMERGENCY RAMP RATE CURVE |  |  | Operational Parameters - ERRC |  |  | Not in table | Not in table | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit.
Wind | MW Number |  |  | Operational Parameters - ERRC |  | List | RAMP_RATES_ERRC | MW_NUMBER_ERRC | Select from List | [6 empty] | N | N
Wind | ERRC Code |  | UPDATED 03/2012 | Operational Parameters - ERRC |  | Automatic | RAMP_RATES_ERRC | UNIT_MW_ERRC | Capture Unit Code and Unit MW Number and prepopulate this field with Unit CODE_UNIT_MW_NUMBER_ERRC. | R A | Character |  |  |  |  | N | N
Wind | ERRC MW |  | UPDATED 03/2012 | Operational Parameters - ERRC |  | MW | RAMP_RATES_NRRC | MW_RATING_ERRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric | B | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS |  | N | N
Wind | Upward Ramprate |  | UPDATED 03/2012 | Operational Parameters - ERRC |  | MW/min | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Wind | Downward Ramprate |  | UPDATED 03/2012 | Operational Parameters - ERRC |  | MW/min | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Solar Photovoltaic (PV) | Operational Parameters |  |  | Operational Parameters - RENEW |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type Selected is 'GEN' where GEN is non-CC non-wind Generation Resources. | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | MMS,NMMS
Solar Photovoltaic (PV) | GENERATOR DETAILS |  |  | Operational Parameters - RENEW |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | Unit Name | Do not show Message on Audit or Delta | Added 05/01/2017 | Operational Parameters - RENEW |  | List | RENEWABLE | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | N
Solar Photovoltaic (PV) | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code 05/17/2012 Update #3 validation | Added 05/01/2017 | Operational Parameters - RENEW |  | Automatic | RENEWABLE | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | N
Solar Photovoltaic (PV) | RESOURCE PARAMETERS |  |  | Operational Parameters - RENEW |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | Minimum On Line Time |  | Added 05/01/2017 | Operational Parameters - RENEW |  | hours | RENEWABLE | MIN_ONLINE_TIME | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum On Line Time >= 0 | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Solar Photovoltaic (PV) | Minimum Off Line Time |  | Added 05/01/2017 | Operational Parameters - RENEW |  | hours | RENEWABLE | MIN_OFFLINE_TIME | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum Off Line Time >= 0 | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Solar Photovoltaic (PV) | Hot Start Time |  | Added 05/01/2017 | Operational Parameters - RENEW |  | hours | RENEWABLE | HOTSTART | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot Start Time >= 0 3. Hot Start Time <= Intermediate Start Time | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Solar Photovoltaic (PV) | Intermediate Start Time |  | Added 05/01/2017 | Operational Parameters - RENEW |  | hours | RENEWABLE | INTERMSTART | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate Start Time >= 0 3. Cold Start Time >= Intermediate Start Time >= Hot Start Time | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Solar Photovoltaic (PV) | Cold Start Time |  | Added 05/01/2017 | Operational Parameters - RENEW |  | hours | RENEWABLE | COLDSTART | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Cold Start Time >= 0 3. Cold Start Time >= Intermediate Start Time | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Solar Photovoltaic (PV) | Max Weekly Starts |  | Added 05/01/2017 | Operational Parameters - RENEW |  |  | RENEWABLE | MAXWKLYSTARTS | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Solar Photovoltaic (PV) | Max On Line Time |  | Added 05/01/2017 | Operational Parameters - RENEW |  | hours | RENEWABLE | MAX_ONLINE_TIME | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Max OnLine Time > 0 | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Solar Photovoltaic (PV) | Max Daily Starts |  | Added 05/01/2017 | Operational Parameters - RENEW |  |  | RENEWABLE | MAXDLYSTARTS | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Daily Start >= 0 3. Max Daily Start <= 999 | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Solar Photovoltaic (PV) | Max Weekly Energy |  | Added 05/01/2017 | Operational Parameters - RENEW |  | MWh | RENEWABLE | MAXWKLYENRGY | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Energy >= 0 3. Max Weekly Energy < 1e10 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Solar Photovoltaic (PV) | Hot-to-intermediate Time |  | Added 05/01/2017 | Operational Parameters - RENEW |  | hours | RENEWABLE | HOT_TO_INTMDT_TIME | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot-to-Intermediate Time >= 0 | R | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | NMMS |  | N | N
Solar Photovoltaic (PV) | Intermediate-to-cold Time |  | Added 05/01/2017 | Operational Parameters - RENEW |  | hours | RENEWABLE | INTMDT_TO_COLD_TIME | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate-to-Cold Time >= 0 | R | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | NMMS |  | N | N
Solar Photovoltaic (PV) | Operational Parameters - NRRC |  |  | Operational Parameters - NRRC |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | GENERATOR DETAILS |  |  | Operational Parameters - NRRC |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | Unit Name | Do not show Message on Audit or Delta | Added 05/01/2017 | Operational Parameters - NRRC |  | List | RAMP_RATES_NRRC | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | N
Solar Photovoltaic (PV) | Resource Name (Unit Code/Mnemonic) |  | Added 05/01/2017 | Operational Parameters - NRRC |  | List | RAMP_RATES_NRRC | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | N
Solar Photovoltaic (PV) | NORMAL RAMP RATE CURVE |  |  | Operational Parameters - NRRC |  |  | Not in table | Not in table | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit. |  |  |  |  | NMMS
Solar Photovoltaic (PV) | MW Number |  | Added 05/01/2017 | Operational Parameters - NRRC |  | List | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1) This field is required 2) Data type must be Numeric | R | [5 empty] | N | N
Solar Photovoltaic (PV) | NRRC Code |  | Added 05/01/2017 | Operational Parameters - NRRC |  | Automatic | RAMP_RATES_NRRC | UNIT_MW_NRRC | Capture Unit Code and UNIT MW Number and NRRC, prepopulate this field with UNIT_CODE_UNIT_MW_NUMBER_NRRC. | R | Character |  |  |  |  | N | N
Solar Photovoltaic (PV) | NRRC MW |  | Added 05/01/2017 | Operational Parameters - NRRC |  | MW | RAMP_RATES_NRRC | MW_RATING_NRRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric | B | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS |  | N | N
Solar Photovoltaic (PV) | Upward Ramprate |  | Added 05/01/2017 | Operational Parameters - NRRC |  | MW/min | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2.. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Solar Photovoltaic (PV) | Downward Ramprate |  | Added 05/01/2017 | Operational Parameters - NRRC |  | MW/min | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Solar Photovoltaic (PV) | Operational Parameters - ERRC |  |  | Operational Parameters - ERRC |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | GENERATOR DETAILS |  |  | Operational Parameters - ERRC |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | Unit Name | Do not show Message on Audit or Delta | Added 05/01/2017 | Operational Parameters - ERRC |  | List | RAMP_RATES_ERRC | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | N
Solar Photovoltaic (PV) | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code | Added 05/01/2017 | Operational Parameters - ERRC |  | List | RAMP_RATES_ERRC | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | N
Solar Photovoltaic (PV) | EMERGENCY RAMP RATE CURVE |  |  | Operational Parameters - ERRC |  |  | Not in table | Not in table | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit. |  |  |  | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS
Solar Photovoltaic (PV) | MW Number |  | Added 05/01/2017 | Operational Parameters - ERRC |  | List | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1) This field is required 2) Data type must be Numeric | [6 empty] | N | N
Solar Photovoltaic (PV) | ERRC Code |  | Added 05/01/2017 | Operational Parameters - ERRC |  | Automatic | RAMP_RATES_ERRC | UNIT_MW_ERRC | Capture Unit Code and UNIT MW Number and ERRC, prepopulate this field with UNIT_CODE_UNIT_MW_NUMBER_ERRC. | R | Character |  |  |  |  | N | N
Solar Photovoltaic (PV) | ERRC MW |  | Added 05/01/2017 | Operational Parameters - ERRC |  | MW | RAMP_RATES_ERRC | MW_RATING_ERRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric | B | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS |  | N | N
Solar Photovoltaic (PV) | Upward Ramprate |  | Added 05/01/2017 | Operational Parameters - ERRC |  | MW/min | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Solar Photovoltaic (PV) | Downward Ramprate |  | Added 05/01/2017 | Operational Parameters - ERRC |  | MW/min | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS |  | N | N
Generation | Reactive Capability - GEN |  |  | Reactive Capability - GEN |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type Selected is 'GEN' where GEN is non-CC non-wind Generation Resources. All the fields in this tab should be filled in. | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,MMS,NMMS
Generation | GENERATOR DETAILS |  |  | Reactive Capability - GEN |  |  | Not in table | Not in table
Generation | Unit Name | Do not show Message on Audit or Delta |  | Reactive Capability - GEN |  | List | GENERATION | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | Y | Y
Generation | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | Reactive Capability - GEN |  | Automatic | GENERATION | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | Y | Y |  |  |  | This is filled automatically in the form, why is there any validation?
Generation | REACTIVE CAPABILITY CURVES DETAILS |  |  | Reactive Capability - GEN |  |  | Not in table | Not in table
Generation | Reactive Capability Data Provided Below Is Gross Values? | 04/02/2012 - Updated RARF Field Name, DB Field and removed Net from Drop down List in data Validation | ADDED 06/27/2012 | Reactive Capability - GEN | Generation_ReactiveCapability.View | List | GENERATION | REACT_CAPB_DATA_GROSS_VAL | Select from the list: GROSS | R | Dropdown List |  |  |  |  | Y | Y
Generation | Reactive Capability Data Provided Below Is From NDCRC Test Data? |  | ADDED 06/27/2012 | Reactive Capability - GEN | Generation_ReactiveCapability.View | Y/N | GENERATION | REACT_CAPB_NDCRC_TEST_DATA | Select from the list: Y or N | R | Dropdown List |  |  |  |  | N | N
Generation | If Reactive Capability Data Provided Below Is From NDCRC Test Data Then Enter The Date On Which The Test Was Performed. |  | ADDED 06/27/2012 | Reactive Capability - GEN | Generation_ReactiveCapability.View | mm/dd/yyyy | GENERATION | REACT_CAPB_NDCRC_TEST_DATA_DT | This field is optional. Format should be: MM/DD/YYYY | O C | Date |  |  |  |  | N | N
Generation | Mw1 |  |  | Reactive Capability - GEN |  | MW | GENERATION | MW1 | 1. MW1 >=0 .1 2. MW1<MW2. 3. X(1) <= WMN(Unit Minimal output) where X(1) represents MW1( Generate a Warning Only when Business Rule#2 fails) | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS |  | N | Y
Generation | Lagging MVAR limit associated with Mw1 output | 2015-11-03 | 11/3/2015 Added validation rule 4 updated validation rule #3 | Reactive Capability - GEN |  | MVAR | GENERATION | MVAR1LAG | 1. Lagging MVAR limit associated with MW1 output >=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than or equal to Leading MVAR 4. Lagging MVAR <= Maximum Lagging Operating Capability | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS |  | N | Y
Generation | Leading MVAR limit associated with Mw1 output | 2015-11-03 | 11/3/2015 Added validation rule 3 | Reactive Capability - GEN |  | MVAR | GENERATION | MVAR1LEAD | 1. Leading MVAR limit associated with MW1 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Leading MVAR >= Maximum Leading Operating Capability | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS |  | N | Y
Generation | Mw2 |  |  | Reactive Capability - GEN |  | MW | GENERATION | MW2 | 1. MW2>0 2. MW2<MW3 | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS |  | N | Y
Generation | Lagging MVAR limit associated with Mw2 output | 2015-11-03 | 11/3/2015 Added validation rule 4 updated validation rule #3 | Reactive Capability - GEN |  | MVAR | GENERATION | MVAR2LAG | 1.Lagging MVAR limit associated with MW2 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR 4. Lagging MVAR <= Maximum Lagging Operating Capability | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS |  | N | Y
Generation | Leading MVAR limit associated with Mw2 output | 2015-11-03 | 11/3/2015 Added validation rule 3 | Reactive Capability - GEN |  | MVAR | GENERATION | MVAR2LEAD | 1. Leading MVAR limit associated with MW2 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Leading MVAR >= Maximum Leading Operating Capability | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS |  | N | Y
Generation | Mw3 |  |  | Reactive Capability - GEN |  | MW | GENERATION | MW3 | 1. MW3 >0 2. MW3<MW4 | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS |  | N | Y
Generation | Lagging MVAR limit associated with Mw3 output | 2015-11-03 | 11/3/2015 Added validation rule 4 updated validation rule #3 | Reactive Capability - GEN |  | MVAR | GENERATION | MVAR3LAG | 1. Lagging MVAR limit associated with MW3 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR 4. Lagging MVAR <= Maximum Lagging Operating Capability | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS |  | N | Y
Generation | Leading MVAR limit associated with Mw3 output | 2015-11-03 | 11/3/2015 Added validation rule 3 | Reactive Capability - GEN |  | MVAR | GENERATION | MVAR3LEAD | 1.Leading MVAR limit associated with MW3 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Leading MVAR >= Maximum Leading Operating Capability | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS |  | N | Y
Generation | Mw4 |  |  | Reactive Capability - GEN |  | MW | GENERATION | MW4 | 1. MW4 >0 2. MW4<MW5 3. X(n) > = WMX (Unit Max output) where n is the last MW value in the curve. If the curve has 4 points, X(n) is X(4) [ Generate a Warning Only When Business Rule#2 Fails] | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS |  | N | Y
Generation | Lagging MVAR limit associated with Mw4 output | 2015-11-03 | 11/3/2015 Added validation rule 4 updated validation rule #3 | Reactive Capability - GEN |  | MVAR | GENERATION | MVAR4LAG | 1. Lagging MVAR limit associated with MW4 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than or equal to Leading MVAR 4. Lagging MVAR <= Maximum Lagging Operating Capability | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS |  | N | Y
Generation | Leading MVAR limit associated with Mw4 output | 2015-11-03 | 11/3/2015 Added validation rule 3 | Reactive Capability - GEN |  | MVAR | GENERATION | MVAR4LEAD | 1.Leading MVAR limit associated with MW4 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Leading MVAR >= Maximum Leading Operating Capability | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS |  | N | Y
Generation | Mw5 - Unity Power Factor |  |  | Reactive Capability - GEN |  | MW | GENERATION | MW5UNITYPF | 1. MW5 >0 2. MW5 >MW4 3. MW5 =>= HRL | R | Numeric | B,DVB | Lin Xu | MMS,NMMS |  | N | Y
Generation | If Hydrogen Cooled, Indicate Hydrogen Pressure (PSI) Associated With Your Reactive Curve Submitted For ERCOT Studies |  |  | Reactive Capability - GEN |  | PSI | GENERATION | HYDROCOOLED | Data type is Numeric | O | Numeric | B | Angela Moy\RARF Guide Version 4.0/RARF Glossary Version 4.0 |  |  | N | N
Generation | Maximum Lagging Operating Capability | 2015-11-03 | 11/3/2015 Updated Validation rule 1, 2 and 3 | Reactive Capability - GEN |  | MVAR | GENERATION | NETMAXLAG | 1.Net Maximum Lagging Operating Capability >=0 2. Maximum Lagging Operating Capability >= Maximum Leading Operating Capability | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,MMS |  | Y | Y
Generation | Maximum Leading Operating Capability | 2015-11-03 | 11/3/2015 updated Validation rule 1 | Reactive Capability - GEN |  | MVAR | GENERATION | NETMAXLEAD | 1. Maximum Leading Operating Capability <=0 | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,MMS |  | Y | Y
Generation | Manufacturer's Capability Curve submitted? |  |  | Reactive Capability - GEN |  | Y/N | GENERATION | MFR_CAPABILITY_CURVE_FLG | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 |  |  | N | Y
CC | Reactive Capability - CC |  |  | Reactive Capability - CC |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type selected is 'Combined Cycle '. Required for each configuration. All the fields in this tab should be filled. | C |  |  |  | EMS,MMS,NMMS
CC | GENERATOR DETAILS |  |  | Reactive Capability - CC |  |  | Not in table | Not in table
CC | Unit Name | Do not show Message on Audit or Delta |  | Reactive Capability - CC |  | List | CCUNIT | UNIT_NAME | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | Y | Y
CC | SITE_CODE |  |  | Reactive Capability - CC |  | Automatic | CCUNIT | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | A | [5 empty] | N | N |  |  |  | This is filled automatically in the form, why is there any validation?
CC | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | Reactive Capability - CC |  | Automatic | CCUNIT | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | Y | Y |  |  |  | This is filled automatically in the form, why is there any validation?
CC | REACTIVE CAPABILITY CURVES DETAILS |  |  | Reactive Capability - CC |  |  | Not in table | Not in table | 4. Can not exceed 13 characters for split gen resources
CC | Reactive Capability Data Provided is Gross Values? | 04/02/2012 - Updated RARF Field Name, DB Field and removed Net from Drop down List in data Validation | ADDED 06/27/2012 | Reactive Capability - CC | CC_ReactiveCapability.View | List | CCUNIT | REACT_CAPB_DATA_GROSS_NET_VAL | Select from the list: GROSS | R | Dropdown List |  |  |  |  | Y | Y
CC | Reactive Capability Data Provided is from NDCRC Test Data? |  | ADDED 06/27/2012 | Reactive Capability - CC | CC_ReactiveCapability.View | Y/N | CCUNIT | REACT_CAPB_NDCRC_TEST_DATA | Select from the list: Y or N | R | Dropdown List |  |  |  |  | N | N
CC | If Reactive Capability Data Provided Is From NDCRC test Data Then Enter The Date On Which The Test Was Performed. |  | ADDED 06/27/2012 | Reactive Capability - CC | CC_ReactiveCapability.View | mm/dd/yyyy | CCUNIT | REACT_CAPB_NDCRC_TEST_DATA_DT | This field is optional. Format should be: MM/DD/YYYY | O C | Date |  |  |  |  | N | N
CC | Mw1 |  |  | Reactive Capability - CC |  | MW | CCUNIT | MW1_GEN | 1. MW1 >=0 .1 21.MW1<MW2. 32. X(1) <= WMN(Unit Minimal output) where X(1) represents MW1( Generate a Warning Only when Business Rule#2 fails) | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS |  | N | Y |  |  |  | Business rule #3 is utter nonsense. Glossary requires non-IRRs to use the lowest Seasonal Net minimum Sustaiable rating (converted to gross value)
CC | Lagging MVAR Limit Associated With Mw1 Output | 2015-11-03 | 11/3/2015 Added validation rule 4 updated validation rule #3 | Reactive Capability - CC |  | MVAR | CCUNIT | MVAR1LAG_GEN | 1. Lagging MVAR limit associated with MW1 output >=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR 4. Lagging MVAR <= Maximum Lagging Operating Capability | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS |  | N | Y |  |  |  | Business rule #2 makes no mathematical sense
CC | Leading MVAR Limit Associated With Mw1 Output | 2015-11-03 | 11/3/2015 Added validation rule 3 | Reactive Capability - CC |  | MVAR | CCUNIT | MVAR1LEAD_GEN | 1. Leading MVAR limit associated with MW1 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Leading MVAR >= Maximum Leading Operating Capability | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS |  | N | Y |  |  |  | Business rule #2 makes no mathematical sense
CC | Mw2 |  |  | Reactive Capability - CC |  | MW | CCUNIT | MW2_GEN | 1. MW2>0 2.MW2<MW3 | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS |  | N | Y
CC | Lagging MVAR Limit Associated With Mw2 Output | 2015-11-03 | 11/3/2015 Added validation rule 4 updated validation rule #3 | Reactive Capability - CC |  | MVAR | CCUNIT | MVAR2LAG_GEN | 1. Lagging MVAR limit associated with MW2 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than or equal to Leading MVAR 4. Lagging MVAR <= Maximum Lagging Operating Capability | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS |  | N | Y |  |  |  | Business rule #2 makes no mathematical sense
CC | Leading MVAR Limit Associated With Mw2 Output | 2015-11-03 | 11/3/2015 Added validation rule 3 | Reactive Capability - CC |  | MVAR | CCUNIT | MVAR2LEAD_GEN | 1. Leading MVAR limit associated with MW2 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Leading MVAR >= Maximum Leading Operating Capability | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS |  | N | Y |  |  |  | Business rule #2 makes no mathematical sense
CC | Mw3 |  |  | Reactive Capability - CC |  | MW | CCUNIT | MW3_GEN | 1.MW3 >0 2.MW3<MW4 | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS |  | N | Y
CC | Lagging MVAR Limit Associated With Mw3 Output | 2015-11-03 | 11/3/2015 Added validation rule 4 updated validation rule #3 | Reactive Capability - CC |  | MVAR | CCUNIT | MVAR3LAG_GEN | 1. Lagging MVAR limit associated with MW3 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR 4. Lagging MVAR <= Maximum Lagging Operating Capability | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS |  | N | Y |  |  |  | Business rule #2 makes no mathematical sense
CC | Leading MVAR Limit Associated With Mw3 Output | 2015-11-03 | 11/3/2015 Added validation rule 3 | Reactive Capability - CC |  | MVAR | CCUNIT | MVAR3LEAD_GEN | 1. Leading MVAR limit associated with MW3 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Leading MVAR >= Maximum Leading Operating Capability | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS |  | N | Y |  |  |  | Business rule #2 makes no mathematical sense
CC | Mw4 |  |  | Reactive Capability - CC |  | MW | CCUNIT | MW4_GEN | 1. MW4> 0 2.MW4<MW5 3. X(n) > = WMX (Unit Max output) where n is the last MW value in the curve. If the curve has 4 points, X(n) is X(4) [ Generate a Warning Only When Business Rule#2 Fails] | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS |  | N | Y
CC | Lagging MVAR Limit Associated With Mw4 Output | 2015-11-03 | 11/3/2015 Added validation rule 4 updated validation rule #3 | Reactive Capability - CC |  | MVAR | CCUNIT | MVAR4LAG_GEN | 1. Lagging MVAR limit associated with MW4 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR 4. Lagging MVAR <= Maximum Lagging Operating Capability | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS |  | N | Y |  |  |  | Business rule #2 makes no mathematical sense
CC | Leading MVAR Limit Associated With Mw4 Output | 2015-11-03 | 11/3/2015 Added validation rule 3 | Reactive Capability - CC |  | MVAR | CCUNIT | MVAR4LEAD_GEN | 1.MVAR limit associated with MW4 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Leading MVAR >= Maximum Leading Operating Capability | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS |  | N | Y |  |  |  | Business rule #2 makes no mathematical sense
CC | Mw5 - Unity Power Factor |  |  | Reactive Capability - CC |  | MW | CCUNIT | MW5UNITYPF_GEN | 1. MW5 >0 2.MW5>MW4 3. MW5 =>= HRL | R | Numeric | B,DVB | Lin Xu | MMS,NMMS |  | N | Y |  |  |  | Maximum capability may be between two points on the curve
CC | If Hydrogen Cooled, Indicate Hydrogen Pressure (PSI) Associated With Your Reactive Curve Submitted For ERCOT Studies |  |  | Reactive Capability - CC |  | PSI | CCUNIT | HYDROCOOLED | Data type is Numeric | O | Numeric | B | Angela Moy/RARF Guide Version 4.0 |  |  | N | N |  |  |  | Maximum capability may be between two points on the curve
CC | Maximum Lagging Operating Capability | 2015-11-03 | 11/3/2015 Updated Validation rule 1, 2 and 3 | Reactive Capability - CC |  | MVAR | CCUNIT | NETMAXLAG_GEN | 1. Maximum Lagging Operating Capability >= 0 2. Maximum Lagging Operating Capability >= Maximum Leading Operating Capability | R | Numeric | B,DVB | Lin Xu | MMS |  | Y | Y
CC | Maximum Leading Operating Capability | 2015-11-03 | 11/3/2015 updated Validation rule 1 | Reactive Capability - CC |  | MVAR | CCUNIT | NETMAXLEAD_GEN | 1. Maximum Leading Operating Capability <= 0 | R | Numeric | B,DVB | Lin Xu | MMS |  | Y | Y
CC | Manufacturer's Capability Curve Submitted? |  |  | Reactive Capability - CC |  | Y/N | CCUNIT | MFR_CAPABILITY_CURVE_FLG | Select from Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 |  |  | N | Y
Wind | Reactive Capability - RENEWABLE | 12/10/13 Updated Validation Rule #3 | 12/10/13 Updated Validation Rule #3 | Reactive Capability - RENEWABLE |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type selected is 'WIND '. If the Unit Info-Wind tab shows a Single Unit, Produce an error if the corresponding data is missing in the Reactive Capability-Wind Tab. | C |  | B,DVB | Angela Moy | EMS,MMS,NMMS
Wind | GENERATOR DETAILS |  |  | Reactive Capability - RENEWABLE |  |  | Not in table | Not in table
Wind | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | Reactive Capability - RENEWABLE |  | Automatic | REACT_CAP_Renewable | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | Y | Y |  |  |  | This is filled automatically in the form, why is there any validation?
Wind | REACTIVE CAPABILITY CURVES DETAILS |  |  | Reactive Capability - RENEWABLE |  |  | Not in table | Not in table
Wind | Reactive Capability Data Provided Below Is Gross Values? | 04/02/2012 - Updated RARF Field Name, DB Field and removed Net from Drop down List in data Validation | ADDED 06/27/2012 | Reactive Capability - RENEWABLE | Wind_ReactiveCapability.View | List | REACT_CAP_Renewable | REACT_CAPB_DATA_GROSS_NET_VAL | Select from the list: GROSS | R | Dropdown List |  |  |  |  | Y | Y |  |  |  | If you only allow "GROSS", then make it automatic
Wind | Reactive Capability Data Provided is from NDCRC Test Data? |  | ADDED 06/27/2012 | Reactive Capability - RENEWABLE | Wind_ReactiveCapability.View | Y/N | REACT_CAP_Renewable | REACT_CAPB_NDCRC_TEST_DATA | Select from the list: Y or N | R | Dropdown List |  |  |  |  | N | N
Wind | If Reactive Capability Data Provided Is From NDCRC test Data Then Enter The Date On Which The Test Was Performed. |  | ADDED 06/27/2012 | Reactive Capability - RENEWABLE | Wind_ReactiveCapability.View | mm/dd/yyyy | REACT_CAP_Renewable | REACT_CAPB_NDCRC_TEST_DATA_DT | This field is optional. Format should be: MM/DD/YYYY | OC | Date |  |  |  |  | N | N
Wind | Mw1 |  |  | Reactive Capability - RENEWABLE |  | MW | REACT_CAP_Renewable | MW1 | 1. MW1 >=0.1 2.MW1<MW2. 3. X(1) <= WMN(Unit Minimal output or LRL) where X(1) represents MW1( Generate a Warning Only when this rule fails). This is a WARNING ONLY | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS |  | N | Y |  |  |  | Business rule #3 is utter nonsense. Glossary requires IRRs to use 0.1 MW
Wind | Lagging MVAR Limit Associated With Mw1 Output | 2015-11-03 | 11/3/2015 Added validation rule 4 updated validation rule #3 | Reactive Capability - RENEWABLE |  | MVAR | REACT_CAP_Renewable | MVAR1LAG | 1. Lagging MVAR limit associated with MW1 output >=0. Generate a Warning only if LAG value is negative 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than or equal to Leading MVAR 4. Lagging MVAR <= Maximum Lagging Operating Capability | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS |  | N | Y |  |  |  | Business rule #2 makes no mathematical sense
Wind | Leading MVAR Limit Associated With Mw1 Output | 2015-11-03 | 11/3/2015 Added validation rule 3 | Reactive Capability - RENEWABLE |  | MVAR | REACT_CAP_Renewable | MVAR1LEAD | 1. Leading MVAR limit associated with MW1 output <=0 .Generate a Warning only if LEAD value is positive 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Leading MVAR >= Maximum Leading Operating Capability | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS |  | N | Y |  |  |  | Business rule #2 makes no mathematical sense
Wind | Mw2 |  |  | Reactive Capability - RENEWABLE |  | MW | REACT_CAP_Renewable | MW2 | 1. MW2 >0 2. MW2<MW3 | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS |  | N | Y
Wind | Lagging MVAR Limit Associated With Mw2 Output | 2015-11-03 | 11/3/2015 Added validation rule 4 updated validation rule #3 | Reactive Capability - RENEWABLE |  | MVAR | REACT_CAP_Renewable | MVAR2LAG | 1. Lagging MVAR limit associated with MW2 output >=0 . Generate a Warning only if LAG value is negative 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR 4. Lagging MVAR <= Maximum Lagging Operating Capability | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS |  | N | Y |  |  |  | Business rule #2 makes no mathematical sense
Wind | Leading MVAR Limit Associated With Mw2 Output | 2015-11-03 | 11/3/2015 Added validation rule 3 | Reactive Capability - RENEWABLE |  | MVAR | REACT_CAP_Renewable | MVAR2LEAD | 1.Leading MVAR limit associated with MW2 output <=0 .Generate a Warning only if LEAD value is positive 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Leading MVAR >= Maximum Leading Operating Capability | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS |  | N | Y |  |  |  | Business rule #2 makes no mathematical sense
Wind | Mw3 |  |  | Reactive Capability - RENEWABLE |  | MW | REACT_CAP_Renewable | MW3 | 1. MW3 >0 2.MW3<MW4 | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS |  | N | Y
Wind | Lagging MVAR Limit Associated With Mw3 Output | 2015-11-03 | 11/3/2015 Added validation rule 4 | Reactive Capability - RENEWABLE |  | MVAR | REACT_CAP_Renewable | MVAR3LAG | 1. Lagging MVAR limit associated with MW3 output >=0 .Generate a Warning only if LAG value is negative 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Generate a Warning only if LAG value is negative 3. Lagging MVAR must always be greater than or equal to Leading MVAR 4. Lagging MVAR <= Maximum Lagging Operating Capability | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS |  | N | Y |  |  |  | Business rule #2 makes no mathematical sense
Wind | Leading MVAR Limit Associated With Mw3 Output | 2015-11-03 | 11/3/2015 Added validation rule 3 | Reactive Capability - RENEWABLE |  | MVAR | REACT_CAP_Renewable | MVAR3LEAD | 1. Leading MVAR limit associated with MW3 output <=0 .Generate a Warning only if LEAD value is positive 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Leading MVAR >= Maximum Leading Operating Capability | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS |  | N | Y |  |  |  | Business rule #2 makes no mathematical sense
Wind | Mw4 | 12/10/13 Updated Validation Rule #3 | 12/10/13 Updated Validation Rule #3 | Reactive Capability - RENEWABLE |  | MW | REACT_CAP_Renewable | MW4 | 1. MW4>0 2. X(n) > = WMX (Unit Max output or HRL), where n is the last MW value in the curve. If the curve has 4 points, X(n) is X(4) [ Generate an Error When this rule fails. 3 Error when MW4 should be >= HRL | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS |  | N | Y
Wind | Lagging MVAR Limit Associated With Mw4 Output | 2015-11-03 | 11/3/2015 Added validation rule 4 updated validation rule #3 | Reactive Capability - RENEWABLE |  | MVAR | REACT_CAP_Renewable | MVAR4LAG | 1. Lagging MVAR limit associated with MW4 output >=0. Generate a Warning only if LAG value is negative 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than or equal to Leading MVAR 4. Lagging MVAR <= Maximum Lagging Operating Capability | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS |  | N | Y |  |  |  | Business rule #2 makes no mathematical sense
Wind | Leading MVAR Limit Associated With Mw4 Output | 2015-11-03 | 11/3/2015 Added validation rule 3 | Reactive Capability - RENEWABLE |  | MVAR | REACT_CAP_Renewable | MVAR4LEAD | 1. Leading MVAR limit associated with MW4 output <=0 .Generate a Warning only if LEAD value is positive 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Leading MVAR >= Maximum Leading Operating Capability | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS |  | N | Y |  |  |  | Business rule #2 makes no mathematical sense
Wind | Maximum Lagging Operating Capability (MVAR) | 2015-11-03 | 11/3/2015 Updated Validation rule 1, 2 and 3 | Reactive Capability - RENEWABLE |  | MVAR | REACT_CAP_Renewable | NETMAXLAG | 1. Maximum Lagging Operating Capability >=0 2. Maximum Lagging Operating Capability >= Maximum Leading Operating Capability | R | Numeric | B,DVB | Lin Xu | MMS |  | Y | Y |  |  |  | Maximum capability may be between two points on the curve
Wind | Maximum Leading Operating Capability (MVAR) | 2015-11-03 | 11/3/2015 updated Validation rule 1 | Reactive Capability - RENEWABLE |  | MVAR | REACT_CAP_Renewable | NETMAXLEAD | 1. Maximum Leading Operating Capability <=0 | R | Numeric | B,DVB | Lin Xu | MMS |  | Y | Y |  |  |  | Maximum capability may be between two points on the curve
Wind | Manufacturer's Capability Curve Submitted? |  |  | Reactive Capability - RENEWABLE |  | Y/N | REACT_CAP_Renewable | MFR_CAP_CURVE | Select from Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 |  |  | N | Y
Solar Photovoltaic (PV) | Reactive Capability - Solar Photovoltaic (PV) |  |  | Reactive Capability - RENEWABLE |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type Selected is 'GEN' where GEN is non-CC non-wind Generation Resources. All the fields in this tab should be filled in. | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,MMS,NMMS
Solar Photovoltaic (PV) | GENERATOR DETAILS |  |  | Reactive Capability - RENEWABLE |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | Unit Name | Do not show Message on Audit or Delta | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | List | RENEWABLE | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | Y | Y
Solar Photovoltaic (PV) | Resource Name (Unit Code/Mnemonic) |  | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | Automatic | RENEWABLE | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | Y | Y
Solar Photovoltaic (PV) | REACTIVE CAPABILITY CURVES DETAILS |  |  | Reactive Capability - RENEWABLE |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | Reactive Capability Data Provided Below Is Gross Values? |  | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | List | RENEWABLE | REACT_CAPB_DATA_GROSS_VAL | Select from the list: GROSS |  | Dropdown List
Solar Photovoltaic (PV) | Reactive Capability Data Provided Below Is From NDCRC Test Data? |  | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | Y/N | RENEWABLE | REACT_CAPB_NDCRC_TEST_DATA | Select from the list: Y or N |  | Dropdown List
Solar Photovoltaic (PV) | If Reactive Capability Data Provided Below Is From NDCRC Test Data Then Enter The Date On Which The Test Was Performed. |  | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | mm/dd/yyyy | RENEWABLE | REACT_CAPB_NDCRC_TEST_DATA_DT | This field is optional. Format should be: MM/DD/YYYY | O | Date
Solar Photovoltaic (PV) | Mw1 |  | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | MW | RENEWABLE | MW1 | 1. MW1 >=0 .1 2. MW1<MW2. 3. X(1) <= WMN(Unit Minimal output) where X(1) represents MW1( Generate a Warning Only when Business Rule#2 fails) | R | Numeric | B,DVB | Lin Xu/ WeiHui
Solar Photovoltaic (PV) | Lagging MVAR limit associated with Mw1 output |  | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | MVAR | RENEWABLE | MVAR1LAG | 1. Lagging MVAR limit associated with MW1 output >=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than or equal to Leading MVAR 4. Lagging MVAR <= Maximum Lagging Operating Capability | R | Numeric | B,DVB | Lin Xu/ WeiHui
Solar Photovoltaic (PV) | Leading MVAR limit associated with Mw1 output |  | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | MVAR | RENEWABLE | MVAR1LEAD | 1. Leading MVAR limit associated with MW1 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Leading MVAR >= Maximum Leading Operating Capability | R | Numeric | B,DVB | Lin Xu/ WeiHui
Solar Photovoltaic (PV) | Mw2 |  | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | MW | RENEWABLE | MW2 | 1. MW2>0 2. MW2<MW3 | R | Numeric | B,DVB | Lin Xu/ WeiHui
Solar Photovoltaic (PV) | Lagging MVAR limit associated with Mw2 output |  | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | MVAR | RENEWABLE | MVAR2LAG | 1.Lagging MVAR limit associated with MW2 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR 4. Lagging MVAR <= Maximum Lagging Operating Capability | R | Numeric | B,DVB | Lin Xu/ WeiHui
Solar Photovoltaic (PV) | Leading MVAR limit associated with Mw2 output |  | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | MVAR | RENEWABLE | MVAR2LEAD | 1. Leading MVAR limit associated with MW2 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Leading MVAR >= Maximum Leading Operating Capability | R | Numeric | B,DVB | Lin Xu/ WeiHui
Solar Photovoltaic (PV) | Mw3 |  | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | MW | RENEWABLE | MW3 | 1. MW3 >0 2. MW3<MW4 | R | Numeric | B,DVB | Lin Xu/ WeiHui
Solar Photovoltaic (PV) | Lagging MVAR limit associated with Mw3 output |  | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | MVAR | RENEWABLE | MVAR3LAG | 1. Lagging MVAR limit associated with MW3 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR 4. Lagging MVAR <= Maximum Lagging Operating Capability | R | Numeric | B,DVB | Lin Xu/ WeiHui
Solar Photovoltaic (PV) | Leading MVAR limit associated with Mw3 output |  | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | MVAR | RENEWABLE | MVAR3LEAD | 1.Leading MVAR limit associated with MW3 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Leading MVAR >= Maximum Leading Operating Capability | R | Numeric | B,DVB | Lin Xu/ WeiHui
Solar Photovoltaic (PV) | Mw4 |  | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | MW | RENEWABLE | MW4 | 1. MW4 >0 2. MW4<MW5 3. X(n) > = WMX (Unit Max output) where n is the last MW value in the curve. If the curve has 4 points, X(n) is X(4) [ Generate a Warning Only When Business Rule#2 Fails] | R | Numeric | B,DVB | Lin Xu/ WeiHui
Solar Photovoltaic (PV) | Lagging MVAR limit associated with Mw4 output |  | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | MVAR | RENEWABLE | MVAR4LAG | 1. Lagging MVAR limit associated with MW4 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than or equal to Leading MVAR 4. Lagging MVAR <= Maximum Lagging Operating Capability | R | Numeric | B,DVB | Lin Xu
Solar Photovoltaic (PV) | Leading MVAR limit associated with Mw4 output |  | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | MVAR | RENEWABLE | MVAR4LEAD | 1.Leading MVAR limit associated with MW4 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Leading MVAR >= Maximum Leading Operating Capability | R | Numeric | B,DVB | Lin Xu
Solar Photovoltaic (PV) | Mw5 - Unity Power Factor |  | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | MW | RENEWABLE | MW5UNITYPF | 1. MW5 >0 2. MW5 >MW4 3. MW5 =>= HRL | R | Numeric | B,DVB | Lin Xu
Solar Photovoltaic (PV) | Maximum Lagging Operating Capability |  | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | MVAR | RENEWABLE | NETMAXLAG | 1.Net Maximum Lagging Operating Capability >=0 2. Maximum Lagging Operating Capability >= Maximum Leading Operating Capability 2. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB | Lin Xu/WeiHui
Solar Photovoltaic (PV) | Maximum Leading Operating Capability |  | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | MVAR | RENEWABLE | NETMAXLEAD | 1.Net Maximum Leading Operating Capability <=0 | R | Numeric | B,DVB | Lin Xu/WeiHui
Solar Photovoltaic (PV) | Manufacturer's Capability Curve submitted? |  | Added 05/01/2017 | Reactive Capability - RENEWABLE |  | Y/N | RENEWABLE | MFR_CAP_CURVE | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0
CC | CC Configurations |  |  | CC Config |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type selected is 'CC'. Can register up to 3 trains at one site. Register Operationally Unique Configurations. | C |  |  |  | NMMS
CC | GENERATOR DETAILS |  |  | CC Config |  |  | Not in table | Not in table
CC | TRAIN CODE | Corrected 02/23/2012 |  | CC Config |  | List | TRAIN | TRAIN_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | [5 empty] | N | N
CC | SITE CODE |  |  | CC Config |  | Automatic | CCUNIT_CONFIGURATION | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | A | Character |  |  |  |  | N | N |  |  |  | This is filled automatically in the form, why is there any validation?
CC | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | CC Config |  | List | CCUNIT_CONFIGURATION | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | N
CC | CONFIGURATION DETAILS |  |  | CC Config |  |  | Not in table | Not in table
CC | Configuration # | 04/09/2012 Add Column to Database | ADDED 06/27/2012 | CC Config |  | # | CCUNIT_CONFIGURATION | CONFIG_NO | Data type is Numeric | R | Numeric |  | WCS |  |  | N | N
CC | Configuration Code |  |  | CC Config |  | Automatic | CCUNIT_CONFIGURATION | CONFIG_CODE | Concantanate SITE_CODE, TRAIN_CODE and CONFIG_NUM | A | [5 empty] | N | N |  |  |  | This is filled automatically in the form, why is there any validation?
CC | Configuration Type |  |  | CC Config |  | List | CCUNIT_CONFIGURATION | CONFIG_TYPE | There is no limit to the no. of configurations that can be registered but they should be Operationally Unique and should Increase in number of units and MWs from left to right | R | Integer | B,DVB | RARF Guide Version 4.0/ Lin Xu | NMMS |  | N | N
CC | CC Transitions |  |  | CC Transitions |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type selected is 'CC'. Should be populated (should match it) from CC configuration | C |  |  | Jamil Daouk | EMS,MMS,NMMS
CC | GENERATOR DETAILS |  |  | CC Transitions |  |  | Not in table | Not in table
CC | Sitecode |  |  | CC Transitions |  | List | TRANSITIONS | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R | [5 empty] | N | N
CC | Mnemonic for Combine Cyle Train |  |  | CC Transitions |  | List | TRANSITIONS | TRAIN_CODE | CONCANTENATE SITE_CODE and TRAIN_NAME | R | [5 empty] | N | N
CC | Configuration Code From |  | UPDATED 03/2012 | CC Transitions |  | List | TRANSITIONS | CONFIGCODE_FROM | 1.Each configuration in Transitions including Offline can be reached. Each configuration in CC1 Transitions including Offline can reach at least one of the other configurations including Offline . 2.Values allowed are X for Main Transition , A for Alternate Transition ,Null for Non Transition 3. 1.If a RARF is submitted that does not have the first Transition from OFFLINE, Generate an ERROR. 4. Generate a Warning if the Transitions skip. For instance the transitions table has ‘Offline’ to ‘CC1_2’ and so it skips CC1_1. This is an acceptable possibility, but the resource needs to be notified of it because they would not be in RUC until the CC1_2 configuration, in this case would only be in RUC with both units available, not just the single unit associated to CC1_1. 5) Generate a Warning if the Transition is missing for a Configuration | C | [5 empty] | N | N
CC | Configuration Code To |  | UPDATED 03/2012 | CC Transitions |  | List | TRANSITIONS | CONFIGCODE_TO | 1.Each configuration in CC2 Transitions except Offline needs to be defined in CC2 Config. 2.Each configuration in CC2 Transitions including Offline can be reached. Each configuration in CC2 Transitions including Offline can reach at least one of the other configurations including Offline 3. 1.If a RARF is submitted that does not have the first Transition from OFFLINE, Generate an ERROR. 4. Generate a Warning if the Transitions skip. For instance the transitions table has ‘Offline’ to ‘CC1_2’ and so it skips CC1_1. This is an acceptable possibility, but the resource needs to be notified of it because they would not be in RUC until the CC1_2 configuration, in this case would only be in RUC with both units available, not just the single unit associated to CC1_1. 5. Generate a Warning if the Transition is missing for a Configuration | C | [5 empty] | N | N
Generation | Planning - GEN |  |  | Planning - GEN |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type Selected is 'GEN' where GEN is non-CC non-wind Generation Resources. This tab is unit specific and required for all non-cc non-wind units. All the fields in this section should be complete. For all the UNITS in the Unit info-GEN tab , there should be corresponding data in Planning-GEN Tab | C |  |  | RARF Guide Version 4.0 | MMS,NMMS
Generation | GENERATOR DETAILS |  |  | Planning - GEN |  |  | Not in table | Not in table
Generation | Unit Name | Do not show Message on Audit or Delta |  | Planning - GEN |  | List | GENERATION | UNIT_NAME | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | Y
Generation | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | Planning - GEN |  | Automatic | GENERATION | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | Y
Generation | PLANNING DETAILS |  |  | Planning - GEN |  |  | Not in table | Not in table
Generation | What Is The Mva Base That The Following Data Is Based On? |  |  | Planning - GEN |  | MVA | GENERATION | MVABASE | 1) This field is required 2) Value must be Float 3) Generate a Warning if MVABASE > 2500 4)[ If MVABASE value is within +/- 25% range of Unit Name Plate Rating] OR [MVABASE value = 100, then it is OK.If MVABASE value is outside the +/- 25% range of Unit Name Plate Rating, then Generate a Warning that the MVABSE is outside the typical +/- 25% variation of unit name plate rating | R | Float | B | Planning Team |  |  | N | Y
Generation | What Is The Kv Base That The Following Data Is Based On? |  |  | Planning - GEN |  | KV | GENERATION | KVBASE | 1) This field is required 2) Value must be >0 and <1000 3) Generate a Warning if KVBASE > 40 4) If KVBASE value is within +/- 25% range of Unit KV value in the unit-information tab then it is OK.If If KVBASE value is outside the typical +/- 25% variation of Unit KV value in the unit-information tab then Generate a Warning that the KVBASE is outside the typical +/- 25% variation of Unit KV value | R | Float | B,DVB | Planning Team |  |  | N | Y
Generation | Direct Axis Subtransient Reactance, X"di (unsaturated) | 05/06/2013 Added Validation #4 and updated Validation 2. |  | Planning - GEN |  | p.u. | GENERATION | DIRECT_AXIS_SUBSTNT_REACTANCE | 1) This field is required and Data type is float 2) Value must be between 0.0 and 1.0 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) 4) Generate a Warning if X"di (unsaturated) < X"dv (saturated) | R | Float | B | Planning Team |  |  | N | Y
Generation | Direct Axis Transient Reactance, X'di (unsaturated) | 05/06/2013 Added Validation #4 |  | Planning - GEN |  | p.u. | GENERATION | DIRECT_AXIS_TRANSNT_REACTANCE | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) 4) Generate a Warning if X’di (unsaturated) < X’dv (saturated) | R | Float | B | Planning Team |  |  | N | Y
Generation | Positive Sequence (Synchronous) Z (unsaturated) | 2/10/2016Updated Field Name 07/03/2012 Change field name in Data base |  | Planning - GEN |  | R in p.u. | GENERATION | POSITIVE_SEQ_Z_R_UNSATURATED_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R |  |  | Planning Team |  |  | N | Y
Generation | Positive Sequence (Synchronous) Z (unsaturated) | 3/1/2016 Updated validation rule #3 2/10/2016Updated Field Name 7/03/2012 Change field name in Data base | 3/1/2016 Updated validation rule #3 2/10/2016 Field Name Updated ADDED 06/27/2012 | Planning - GEN |  | X in p.u. | GENERATION | POSITIVE_SEQ_Z_X_UNSATURATED_PU | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base:Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60* [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 3.0 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R |  |  | Planning Team |  |  | N | Y
Generation | Negative Sequence Z (unsaturated) | 07/03/2012 Change field name in Data base |  | Planning - GEN |  | R in p.u. | GENERATION | NEGATIVE_SEQ_Z_R_UNSATURATED_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1 |  |  |  | Planning Team |  |  | N | Y
Generation | Negative Sequence Z (unsaturated) | 07/03/2012 Change field name in Data base 11/10/2015 Update Valadation Rule #2 | 11/10/2015 Change Validation Rule # 2 2) Value must be between 0 and 100, OR equal to 99999 for Solar PV and Battery Energy Storage Systems | Planning - GEN |  | X in p.u. | GENERATION | NEGATIVE_SEQ_Z_X-UNSATURATED_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 100, or optionally 99999 if resource category is Power Storage or Other and unit type is OT" if 99999 is valid but not required 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] |  |  |  | Planning Team |  |  | N | Y
Generation | Zero Sequence Z (unsaturated) | 07/03/2012 Change field name in Data base |  | Planning - GEN |  | R in p.u. | GENERATION | ZERO_SEQ_Z_R_UNSATURATED_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U |  |  |  | Planning Team |  |  | N | Y
Generation | Zero Sequence Z (unsaturated) | 07/03/2012 Change field name in Data base 11/10/2015 Update Valadation Rule #2 | 11/10/2015 Change Validation Rule # 2 2) Value must be between 0 and 100, OR equal to 99999 for Solar PV and Battery Energy Storage Systems | Planning - GEN |  | X in p.u. | GENERATION | ZERO_SEQ_Z_X_UNSATURATED_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 100, or optionally 99999 if resource category is Power Storage or Other and unit type is OT" if 99999 is valid but not required 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] |  |  |  | Planning Team |  |  | N | Y
Generation | Direct Axis Subtransient Reactance, X"dv (saturated) |  | ADDED 06/27/2012 | Planning - GEN | Audit - Planning_GEN.View Delta -Planning_GENERATION.View | p.u. | GENERATION | DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value.(* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team |  |  | N | Y
Generation | Direct Axis Transient Reactance, X'dv (saturated) |  | ADDED 06/27/2012 | Planning - GEN | Audit - Planning_GEN.View Delta -Planning_GENERATION.View | p.u. | GENERATION | DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team |  |  | N | Y
Generation | Positive Sequence (Synchronous) Z (saturated - R in p.u.): | 06/28/2012 updated | 2/10/2016 Field Name Updated ADDED 06/27/2012 | Planning - GEN | Audit - Planning_GEN.View Delta -Planning_GENERATION.View | R in p.u. | GENERATION | POSITIVE_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B | Planning Team | NMMS |  | N | Y
Generation | Positive Sequence (Synchronous) Z (saturated) | 3/1/2016 Updated validation rule #3 2/10/2016Updated Field Name 7/03/2012 Change field name in Data base | 3/1/2016 Updated validation rule #3 2/10/2016 Field Name Updated ADDED 06/27/2012 | Planning - GEN | Audit - Planning_GEN.View Delta -Planning_GENERATION.View | X in p.u. | GENERATION | POSITIVE_SEQ_Z_X_PU | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 3.0 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B | Planning Team | NMMS |  | N | Y
Generation | Negative Sequence Z (saturated) | 06/28/2012 updated | ADDED 06/27/2012 | Planning - GEN | Audit - Planning_GEN.View Delta -Planning_GENERATION.View | R in p.u. | GENERATION | NEGATIVE_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B | Planning Team |  |  | N | Y
Generation | Negative Sequence Z (saturated) | 06/28/2012 updated 11/10/2015 Update Valadation Rule #2 | ADDED 06/27/2012 11/10/2015 Change Validation Rule # 2 2) Value must be between 0 and 100, OR equal to 99999 for Solar PV and Battery Energy Storage Systems | Planning - GEN | Audit - Planning_GEN.View Delta -Planning_GENERATION.View | X in p.u. | GENERATION | NEGATIVE_SEQ_Z_X_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 100, or optionally 99999 if resource category is Power Storage or Other and unit type is OT" if 99999 is valid but not required 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team |  |  | N | Y
Generation | Zero Sequence Z (saturated) | 06/28/2012 updated | ADDED 06/27/2012 | Planning - GEN | Audit - Planning_GEN.View Delta -Planning_GENERATION.View | R in p.u. | GENERATION | ZERO_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U | R | Float | B | Planning Team | NMMS |  | N | Y
Generation | Zero Sequence Z (saturated) | 06/28/2012 updated 11/10/2015 Update Valadation Rule #2 | ADDED 06/27/2012 11/10/2015 Change Validation Rule # 2 2) Value must be between 0 and 100, OR equal to 99999 for Solar PV and Battery Energy Storage Systems | Planning - GEN | Audit - Planning_GEN.View Delta -Planning_GENERATION.View | X in p.u. | GENERATION | ZERO_SEQ_Z_X_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 100, or optionally 99999 if resource category is Power Storage or Other and unit type is OT" if 99999 is valid but not required 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team | NMMS |  | N | Y
Generation | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | 10/04/2012 Change rule #2 and remove rule #3 | ADDED 06/27/2012 | Planning - GEN | Audit - Planning_GEN.View Delta -Planning_GENERATION.View | p.u. | GENERATION | ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU | 1) This field is required and Data type is numeric 2) Value must be greater than or equal to 0.0 and less than or equal to 99999.0 | R |  |  | Model Adminstration |  |  | N | Y
Generation | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | 10/04/2012 Change rule #2 and remove rule #3 | ADDED 06/27/2012 | Planning - GEN | Audit - Planning_GEN.View Delta -Planning_GENERATION.View | p.u. | GENERATION | ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU | 1) This field is required and Data type is numeric 2.) Value must be greater than or equal to 0.0 and less than or equal to 99999.0 | R |  |  | Model Adminstration |  |  | N | Y
Generation | GENERATOR AUXILIARY LOAD |  |  | Planning - GEN |  |  | Not in table | Not in table
Generation | Average Amount of Auxiliary Real Power | 09/06/13 changed field type to Conditional 10/08/2012 Updated Validation rule CR46800 | 09/06/13 updated rules 4 & 5 | Planning - GEN | PLANNING_GEN.View | MW | GENERATION | AUX_MWTOTAL | 1) This field is required 2) Data type is float 3) Value must be < Reactive Capability – GEN – MW4 4) Warn if value > Reactive Capability – GEN – MW4 * 0.20 | R | Float | B | Planning Team |  |  | Y | Y
Generation | Average Amount of Auxiliary Reactive Power | 09/06/13 changed field type to Conditional 10/19/2012 updated #3. 10/08/2012 Updated Validation rule CR46800 | 09/06/13 updated rules 4 & 5 | Planning - GEN | PLANNING_GEN.View | MVAR | GENERATION+B858A858:H858K858C858:H858 | AUX_MVARTOTAL | 1) This field is conditionally required (see below) 2) Data type is Float 3) Warn if value > Reactive Capability – GEN – Lagging MVAR Limit Associated With Mw4 Output * 0.5 Either Auxiliary Reactive Power or Power Factor is required | C | Float | B | Planning Team |  |  | Y | Y
Generation | Auxiliary Load Power Factor | 09/06/13 updated spreadsheet to reflect field is conditional. 10/08/2012 Updated Validation rule CR46800 | 09/06/13 updated spreadsheet to reflect field is conditional. ADDED 06/27/2012 | Planning - GEN | Audit - Planning_GEN.View Delta -Planning_GENERATION.View |  | GENERATION | AUX_LOAD_PWR_FACT | Between .6 and 1.0 conditionally required (see below) Either Auxiliary Reactive Power or Power Factor is required | C |  |  | Planning Team |  |  | Y | Y
Generation | Generation Auxiliary Load Characteristics for Mw Load |  |  | Planning - GEN |  |  | Not in table | Not in table
Generation | Large Motor, Percent Of Total Mw Load | 09/06/13 changed field type to Conditional 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated rule 1 05/03/2012 removed percent from label on form | Planning - GEN | PLANNING_GEN.View |  | GENERATION | AUXMW_LARGEMTR_PCT | 1)This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS |  | N | N
Generation | Small Motor, Percent Of Total Mw Load | 09/06/13 changed field type to Conditional 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated rule 1 05/03/2012 removed percent from label on form | Planning - GEN | PLANNING_GEN.View |  | GENERATION | AUXMW_SMALLMTR_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS |  | N | N
Generation | Resistive (heating) Load, Percent Of Total Mw Load | 09/06/13 changed field type to Conditional 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated rule 1 05/03/2012 removed percent from label on form | Planning - GEN | PLANNING_GEN.View |  | GENERATION | AUXMW_RESISTIVE_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS |  | N | N
Generation | Discharge Lighting, Percent Of Total Mw Load | 09/06/13 changed field type to Conditional 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated rule 1 05/03/2012 removed percent from label on form | Planning - GEN | PLANNING_GEN.View |  | GENERATION | AUXMW_DISCHARGE_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS |  | N | N
Generation | Other, Percent Of Total Mw Load | 09/06/13 changed field type to Conditional 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated rule 1 05/03/2012 removed percent from label on form | Planning - GEN | PLANNING_GEN.View |  | GENERATION | AUXMW_OTHER_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS |  | N | N
Generation | Generation Auxiliary Load Characteristics For MVAR Load |  |  | Planning - GEN |  |  | Not in table | Not in table
Generation | Large Motor, Percent Of Total Mvar Load | 09/06/13 changed field type to Conditional 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated rule 1 05/03/2012 removed percent from label on form | Planning - GEN | PLANNING_GEN.View |  | GENERATION | AUXMVAR_LARGEMTR_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS |  | N | N
Generation | Small Motor, Percent Of Total Mvar Load | 09/06/13 changed field type to Conditional 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated rule 1 05/03/2012 removed percent from label on form | Planning - GEN | PLANNING_GEN.View |  | GENERATION | AUXMVAR_SMALLMTR_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS |  | N | N
Generation | Discharge Lighting, Percent Of Total Mvar Load | 09/06/13 changed field type to Conditional 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated rule 1 05/03/2012 removed percent from label on form | Planning - GEN | PLANNING_GEN.View |  | GENERATION | AUXMVAR_DISCHARGE_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS |  | N | N
Generation | Other, Percent Of Total Mvar Load | 09/06/13 changed field type to Conditional 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated rule 1 05/03/2012 removed percent from label on form | Planning - GEN | PLANNING_GEN.View |  | GENERATION | AUXMVAR_OTHER_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS |  | N | N
Generation | PSSE MODEL : THE FOLLOWING LIST OF FILES ARE REQUIRED TO BE SUBMITTED IF THIS IS AN INITIAL REGISTRATION OR IF THERE ARE CHANGES MODIFYING PREVIOUSLY SUBMITTED PSSE FILES. PLEASE INCLUDE ALL PSSE FILES IN A ZIP OR COMPRESSED FOLDER FILE ALONG WITH YOUR RARF SUBMITTAL IN THE SAME SERVICE REQUEST. |  |  | Planning - GEN |  |  | Not in table | Not in table
Generation | Generator Form |  |  | Planning - GEN |  |  | Not in table | Not in table | [7 empty] | N | Y
Generation | Turbine-governor Form |  |  | Planning - GEN |  |  | Not in table | Not in table | [7 empty] | N | Y
Generation | Excitation Form |  |  | Planning - GEN |  |  | Not in table | Not in table | [7 empty] | N | Y
Generation | Power System Stabilizer Form (required If There Is A Power System Stabilizer) |  |  | Planning - GEN |  |  | Not in table | Not in table | [7 empty] | N | Y
Generation | Compensator Form (required If There Is A Compensator) |  |  | Planning - GEN |  |  | Not in table | Not in table | [7 empty] | N | Y
Generation | Over Excitation Limiter Form (required If There Is An Over Excitation Limiter) |  |  | Planning - GEN |  |  | Not in table | Not in table | [7 empty] | N | Y
Generation | Under Excitation Limiter Form (required If There Is An Under Excitation Limiter) |  |  | Planning - GEN |  |  | Not in table | Not in table | [7 empty] | N | Y
CC | Planning - CC |  |  | Planning - CC |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type selected is 'CC'.This tab is unit specific and is required for all CC units. All the fields in this tab are required. Can register up to 3 trains at one site. This information is required for each unit of the train. For all the CCUNITS in the unit info-cc tab , there should be corresponding data in planning-cc Tab | C |  |  | RARF Glossary Version 4.0 | MMS
CC | GENERATOR DETAILS |  |  | Planning - CC |  |  | Not in table | Not in table
CC | Unit Name | Do not show Message on Audit or Delta |  | Planning - CC |  | List | CCUNIT | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | Y | Y
CC | SITE_CODE |  |  | Planning - CC |  | Automatic | CCUNIT | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | A | Character |  |  |  |  | N | N |  |  |  | This is filled automatically in the form, why is there any validation?
CC | Resource Name (Unit Code/mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | Planning - CC |  | Automatic | CCUNIT | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | Y | Y |  |  |  | This is filled automatically in the form, why is there any validation?
CC | PLANNING DETAILS |  |  | Planning - CC |  |  | Not in table | Not in table
CC | What Is The Mva Base That The Following Data Is Based On? |  |  | Planning - CC |  | MVA | CCUNIT | MVABASE | 1) This field is required 2) Value must be Float 3) Generate a Warning if MVABASE > 2500 4)[ If MVABASE value is within +/- 25% range of Unit Name Plate Rating] OR [MVABASE value = 100, then it is OK.If MVABASE value is outside the +/- 25% range of Unit Name Plate Rating, then Generate a Warning that the MVABSE is outside the typical +/- 25% variation of unit name plate rating | R | Float | B | Planning Team |  |  | N | Y
CC | What Is The Kv Base That The Following Data Is Based On? |  |  | Planning - CC |  | kV | CCUNIT | KVBASE | 1) This field is required 2) Value must be >0 and <1000 3) Generate a Warning if KVBASE > 40 4) If KVBASE value is within +/- 25% range of Unit KV value in the unit-information tab then it is OK.If If KVBASE value is outside the typical +/- 25% variation of Unit KV value in the unit-information tab then Generate a Warning that the KVBASE is outside the typical +/- 25% variation of Unit KV value | R | Float | B,DVB | Planning Team |  |  | N | Y
CC | Direct Axis Subtransient Reactance, X"di (unsaturated) | 05/06/2013 Added Validation #4 and updated Validation 2. |  | Planning - CC |  | p.u. | CCUNIT | DIRECT_AXIS_SUBSTNT_REACTANCE | 1) This field is required and Data type is float 2) Value must be between and 0 and 1. 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) 4) Generate a Warning if X"di (unsaturated) < X"dv (saturated) | R | Float | B | Planning Team |  |  | N | Y
CC | Direct Axis Transient Reactance, X'di (unsaturated) | 05/06/2013 Added Validation #4 |  | Planning - CC |  | p.u. | CCUNIT | DIRECT_AXIS_TRANSNT_REACTANCE | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) 4) Generate a Warning if X"di (unsaturated) < X"dv (saturated) | R | Float | B | Planning Team |  |  | N | Y
CC | Positive Sequence (Synchronous) Z (Unsaturated - R in p.u.): | 2/10/2016Updated Field Name 07/03/2012 Change field name in Data base |  | Planning - CC |  | R in p.u. | CCUNIT | POSITIVE_SEQ_Z_R_UNSATURATED_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R |  |  | Planning Team |  |  | N | Y
CC | Positive Sequence (Synchronous) Z (Unsaturated - X in p.u.): | 3/1/2016 Updated validation rule #3 2/10/2016Updated Field Name 7/03/2012 Change field name in Data base | 3/1/2016 Updated validation rule #3 2/10/2016 Field Name Updated ADDED 06/27/2012 | Planning - CC |  | X in p.u. | CCUNIT | POSITIVE_SEQ_Z_X_UNSATURATED_PU | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 3.0 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team |  |  | N | Y
CC | Negative Sequence Z (unsaturated) | 07/03/2012 Change field name in Data base |  | Planning - CC |  | R in p.u. | CCUNIT | NEGATIVE_SEQ_Z_R_UNSATURATED_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning when value is > 1.0 P.U | R |  |  | Planning Team |  |  | N | Y
CC | Negative Sequence Z (unsaturated) | 07/03/2012 Change field name in Data base |  | Planning - CC |  | X in p.u. | CCUNIT | NEGATIVE_SEQ_Z_X-UNSATURATED_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team |  |  | N | Y
CC | Zero Sequence Z (unsaturated) | 07/03/2012 Change field name in Data base |  | Planning - CC |  | R in p.u. | CCUNIT | ZERO_SEQ_Z_R_SATURATED_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U | R |  |  | Planning Team |  |  | N | Y
CC | Zero Sequence Z (unsaturated) | 07/03/2012 Change field name in Data base |  | Planning - CC |  | X in p.u. | CCUNIT | ZERO_SEQ_Z_X_SATURATED_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team |  |  | N | Y
CC | Direct Axis Subtransient Reactance, X"dv (saturated) |  | ADDED 06/27/2012 | Planning - CC | Planning_CC.View | p.u. | CCUNIT | DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value.(* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team |  |  | N | Y
CC | Direct Axis Transient Reactance, X'dv (saturated) |  | ADDED 06/27/2012 | Planning - CC | Planning_CC.View | p.u. | CCUNIT | DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team |  |  | N | Y
CC | Positive Sequence (Synchronous) Z (Saturated - R in p.u.): | 2/10/2016Updated Field Name 07/03/2012 Change field name in Data base | ADDED 06/27/2012 | Planning - CC | Planning_CC.View | R in p.u. | CCUNIT | POSITIVE_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B | Planning Team | NMMS |  | N | Y
CC | Positive Sequence (Synchronous) Z (Saturated - X in p.u.): | 3/1/2016 Updated validation rule #3 2/10/2016Updated Field Name 7/03/2012 Change field name in Data base | 3/1/2016 Updated validation rule #3 2/10/2016 Field Name Updated ADDED 06/27/2012 | Planning - CC | Planning_CC.View | X in p.u. | CCUNIT | POSITIVE_SEQ_Z_X_PU | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 3.0 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B | Planning Team | NMMS |  | N | Y
CC | Negative Sequence Z (saturated) | 06/28/2012 updated | ADDED 06/27/2012 | Planning - CC | Planning_CC.View | R in p.u. | CCUNIT | NEGATIVE_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B | Planning Team |  |  | N | Y
CC | Negative Sequence Z (saturated) | 06/28/2012 updated | ADDED 06/27/2012 | Planning - CC | Planning_CC.View | X in p.u. | CCUNIT | NEGATIVE_SEQ_Z_X_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team |  |  | N | Y
CC | Zero Sequence Z (saturated) | 06/28/2012 updated | ADDED 06/27/2012 | Planning - CC | Planning_CC.View | R in p.u. | CCUNIT | ZERO_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U | R | Float | B | Planning Team | NMMS |  | N | Y
CC | Zero Sequence Z (saturated) | 06/28/2012 updated | ADDED 06/27/2012 | Planning - CC | Planning_CC.View | X in p.u. | CCUNIT | ZERO_SEQ_Z_X_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team | NMMS |  | N | Y
CC | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | 10/04/2012 Change rule #2 and remove rule #3 | ADDED 06/27/2012 | Planning - CC | Planning_CC.View | p.u. | CCUNIT | ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU | 1) This field is required and Data type is numeric 2) Value must be greater than or equal to 0.0 and less than or equal to 99999.0 | R |  |  | Model Adminstration |  |  | N | Y
CC | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | 10/04/2012 Change rule #2 and remove rule #3 | ADDED 06/27/2012 | Planning - CC | Planning_CC.View | p.u. | CCUNIT | ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU | 1) This field is required and Data type is numeric 2) Value must be greater than or equal to 0.0 and less than or equal to 99999.0 | R |  |  | Model Adminstration |  |  | N | Y
CC | GENERATOR AUXILIARY LOAD |  |  | Planning - CC |  |  | Not in table | Not in table
CC | Average Amount of Auxiliary Real Power | 09/06/13 changed field type to Conditional 10/08/2012 Updated Validation rule CR46800 | 09/06/13 updated rules 4 & 5 | Planning - CC | PLANNING_CC.View | MW | CCUNIT | AUX_MWTOTAL | 1) This field is required 2) Data type is float 3) Value must be < Reactive Capability – WIND– MW4 4) Warn if value > Reactive Capability – WIND – MW4 * 0.20 | R | Planning Team | Shouldn't the average amount be referenced to full load on the generator? Also, the glossary is jacked up on this. | Planning Team |  |  | Y | Y |  |  |  | Shouldn't the average amount be referenced to full load on the generator? Also, the glossary is jacked up on this.
CC | Average Amount of Auxiliary Reactive Power | 09/06/13 changed field type to Conditional 10/08/2012 Updated Validation rule CR46800 | 09/06/13 updated rules 4 & 5 | Planning - CC | PLANNING_CC.View | MVAR | CCUNIT | AUX_MVARTOTAL | 1) This field is conditionally required (see below) 2) Data type is Float 3) Warn if value > Reactive Capability – CC – Lagging MVAR Limit Associated With Mw4 Output * 0.5 4)Either Auxiliary Reactive Power or Power Factor is required | C | Float | B | Planning Team |  |  | Y | Y
CC | Auxiliary Load Power Factor | 09/06/13 updated spreadsheet to reflect field is conditional. 10/08/2012 Updated Validation rule CR46800 | 09/06/13 updated spreadsheet to reflect field is conditional. ADDED 06/27/2012 | Planning - CC | Planning_CC.View |  | CCUNIT | AUX_LOAD_PWR_FACT | Between .6 and 1.0 conditionally required (see below) Either Auxiliary Reactive Power or Power Factor is required | C |  |  | Planning Team |  |  | Y | Y
CC | Generation Auxiliary Load Characteristics For Mw Load |  |  | Planning - CC |  |  | Not in table | Not in table
CC | Large Motor, Percent Of Total Mw Load | 09/06/13 changed field type to Conditional 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated rule 1 05/03/2012 removed percent from label on form | Planning - CC | PLANNING_CC.View |  | CCUNIT | AUXMW_LARGEMTR_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent (where 1 = 100%) 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Percent | B,DVB | Planning Team | MMS |  | N | N |  |  |  | 4160V is greater than 2400V, so why even mention 4160V?
CC | Small Motor, Percent Of Total Mw Load | 09/06/13 changed field type to Conditional 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated rule 1 05/03/2012 removed percent from label on form | Planning - CC | PLANNING_CC.View |  | CCUNIT | AUXMW_SMALLMTR_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent (where 1 = 100%) 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Percent | B,DVB | Planning Team | MMS |  | N | N |  |  |  | 4160V is greater than 2400V, so why even mention 4160V?
CC | Resistive (heating) Load, Percent Of Total Mw Load | 09/06/13 changed field type to Conditional 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated rule 1 05/03/2012 removed percent from label on form | Planning - CC | PLANNING_CC.View |  | CCUNIT | AUXMW_RESISTIVE_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent (where 1 = 100%) 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB | Planning Team | MMS |  | N | N
CC | Discharge Lighting, Percent Of Total Mw Load | 09/06/13 changed field type to Conditional 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated rule 1 05/03/2012 removed percent from label on form | Planning - CC | PLANNING_CC.View |  | CCUNIT | AUXMW_DISCHARGE_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent (where 1 = 100%) 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB | Planning Team | MMS |  | N | N
CC | Other, Percent Of Total Mw Load | 09/06/13 changed field type to Conditional 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated rule 1 05/03/2012 removed percent from label on form | Planning - CC | PLANNING_CC.View |  | CCUNIT | AUXMW_OTHER_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent (where 1 = 100%) 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB | Planning Team | MMS |  | N | N
CC | Generation Auxiliary Load Characteristics for MVAR Load |  |  | Planning - CC |  |  | Not in table | Not in table
CC | Large Motor, Percent Of Total Mvar Load | 09/06/13 changed field type to Conditional 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated rule 1 05/03/2012 removed percent from label on form | Planning - CC | PLANNING_CC.View |  | CCUNIT | AUXMVAR_LARGEMTR_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent (where 1 = 100%) 3) SUM(All Generation Auxiliary Load Characteristics for MW MVAR Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Percent | B,DVB | Planning Team | MMS |  | N | N
CC | Small Motor, Percent Of Total Mvar Load | 09/06/13 changed field type to Conditional 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated rule 1 05/03/2012 removed percent from label on form | Planning - CC | PLANNING_CC.View |  | CCUNIT | AUXMVAR_LARGEMTR_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent (where 1 = 100%) 3) SUM(All Generation Auxiliary Load Characteristics for MW MVAR Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Percent | B,DVB | Planning Team | MMS |  | N | N
CC | Discharge Lighting, Percent Of Total Mvar Load | 09/06/13 changed field type to Conditional 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated rule 1 05/03/2012 removed percent from label on form | Planning - CC | PLANNING_CC.View |  | CCUNIT | AUXMVAR_DISCHARGE_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent (where 1 = 100%) 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | C | Percent | B,DVB | Planning Team | MMS |  | N | N
CC | Other, Percent Of Total Mvar Load | 09/06/13 changed field type to Conditional 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated rule 1 05/03/2012 removed percent from label on form | Planning - CC | PLANNING_CC.View |  | CCUNIT | AUXMVAR_OTHER_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent (where 1 = 100%) 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | C | Percent | B,DVB | Planning Team | MMS |  | N | N
CC | PSSE MODEL : THE FOLLOWING LIST OF FILES ARE REQUIRED TO BE SUBMITTED IF THIS IS AN INITIAL REGISTRATION OR IF THERE ARE CHANGES MODIFYING PREVIOUSLY SUBMITTED PSSE FILES. PLEASE INCLUDE ALL PSSE FILES IN A ZIP OR COMPRESSED FOLDER FILE ALONG WITH YOUR RARF SUBMITTAL IN THE SAME SERVICE REQUEST. |  |  | Planning - CC |  |  | Not in table | Not in table
CC | Generator Form |  |  | Planning - CC |  |  | Not in table | Not in table | [7 empty] | N | Y
CC | Turbine-governor Form |  |  | Planning - CC |  |  | Not in table | Not in table | [7 empty] | N | Y
CC | Excitation Form |  |  | Planning - CC |  |  | Not in table | Not in table | [7 empty] | N | Y
CC | Power System Stabilizer Form (required If There Is A Power System Stabilizer) |  |  | Planning - CC |  |  | Not in table | Not in table | [7 empty] | N | Y
CC | Compensator Form (required If There Is A Compensator) |  |  | Planning - CC |  |  | Not in table | Not in table | [7 empty] | N | Y
CC | Over Excitation Limiter Form (required If There Is An Over Excitation Limiter) |  |  | Planning - CC |  |  | Not in table | Not in table | [7 empty] | N | Y
CC | Under Excitation Limiter Form (required If There Is An Under Excitation Limiter) |  |  | Planning - CC |  |  | Not in table | Not in table | [7 empty] | N | Y
Wind | Planning - WIND |  |  | Planning - RENEWABLE |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type selected is 'WIND '.This tab is unit specific and is required for all wind units. All the fields in this tab should be required. For all the UNITS in the Unit info-WIND tab , there should be corresponding data in Planning-WIND Tab | C |  |  | RARF Guide Version 4.0 | MMS
Wind | Resource Name (Unit Code/Mnemonic) | Do not show Message on Audit or Delta |  | Planning - RENEWABLE |  | all caps | RENEWABLE | UNIT_NAME | 1.This field is not null. Data type: Character. 2.Can not exceed 8 characters for single owner units 3. Should not allow spaces | R A | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | Y | Y |  |  |  | This is filled automatically in the form, why is there any validation?
Wind | GENERATOR AUXILIARY LOAD |  |  | Planning - RENEWABLE |  |  | Not in table | Not in table
Wind | Average Amount Of Auxiliary Real Power | 09/06/13 Updated validation rules 4 and 5 10/08/2012 Updated Validation rule CR46800 | 09/06/13 Updated validation rules 4 and 5 ADDED 06/27/2012 | Planning - RENEWABLE | PLANNING_WIND.View | MW | RENEWABLE | AUX_MWTOTAL | 1) This field is required 2) Data type is float 3) Value must be < Reactive Capability – WIND– MW4 4) Warn if value > Reactive Capability – WIND – MW4 * 0.20 | R | Float | B | Planning Team |  |  | Y | Y |  |  |  | Shouldn't the average amount be referenced to full load on the generator? Also, the glossary is jacked up on this.
Wind | Average Amount Of Auxiliary Reactive Power | 09/06/13 Updated validation rules 4 and 5 and Updated field type to Conditional 10/19/2012 updated #3. 10/08/2012 Updated Validation rule CR46800 | 09/06/13 Updated validation rules 4 and 5 and ADDED 06/27/2012 | Planning - RENEWABLE | PLANNING_WIND.View | MVAR | RENEWABLE | AUX_MVARTOTAL | 1) This field is conditionally required (see below) 2) Data type is Float 3) Warn if value > Reactive Capability – WIND – Lagging MVAR Limit Associated With Mw4 Output * 0.5 4)Either Auxiliary Reactive Power or Power Factor is required | C | Float | B | Planning Team |  |  | Y | Y
Wind | Auxiliary Load Power Factor | 09/06/13 updated spreadsheet to reflect field is conditional. 10/08/2012 Updated Validation rule CR46800 | 09/06/13 updated spreadsheet to reflect field is conditional. ADDED 06/27/2012 | Planning - RENEWABLE | PLANNING_WIND.View |  | RENEWABLE | AUX_LOAD_PWR_FACT | Between .6 and 1.0 conditionally required (see below) Either Auxiliary Reactive Power or Power Factor is required | C |  |  | Planning Team |  |  | Y | Y
Wind | GENERATION AUXILIARY LOAD CHARACTERISTICS FOR MW LOAD |  |  | Planning - RENEWABLE |  |  | Not in table | Not in table | conditionally required (see below)
Wind | Large Motor, Percent Of Total Mw Load | 09/06/13 changed field type to Conditional and updated validation rules 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated validation rules ADDED 06/27/2012 | Planning - RENEWABLE | PLANNING_WIND.View |  | RENEWABLE | LRG_MTR_PER_TOT_MW_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent (where 1 = 100%) 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Numeric | B,DVB | Planning Team |  |  | N | N |  |  |  | 4160V is greater than 2400V, so why even mention 4160V?
Wind | Small Motor, Percent Of Total Mw Load | 09/06/13 changed field type to Conditional and updated validation rules 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated validation rules ADDED 06/27/2012 | Planning - RENEWABLE | PLANNING_WIND.View |  | RENEWABLE | SML_MTR_PER_TOT_MW_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent (where 1 = 100%) 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Numeric | B,DVB | Planning Team |  |  | N | N |  |  |  | 4160V is greater than 2400V, so why even mention 4160V?
Wind | Resistive (heating) Load, Percent Of Total Mw Load | 09/06/13 changed field type to Conditional and updated validation rules 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated validation rules ADDED 06/27/2012 | Planning - RENEWABLE | PLANNING_WIND.View |  | RENEWABLE | RESISTIVE_LOAD_PER_TOT_MW_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent (where 1 = 100%) 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Numeric | B,DVB | Planning Team |  |  | N | N
Wind | Discharge Lighting, Percent Of Total Mw Load | 09/06/13 changed field type to Conditional and updated validation rules 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated validation rules ADDED 06/27/2012 | Planning - RENEWABLE | PLANNING_WIND.View |  | RENEWABLE | DISCHARGE LIGHT_PER_TOT_MW_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent (where 1 = 100%) 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Numeric | B,DVB | Planning Team |  |  | N | N
Wind | Other, Percent Of Total Mw Load | 09/06/13 changed field type to Conditional and updated validation rules 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated validation rules ADDED 06/27/2012 | Planning - RENEWABLE | PLANNING_WIND.View |  | RENEWABLE | OTH_PER_TOT_MW_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent (where 1 = 100%) 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Numeric | B,DVB | Planning Team |  |  | N | N
Wind | GENERATION AUXILIARY LOAD CHARACTERISTICS FOR MVAR LOAD |  |  | Planning - RENEWABLE |  |  | Not in table | Not in table
Wind | Large Motor, Percent Of Total MVAR Load | 09/06/13 changed field type to Conditional and updated validation rules 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated validation rules ADDED 06/27/2012 | Planning - RENEWABLE | PLANNING_WIND.View |  | RENEWABLE | LRG_MTR_PER_TOT_MVAR_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent (where 1 = 100%) 3) SUM(All Generation Auxiliary Load Characteristics for MW MVAR Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Numeric | B,DVB | Planning Team |  |  | N | N
Wind | Small Motor, Percent Of Total MVAR Load | 09/06/13 changed field type to Conditional and updated validation rules 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated validation rules ADDED 06/27/2012 | Planning - RENEWABLE | PLANNING_WIND.View |  | RENEWABLE | SML_MTR_PER_TOT_MVAR_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent (where 1 = 100%) 3) SUM(All Generation Auxiliary Load Characteristics for MW MVAR Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Numeric | B,DVB | Planning Team |  |  | N | N
Wind | Discharge Lighting, Percent Of Total MVAR Load | 09/06/13 changed field type to Conditional and updated validation rules 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated validation rules ADDED 06/27/2012 | Planning - RENEWABLE | PLANNING_WIND.View |  | RENEWABLE | DISCHARGE LIGHT_PER_TOT_MVAR_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent (where 1 = 100%) 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | C | Numeric | B,DVB | Planning Team |  |  | N | N
Wind | Other, Percent Of Total MVAR Load | 09/06/13 changed field type to Conditional and updated validation rules 05/03/2012 removed percent from label on form | 09/06/13 changed field type to Conditional and updated validation rules ADDED 06/27/2012 | Planning - RENEWABLE | PLANNING_WIND.View |  | RENEWABLE | OTH_PER_TOT_MVAR_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent (where 1 = 100%) 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | C | Numeric | B,DVB | Planning Team |  |  | N | N
Solar Photovoltaic (PV) | Planning - Solar Photovoltaic (PV) |  |  | Planning - RENEWABLE |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type Selected is 'GEN' where GEN is non-CC non-wind Generation Resources. This tab is unit specific and required for all non-cc non-wind units. All the fields in this section should be complete. For all the UNITS in the Unit info-GEN tab , there should be corresponding data in Planning-GEN Tab | C |  |  | RARF Guide Version 4.0 | MMS,NMMS
Solar Photovoltaic (PV) | GENERATOR DETAILS |  |  | Planning - RENEWABLE |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | Unit Name | Do not show Message on Audit or Delta | Added 05/01/2017 | Planning - RENEWABLE |  | List | RENEWABLE | UNIT_NAME | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | Y
Solar Photovoltaic (PV) | Resource Name (Unit Code/Mnemonic) |  | Added 05/01/2017 | Planning - RENEWABLE |  | Automatic | RENEWABLE | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | Y
Solar Photovoltaic (PV) | GENERATOR AUXILIARY LOAD |  |  | Planning - RENEWABLE |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | Average Amount of Auxiliary Real Power |  | Added 05/01/2017 | Planning - RENEWABLE |  | MW | RENEWABLE | AUX_MWTOTAL | 1) This field is required 2) Data type is float 3) Value must be < Reactive Capability – SOLAR– MW4 4) Warn if value > Reactive Capability – SOLAR – MW4 * 0.20 | R | Float | B | Planning Team |  |  | Y | Y
Solar Photovoltaic (PV) | Average Amount of Auxiliary Reactive Power |  | Added 05/01/2017 | Planning - RENEWABLE |  | MVAR | RENEWABLE | AUX_MVARTOTAL | 1) This field is conditionally required (see below) 2) Data type is Float 3) Warn if value > Reactive Capability – SOLAR – Lagging MVAR Limit Associated With Mw4 Output * 0.5 4)Either Auxiliary Reactive Power or Power Factor is required | C | Float | B | Planning Team |  |  | Y | Y
Solar Photovoltaic (PV) | Auxiliary Load Power Factor |  | Added 05/01/2017 | Planning - RENEWABLE |  |  | RENEWABLE | AUX_LOAD_PWR_FACT | Between .6 and 1.0 conditionally required (see below) Either Auxiliary Reactive Power or Power Factor is required | C |  |  | Planning Team |  |  | Y | Y
Solar Photovoltaic (PV) | Generation Auxiliary Load Characteristics for Mw Load |  |  | Planning - RENEWABLE |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | Large Motor, Percent Of Total Mw Load |  | Added 05/01/2017 | Planning - RENEWABLE |  | MW | RENEWABLE | LRG_MTR_PER_TOT_MW_LOAD | 1)This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS |  | N | N
Solar Photovoltaic (PV) | Small Motor, Percent Of Total Mw Load |  | Added 05/01/2017 | Planning - RENEWABLE |  | MW | RENEWABLE | SML_MTR_PER_TOT_MW_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS |  | N | N
Solar Photovoltaic (PV) | Resistive (heating) Load, Percent Of Total Mw Load |  | Added 05/01/2017 | Planning - RENEWABLE |  | MW | RENEWABLE | RESISTIVE_LOAD_PER_TOT_MW_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS |  | N | N
Solar Photovoltaic (PV) | Discharge Lighting, Percent Of Total Mw Load |  | Added 05/01/2017 | Planning - RENEWABLE |  | NW | RENEWABLE | DISCHARGE LIGHT_PER_TOT_MW_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS |  | N | N
Solar Photovoltaic (PV) | Other, Percent Of Total Mw Load |  | Added 05/01/2017 | Planning - RENEWABLE |  | MW | RENEWABLE | OTH_PER_TOT_MW_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS |  | N | N
Solar Photovoltaic (PV) | Generation Auxiliary Load Characteristics For MVAR Load |  |  | Planning - RENEWABLE |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | Large Motor, Percent Of Total Mvar Load |  | Added 05/01/2017 | Planning - RENEWABLE |  | MVAR | RENEWABLE | LRG_MTR_PER_TOT_MVAR_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS |  | N | N
Solar Photovoltaic (PV) | Small Motor, Percent Of Total Mvar Load |  | Added 05/01/2017 | Planning - RENEWABLE |  | MVAR | RENEWABLE | SML_MTR_PER_TOT_MVAR_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS |  | N | N
Solar Photovoltaic (PV) | Discharge Lighting, Percent Of Total Mvar Load |  | Added 05/01/2017 | Planning - RENEWABLE |  | MVAR | RENEWABLE | DISCHARGE LIGHT_PER_TOT_MVAR_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS |  | N | N
Solar Photovoltaic (PV) | Other, Percent Of Total Mvar Load |  | Added 05/01/2017 | Planning - RENEWABLE |  | MVAR | RENEWABLE | OTH_PER_TOT_MVAR_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is less than or equal to 1.0 MW) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | C | Percent | B,DVB | Model Adminstration/Planning Team | MMS |  | N | N
Generation | Private Network - Unit - GEN |  |  | Private Network - Unit - GEN |  |  | Not in table | Not in table
Generation | GENERATOR DETAILS |  |  | Private Network - Unit - GEN |  |  | Not in table | Not in table
Generation | Unit Name | Do not show Message on Audit or Delta |  | Private Network - Unit - GEN |  | List | GENERATION | UNIT_NAME | 1. This field is not null. Data type: Character. | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | Y | Y
Generation | SITE_CODE |  |  | Private Network - Unit - GEN |  | Automatic | GENERATION | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters |  | Character |  |  |  |  | N | N
Generation | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | Private Network - Unit - GEN |  | Automatic | SITECODES | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | Y | Y
Generation | Private Network - Unit Information |  |  | Private Network - Unit - GEN |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Resource Type selected is non-cc non-wind Generation Resources | C |  |  | RARF Guide Version 4.0
Generation | Average Amount Of Self-serve Private Load |  |  | Private Network - Unit - GEN |  | MW | GENERATION | AVG_LD_MW_UNIT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS |  | Y | Y
Generation | Average Amount Of Self-serve Private Reactive Load |  |  | Private Network - Unit - GEN |  | MVAR | GENERATION | AVG_LD_MVAR_UNIT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | Y | Y
Generation | Expected Typical Private Network Net Interchange |  |  | Private Network - Unit - GEN |  | MW | GENERATION | NET_INTERCHNG_MW_UNIT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS |  | Y | Y
Generation | Expected Typical Private Network Net Reactive Interchange |  |  | Private Network - Unit - GEN |  | MVAR | GENERATION | NET_INTERCHNG_MVAR_UNIT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | Y | Y
Generation | Private Network Gross Unit Capability |  |  | Private Network - Unit - GEN |  | MW | GENERATION | GROSS_CAPBLTY_MW_UNIT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS |  | Y | Y
Generation | Private Network Gross Unit Reactive Capability |  |  | Private Network - Unit - GEN |  | MVAR | GENERATION | GROSS_CAPBLTY_MVAR_UNIT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | Y | Y
Generation | If Unit trips, Does Load trip? |  |  | Private Network - Unit - GEN |  | Y/N | GENERATION | LOAD_TRIP_FLG | Select from Y or N. | C | Dropdown List | B,DVB | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | N | N
Generation | If yes, Approximate Percentage of Load That Will Trip? | 05/03/2012 removed percent from label on form |  | Private Network - Unit - GEN |  |  | GENERATION | LOAD_TRIP_PCT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | N | N
CC | Private Network - Unit - CC |  |  | Private Network - Unit - CC |  |  | Not in table | Not in table
CC | GENERATOR DETAILS |  |  | Private Network - Unit - CC |  |  | Not in table | Not in table
CC | Unit Name | Do not show Message on Audit or Delta |  | Private Network - Unit - CC |  | List | CCUNIT | UNIT_NAME | 1. This field is not null. Data type: Character. | [6 empty] | Y | Y
CC | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code 05/17/2012 Update #3 validation |  | Private Network - Unit - CC |  | Automatic | CCUNIT | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | Y | Y |  |  |  | This is filled automatically in the form, why is there any validation?
CC | PRIVATE NETWORK - UNIT INFORMATION |  |  | Private Network - Unit - CC |  |  | Not in table | Not in table | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' | C |  |  | RARF Guide Version 4.0
CC | Average Amount Of Self-serve Private Load |  |  | Private Network - Unit - CC |  | MW | CCUNIT | AVG_LD_MW_UNIT | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS |  | Y | Y
CC | Average Amount Of Self-serve Private Reactive Load |  |  | Private Network - Unit - CC |  | MVAR | CCUNIT | AVG_LD_MVAR_UNIT | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | Y | Y
CC | Expected Typical Private Network Net Interchange |  |  | Private Network - Unit - CC |  | MW | CCUNIT | NET_INTERCHNG_MW_UNIT | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS |  | Y | Y
CC | Expected Typical Private Network Net Reactive Interchange |  |  | Private Network - Unit - CC |  | MVAR | CCUNIT | NET_INTERCHNG_MVAR_UNIT | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | Y | Y
CC | Private Network Gross Unit Capability |  |  | Private Network - Unit - CC |  | MW | CCUNIT | GROSS_CAPBLTY_MW_UNIT | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS |  | Y | Y
CC | Private Network Gross Unit Reactive Capability |  |  | Private Network - Unit - CC |  | MVAR | CCUNIT | GROSS_CAPBLTY_MVAR_UNIT | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | Y | Y
CC | If Unit Trips, Does Load Trip? |  |  | Private Network - Unit - CC |  | Y/N | CCUNIT | LOAD_TRIP_FLG | Select from Y or N. | C | Dropdown List | B,DVB | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | N | N
CC | If Yes, Approximate Percentage Of Load That Will Trip? | 05/03/2012 removed percent from label on form |  | Private Network - Unit - CC |  |  | CCUNIT | LOAD_TRIP_PCT | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | N | N
Wind | Private Network - Unit - Wind |  |  | Private Network - Unit |  |  | Not in table | Not in table | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' Wind unit' | C |  |  | RARF Guide Version 4.0
Wind | GENERATOR DETAILS |  |  | Private Network - Unit |  |  | Not in table | Not in table
Wind | Unit Name | Do not show Message on Audit or Delta |  | Private Network - Unit |  | List | RENEWABLE | UNIT_NAME | 1. This field is not null. Data type: Character. | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | Y | Y
Wind | Site Code |  |  | Private Network - Unit |  | Automatic | RENEWABLE | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | A | Character |  |  |  |  | N | N
Wind | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | Private Network - Unit |  | Automatic | RENEWABLE | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | Y | Y |  |  |  | This is filled automatically in the form, why is there any validation?
Wind | PRIVATE NETWORK - UNIT INFORMATION |  |  | Private Network - Unit |  |  | Not in table | Not in table | 3. Should not allow spaces |  |  | RARF Guide Version 4.0
Wind | Average Amount Of Self-Serve Private Load |  |  | Private Network - Unit |  | MW | RENEWABLE | AVG_LD_MW_UNIT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' Wind unit' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS |  | Y | Y
Wind | Average Amount Of Self-Serve Private Reactive Load |  |  | Private Network - Unit |  | MVAR | RENEWABLE | AVG_LD_MVAR_UNIT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' Wind unit' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | Y | Y
Wind | Expected Typical Private Network Net Interchange |  |  | Private Network - Unit |  | MW | RENEWABLE | NET_INTERCHNG_MW_UNIT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' Wind unit' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS |  | Y | Y
Wind | Expected Typical Private Network Net Reactive Interchange |  |  | Private Network - Unit |  | MVAR | RENEWABLE | NET_INTERCHNG_MVAR_UNIT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' Wind unit' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | Y | Y
Wind | Private Network Gross Unit Capability |  |  | Private Network - Unit |  | MW | RENEWABLE | GROSS_CAPBLTY_MW_UNIT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' Wind unit' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS |  | Y | Y
Wind | Private Network Gross Unit Reactive Capability |  |  | Private Network - Unit |  | MVAR | RENEWABLE | GROSS_CAPBLTY_MVAR_UNIT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' Wind unit' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | Y | Y
Wind | If Unit trips, does Load trip? |  |  | Private Network - Unit |  | Y/N | RENEWABLE | LOAD_TRIP_FLG | Select from Y or N. | C | Dropdown List | B,DVB | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | N | N
Wind | If yes, approximate percentage of Load that will trip? | 05/03/2012 removed percent from label on form |  | Private Network - Unit |  |  | RENEWABLE | LOAD_TRIP_PCT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' Wind unit' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | N | N
Solar Photovoltaic (PV) | Private Network - Unit - Solar Photovoltaic (PV) |  |  | Private Network - Unit |  |  | Not in table | Not in table | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' Wind unit' | C |  |  | RARF Guide Version 4.0
Solar Photovoltaic (PV) | GENERATOR DETAILS |  |  | Private Network - Unit |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | Unit Name | Do not show Message on Audit or Delta | Added 05/01/2017 | Private Network - Unit |  | List | RENEWABLE | UNIT_NAME | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | Y | Y
Solar Photovoltaic (PV) | Site Code |  | Added 05/01/2017 | Private Network - Unit |  | Automatic | RENEWABLE | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters |  | Character |  |  |  |  | N | N
Solar Photovoltaic (PV) | Resource Name (Unit Code/Mnemonic) |  | Added 05/01/2017 | Private Network - Unit |  | Automatic | RENEWABLE | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | Y | Y
Solar Photovoltaic (PV) | PRIVATE NETWORK - UNIT INFORMATION |  |  | Private Network - Unit |  |  | Not in table | Not in table | 3. Should not allow spaces |  |  | RARF Guide Version 4.0
Solar Photovoltaic (PV) | Average Amount Of Self-Serve Private Load |  | Added 05/01/2017 | Private Network - Unit |  | MW | RENEWABLE | AVG_LD_MW_UNIT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' PV unit' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS |  | Y | Y
Solar Photovoltaic (PV) | Average Amount Of Self-Serve Private Reactive Load |  | Added 05/01/2017 | Private Network - Unit |  | MVAR | RENEWABLE | AVG_LD_MVAR_UNIT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' PV unit' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | Y | Y
Solar Photovoltaic (PV) | Expected Typical Private Network Net Interchange |  | Added 05/01/2017 | Private Network - Unit |  | MW | RENEWABLE | NET_INTERCHNG_MW_UNIT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' PV unit' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS |  | Y | Y
Solar Photovoltaic (PV) | Expected Typical Private Network Net Reactive Interchange |  | Added 05/01/2017 | Private Network - Unit |  | MVAR | RENEWABLE | NET_INTERCHNG_MVAR_UNIT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' PV unit' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | Y | Y
Solar Photovoltaic (PV) | Private Network Gross Unit Capability |  | Added 05/01/2017 | Private Network - Unit |  | MW | RENEWABLE | GROSS_CAPBLTY_MW_UNIT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' PV unit' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS |  | Y | Y
Solar Photovoltaic (PV) | Private Network Gross Unit Reactive Capability |  | Added 05/01/2017 | Private Network - Unit |  | MVAR | RENEWABLE | GROSS_CAPBLTY_MVAR_UNIT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' PV unit' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | Y | Y
Solar Photovoltaic (PV) | If Unit trips, does Load trip? |  | Added 05/01/2017 | Private Network - Unit |  | Y/N | RENEWABLE | LOAD_TRIP_FLG | Select from Y or N. | C | Dropdown List | B,DVB | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | N | N
Solar Photovoltaic (PV) | If yes, approximate percentage of Load that will trip? |  | Added 05/01/2017 | Private Network - Unit |  |  | RENEWABLE | LOAD_TRIP_PCT | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' pv unit' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | N | N
LAAR | General Information - LAAR |  |  | General Information - LAAR |  |  | Not in table | Not in table | This tab is conditional. Required if the Resource Type is selected as ' Load ' | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0 | EMS,MMS,NMMS
LAAR | This submittal is for: | 03/09/2012 Already in form added to mapping document |  | General Information - LAAR |  |  | LOAD_RESOURCES | SUBMIR_REASON | Not null. Select from the list: New Resource Entity, Revision, Additions or Deletions | R | Dropdown List | B,DVB |  |  |  | N/A | N/A |  |  | N/A
LAAR | Submittal Information |  |  | General Information - LAAR |  |  | Not in table | Not in table | Not null. Select from the list: New Site, Revision, Addition of Units, Deletion of Units | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 4/RARF Guide version 4.0/ Angela Moy |  |  | N/A | N/A |  |  | N/A
LAAR | Date Form Completed: |  |  | General Information - LAAR |  |  | LOAD_RESOURCES | FORM_COMP_DT | Optional | O | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N/A | N/A |  |  | N/A
LAAR | Resource Entity Submitting Form: | 03/09/2012 Updated Validation |  | General Information - LAAR |  |  | RE_RARF | RE_NAME | 1.This field is not null. 2. All should be capital letters 3.No Special characters except spaces and dashes. | R | Character | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | N/A | N/A |  |  | N/A
LAAR | Resource Entity DUNS #: |  |  | General Information - LAAR |  |  | RE_RARF | RE_DUNS | 2. Name must match ERCOT records (SIEBEL) | R | Character | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk |  |  | N/A | N/A |  |  | N/A
LAAR | Primary Contact (name of person ERCOT can contact with questions regarding this form) |  |  | General Information - LAAR |  |  | Not in table | Not in table
LAAR | Printed Name: |  |  | General Information - LAAR |  |  | LOAD_RESOURCES | NAME_AR | Not null | R | Character | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | N/A | N/A |  |  | N/A
LAAR | Title: |  |  | General Information - LAAR |  |  | LOAD_RESOURCES | TITLE_AR | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N/A | N/A |  |  | N/A
LAAR | Phone Number: |  |  | General Information - LAAR |  |  | LOAD_RESOURCES | PHONE_AR | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N/A | N/A |  |  | N/A
LAAR | E-mail Address: |  |  | General Information - LAAR |  |  | LOAD_RESOURCES | EMAIL_AR | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N/A | N/A |  |  | N/A
LAAR | Fax Number: |  |  | General Information - LAAR |  |  | LOAD_RESOURCES | FAX_AR | Optional | O | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  |  | N/A | N/A |  |  | N/A
LAAR | Secondary Contact (if available) |  |  | General Information - LAAR |  |  | Not in table | Not in table
LAAR | Printed Name: |  |  | General Information - LAAR |  |  | Not in table | Not in table
LAAR | Title: |  |  | General Information - LAAR |  |  | Not in table | Not in table
LAAR | Phone Number: |  |  | General Information - LAAR |  |  | Not in table | Not in table
LAAR | E-mail Address: |  |  | General Information - LAAR |  |  | Not in table | Not in table
LAAR | Fax Number: |  |  | General Information - LAAR |  |  | Not in table | Not in table
LAAR | Load Resource Information |  |  | Load Resource Information |  |  | Not in table | Not in table
LAAR | UNIT DETAILS |  |  | Load Resource Information |  |  | Not in table | Not in table
LAAR | Common Name for Load Resource |  |  | Load Resource Information |  |  | LOAD_RESOURCES | COMMON_NAME_LOAD_RSRC | This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  |  | N/A | N/A |  |  | N/A
LAAR | Dispatch Asset Code (provided by ERCOT) |  |  | Load Resource Information |  |  | LOAD_RESOURCES | DISPATCH_ASSET_CODE | [7 empty] | N/A | N/A |  |  | N/A
LAAR | Physical Street Address for Point Of Delivery (POD) |  |  | Load Resource Information |  |  | LOAD_RESOURCES | STREET_ADD_POD | This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  |  | N/A | N/A |  |  | N/A
LAAR | Name of City for Point of Delivery (POD) |  |  | Load Resource Information |  |  | LOAD_RESOURCES | CITY_POD | This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  |  | N/A | N/A |  |  | N/A
LAAR | Is Load Netted From Generation at ERCOT Read Gensite? |  |  | Load Resource Information |  | Y/N | LOAD_RESOURCES | LOAD_NET_FROM_GENSITE_FLG | This field is not null. Select from the list :Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  |  | N/A | N/A |  |  | N/A
LAAR | Is Load Behind a NOIE Settlement Meter Point? |  |  | Load Resource Information |  | Y/N | LOAD_RESOURCES | LOAD_BEHIND_NOIE_FLG | This field is not null. Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  |  | N/A | N/A |  |  | N/A
LAAR | Load Resource Type (CLR/UFR) | Updated field name 2/10/2016 | Updated field name 2/10/2016 | Load Resource Information |  |  | LOAD_RESOURCES | LOAD_RESOURCE_TYPE | Select from the list: CLR,UFR. Load Resource Type is not null | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0 | EMS |  | N/A | N/A |  |  | N/A
LAAR | If CLR, will CLR be Dynamically Scheduling? |  |  | Load Resource Information |  | Y/N | LOAD_RESOURCES | CLR_DYNAMIC_SCHED_FLG | Select from the list Y or N. This field is optional. This field is required for CLR and optional for other types | C/O | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  |  | N/A | N/A |  |  | N/A
LAAR | If CLR, ability to operate as a UFR type Resource? |  |  | Load Resource Information |  | Y/N | LOAD_RESOURCES | CLR_OPERATE_AS_UFR_FLG | Select from the list Y or N. This field is optional. This field is required for CLR and optional for other types | C
LAAR | Load Resource Effective Date |  |  | Load Resource Information |  | Y/N | LOAD_RESOURCES | LOAD_RESOURCE_EFF_DATE | This field is not null. Date format should be MM/DD/YYYY | R | Date time | B | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  |  | N/A | N/A |  |  | N/A
LAAR | Load Resource Expiration Date |  |  | Load Resource Information |  | MM/DD/YYYY | LOAD_RESOURCES | LOAD_RESOURCE_EXP_DATE | This field is optional. Date format should be MM/DD/YYYY. NA is not valid, Leave it blank if not applicable | O | Date time | B | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  |  | N/A | N/A |  |  | N/A
LAAR | Substation Name for POD |  |  | Load Resource Information |  | all caps | LOAD_RESOURCES | SUBSTATION_NAME_POD | This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  |  | N/A | N/A |  |  | N/A
LAAR | Substation Code for POD |  |  | Load Resource Information |  | all caps | LOAD_RESOURCES | SUBSTATION_CODE_POD | This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  |  | N/A | N/A |  |  | N/A
LAAR | Transmission Bus POD (PTI Bus No) |  |  | Load Resource Information |  |  | LOAD_RESOURCES | TRANSMISSION_BUS_POD | 1.This field is not null and should be a number 2.ERCOT needs to associate each load resource to one and only one load in the network model used by State Estimator. For lack of a better source of information; the static network model load connected at this PTI bus number is what this load resource will be mapped to. Therefore there MUST be a static network model load at this PTI bus number (CIM). | R | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  |  | N/A | N/A |  |  | N/A
LAAR | Transmission Station Voltage |  |  | Load Resource Information |  | KV | LOAD_RESOURCES | VOLTAGE_LVL_TLMTRD_LOAD | This field is not null and should be a number | R | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  |  | N/A | N/A |  |  | N/A
LAAR | Transmission Station Load Name in Network Operations Model |  | ADDED 06/27/2012 | Load Resource Information | LOAD_RESOURCES.View | all caps | LOAD_RESOURCES | TRANS_STAT_LOAD_NAM_NOM | ALL CAPS | [6 empty] | N/A | N/A |  |  | N/A
LAAR | Meter Reading Entity | Updated field name 2/10/2016 | Updated field name 2/10/2016 | Load Resource Information |  |  | LOAD_RESOURCES | MTR_RDG_ENTITY_TDSP | This field is not null. | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  |  | N/A | N/A |  |  | N/A
LAAR | Meter Reading Entity Duns Number |  |  | Load Resource Information |  |  | LOAD_RESOURCES | MTR_RDG_ENTITY_DUNS | This field is not null. This is either 9 or 13 digit number. Validate with the existing record in ERCOT?? | R | Integer | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 |  |  | N/A | N/A |  |  | N/A
LAAR | ESI-ID assigned to meter |  |  | Load Resource Information |  |  | LOAD_RESOURCES | ESIID_ASSIGNED | This field is not null and should be a number. Data type is character | R | Character | B | Angela Moy/RARF Glossary Version 4.0 /RARF Guide version 4.0 |  |  | N/A | N/A |  |  | N/A
LAAR | Wholesale Delivery Point? |  |  | Load Resource Information |  | Y/N | LOAD_RESOURCES | WHOLESALE_DLVRY_PT | This field is not null. Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  |  | N/A | N/A |  |  | N/A
LAAR | Load Resource Control Device |  |  | Load Resource Information |  |  | LOAD_RESOURCES | LOAD_RES_CTRL_DEVICE | This field is not null | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0 /RARF Guide version 4.0 |  |  | N/A | N/A |  |  | N/A
LAAR | ERCOT Load Zone |  |  | Load Resource Information |  |  | LOAD_RESOURCES | ERCOT_LOAD_ZONE | This field is a required and data type is character | R | Character | B,DVB | RARF Glossary Version 4.0 /Angela Moy |  |  | N/A | N/A |  |  | N/A
LAAR | Maximum POD Total Load | 10/05/12 correct validation correct validation 07/27/2012 CR- 46145 |  | Load Resource Information |  | MW | LOAD_RESOURCES | MAX_POD_TOTAL_LOAD | Maximum POD Total Load must be greater than or equal to Maximum INT Load MW .This field is not null and should be a Number | R | Numeric | B,DVB | Lin Xu | MMS |  | N/A | N/A |  |  | N/A
LAAR | Maximum Interruptible Load MW | 10/05/12 correct validation correct validation 07/27/2012 CR- 46145 |  | Load Resource Information |  | MW | LOAD_RESOURCES | MAX_INT_LOAD_MW | Maximum INT Load MW must be less than or equal to Maximum POD Total Load and must be less then or equal to High Reasonability Limit .This field is not null and should be a Number | [6 empty] | N/A | N/A |  |  | N/A
LAAR | High Reasonability Limit | 05/05/12 Updated Validation |  | Load Resource Information |  | MW | LOAD_RESOURCES | HIGH_REAS_LIMIT | 1. HRL >=0 . 2. High Reasonability Limit >=HSL or MPC.This field is not null and should be a Number 3. Value must be >= LRL 4. HRL >= Maximum INT Load MW | R | Numeric | B,DVB | RARF Workshop for Load Resources/ RARF Glossary Version 4.0 /RARF Guide version 4.0/Steve Krein | EMS |  | N/A | N/A |  |  | N/A
LAAR | Low Reasonability Limit |  |  | Load Resource Information |  | MW | LOAD_RESOURCES | LOW_REAS_LIMIT | 1. LRL should be <= HRL. LRL must be >= 0 2. Low Reasonability Limit <= LSL or LPC. This field is not null and should be a Number Note in most cases the LRL = LSL = LPC = 0 | R | Numeric | B,DVB | Angela Moy/RARF Workshop for Load Resources/ RARF Glossary Version 4.0 /RARF Guide version 4.0/Steve Krein | EMS |  | N/A | N/A |  |  | N/A
LAAR | CLR High Reasonability Ramp Rate Limit |  |  | Load Resource Information |  | MW/min | LOAD_RESOURCES | HIGH_REAS_RAMPRATE_LIMIT | 1. CLR High Reasonability Ramp Rate Limit >= Low Reasonability Ramp Rate Limit. This field is conditional: Required only if Load Resource type selected is 'CLR'. Must be a positive number. This field can not be null if Load Resource type selected is 'CLR'. | C | Numeric | B,DVB | Lin Xu/kiittipong/Jamil Daouk | MMS |  | N/A | N/A |  |  | N/A
LAAR | CLR Low Reasonability Ramp Rate Limit |  |  | Load Resource Information |  | MW/min | LOAD_RESOURCES | LOW_REAS_RAMPRATE_LIMIT | 1. CLR LowReasonableRampRateLimit <= Emergency Downward ramp rate <= CLR HighReasonableRampRateLimit. This field is conditional: Required only if Load Resource type selected is 'CLR'. Must be a positive number. This field can not be null if Load Resource type selected is 'CLR'. | C | Numeric | B,DVB | Lin Xu/kiittipong/Jamil Daouk | MMS |  | N/A | N/A |  |  | N/A
LAAR | Private Use Network? |  |  | Load Resource Information |  | Y/N | LOAD_RESOURCES | PRIVATE_USE_NETWRK_FLG | Select from the list: Y or N. This field is Not null | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  |  | N/A | N/A |  |  | N/A
LAAR | Load Resource Parameters |  |  | Load Resource Parameters |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Type selected is ' Load ' | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0 | MMS,NMMS
LAAR | Dispatch Asset Code |  |  | Load Resource Parameters |  | List | LD_RES_RAMPRATE_NRRC | DISPATCH_ASSET_CODE |  | R | [5 empty] | N/A | N/A |  |  | N/A
LAAR | Non-CLR Resource Parameters |  |  | Load Resource Parameters |  |  | Not in table | Not in table
LAAR | Minimum Interruption Time |  |  | Load Resource Parameters |  | hours | LOAD_RESOURCES | MIN_INTERUPT_TIME | 1. Minimum Interruption Time <= Maximum Interruption Time. 2.Minimum Interruption Time >=0. This field should not be null 3.Unit of measure is hour - This number should be rounded up to the nearest whole number (can't dispatch for partial hours). Data type is Integer. 4.This Field is conditional: Required {if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Integer | B,DVB | Lin Xu/kiittipong/Jamil Daouk/Scott Middleton | MMS,NMMS |  | N/A | N/A |  |  | N/A
LAAR | Minimum Restoration Time |  |  | Load Resource Parameters |  | hours | LOAD_RESOURCES | MIN_RESTOR_TIME | 1.Minimum Restoration Time >=0. This field should not be null. 2.Unit of measure is hour - This number should be rounded up to the nearest whole number (can't dispatch for partial hours). Data type is Integer 3.This Field is conditional: Required {if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Integer | B,DVB | Lin Xu/kiittipong/Jamil Daouk/Scott Middleton | MMS,NMMS |  | N/A | N/A |  |  | N/A
LAAR | Max WEEKLY Deployments |  |  | Load Resource Parameters |  |  | LOAD_RESOURCES | MAX_WKLY_DEPLOYS | 1.Max WEEKLY Deployments > =0. This field should not be null and It is an Integer. 2.This Field is conditional: Required {if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Integer | B,DVB | Lin Xu/kiittipong/Scott Middleton | MMS,NMMS |  | N/A | N/A |  |  | N/A
LAAR | Max Interruption Time |  |  | Load Resource Parameters |  |  | LOAD_RESOURCES | MAX_INTERUPT_TIME | 1.Max Interruption Time > 0. 2.Unit of measure is hours, with only 1 digit after decimal point 3.This Field is conditional: Required {if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Numeric | B,DVB | Lin Xu/kiittipong/Jamil Daouk/Scott Middleton | MMS,NMMS |  | N/A | N/A |  |  | N/A
LAAR | Max DAILY Deployments |  |  | Load Resource Parameters |  |  | LOAD_RESOURCES | MAX_DAILY_DEPLOYS | 1.Max WEEKLY Deployments > Max DAILY Deployments. 2.Maximum Daily Deployment is not null and it is an Integer 3.This Field is conditional: {Required if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Integer | B,DVB | Lin Xu/kiittipong/Scott Middleton | MMS,NMMS |  | N/A | N/A |  |  | N/A
LAAR | Max Weekly Energy |  |  | Load Resource Parameters |  | MWh | LOAD_RESOURCES | MAX_WKLY_ENERGY | 1.Max Weekly Energy > =0. 2.This Field is conditional: Required {if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Numeric | B,DVB | Lin Xu/kiittipong/Scott Middleton | MMS,NMMS |  | N/A | N/A |  |  | N/A
LAAR | Minimum Notice Time |  |  | Load Resource Parameters |  | minutes | LOAD_RESOURCES | MIN_NOTICE_TIME | 1.Minimum Notice Time > =0 2.Unit of measure is hour - This number should be rounded up to the nearest whole number (can't dispatch for partial hours). Data type is Integer 3.This Field is conditional: Required {if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Integer | B,DVB | Lin Xu/kiittipong/Jamil Daouk/Scott Middleton | MMS,NMMS |  | N/A | N/A |  |  | N/A
LAAR | CLR Resource Parameters | 06/18/2012 Updated Valaidation |  | Load Resource Parameters |  |  | Not in table | Not in table | This section is conditional: Required ONLY if the Load Resource Type is CLR or CLR/UFR | C
LAAR | Max Deployment Time |  |  | Load Resource Parameters |  | hours | LOAD_RESOURCES | MAX_DEPLOY_TIME_CLR | 1.Max Deployment Time > 0 2.Unit of measure is hour - This number should be rounded down to the nearest whole number (can't dispatch for partial hours). Data type is Integer | C | Integer | B,DVB | Lin Xu/kiittipong/Jamil Daouk | MMS |  | N/A | N/A |  |  | N/A
LAAR | Max Weekly Energy |  |  | Load Resource Parameters |  | MWh | LOAD_RESOURCES | MAX_WKLY_ENERGY_CLR | Max Weekly Energy > =0 | C | Numeric | B,DVB | Lin Xu/kiittipong | MMS |  | N/A | N/A |  |  | N/A
LAAR | CLR - NRRC | 06/18/2012 Updated Valaidation |  | CLR - NRRC |  |  | Not in table | Not in table | This section is conditional: Required ONLY if the Load Resource Type is CLR or CLR/UFR
LAAR | Dispatch Asset Code |  |  | CLR - NRRC |  | List | LD_RES_RAMPRATES_NRRC | DISPATCH_ASSET_CODE | [7 empty] | N/A | N/A |  |  | N/A
LAAR | NORMAL RAMP RATE CURVE |  |  | CLR - NRRC |  |  | Not in Table | Not in Table | This section is conditional: Required ONLY if the Load Resource Type is CLR or CLR/UFR | C
LAAR | NRRC MW |  |  | CLR - NRRC |  | List | LD_RES_RAMPRATES_NRRC | MW_NUMBER_NRRC |  |  | LIST |  |  |  |  | N/A | N/A |  |  | N/A
LAAR | MW Rating NRRC | 6/12/2012 This field was removed from the form and should have not been |  | CLR - NRRC |  | MW | LD_RES_RAMPRATES_NRRC | MW_RATING_NRRC | 1. MW1 to MW10 are increasing MW Values. 2.MW1 can't be null, and must have value for both ramp up and ramp down | C | Numeric | B,DVB | RARF Guide Version 4.0/ Jamil Daouk | NMMS |  | N/A | N/A |  |  | N/A
LAAR | Upward Ramprate |  |  | CLR - NRRC |  | MW/min | LD_RES_RAMPRATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. CLR Normal Upward Ramp Rate <= CLR Emergency Upward Ramp Rate. Zero or negative ramp rate values are not allowed. Normal Up ramp rate > 0 if breakpoint is given. 2. If Load Resource Type is 'CLR/UFR' then verify thatLowReasonableRampRateLimit <= Normal Up ramp rate <= HighReasonableRampRateLimit | C | Numeric | B,DVB | Lin Xu/kiittipong | MMS,NMMS |  | N/A | N/A |  |  | N/A
LAAR | Downward Ramprate |  |  | CLR - NRRC |  | MW/min | LD_RES_RAMPRATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1.Zero or negative ramp rate values are not allowed. CLR Normal Downward Ramp Rate <= Emergency Downward Ramp Rate. Normal Dn ramp rate > 0 if breakpoint is given 2. If Load Resource Type is 'CLR/UFR' then verify that LowReasonableRampRateLimit <= Normal Dn ramp rate <= HighReasonableRampRateLimit | C | Numeric | B,DVB | Lin Xu/kiittipong | MMS,NMMS |  | N/A | N/A |  |  | N/A
LAAR | CLR - ERRC | 06/18/2012 Updated Valaidation |  | CLR - ERRC |  |  | Not in Table | Not in Table
LAAR | Dispatch Asset Code |  |  | CLR - ERRC |  | List | LD_RES_RAMPRATES_ERRC | DISPATCH_ASSET_CODE | [7 empty] | N/A | N/A |  |  | N/A
LAAR | EMERGENCY RAMP RATE CURVE | 06/18/2012 Updated Valaidation |  | CLR - ERRC |  |  | Not in Table | Not in Table | This section is conditional: Required ONLY if the Load Resource Type is CLR or CLR/UFR | C
LAAR | ERRC MW |  |  | CLR - ERRC |  | List | LD_RES_RAMPRATES_ERRC | MW_NUMBER_ERRC |  |  | LIST |  |  |  |  | N/A | N/A |  |  | N/A
LAAR | MW Rating ERRC | 6/12/2012 This field was removed from the form and should have not been |  | CLR - ERRC |  | MW | LD_RES_RAMPRATES_ERRC | MW_RATING_ERRC | 1.MW1 to MW10 are increasing MW Values. 2.MW1 can't be null, and must have value for both ramp up and ramp down | C | Numeric | B,DVB | Lin Xu/ Jamil Daouk | MMS,NMMS |  | N/A | N/A |  |  | N/A
LAAR | Upward Ramprate |  |  | CLR - ERRC | RARFAUDIT_ERRC_LOAD_RESOURCES.View | MW/min | LD_RES_RAMPRATES_ERRC | UPWARD_RAMPRATE_ERRC | CLR Normal Upward Ramp Rate <= CLR Emergency Upward Ramp Rate. Zero or negative ramp rate values are not allowed. No null values are allowed, required for each CLR. LowReasonableRampRateLimit <= Emergency Up ramp rate <= HighReasonableRampRateLimit | C | Numeric | B,DVB | Lin Xu/kiittipong | MMS,NMMS |  | N/A | N/A |  |  | N/A
LAAR | Downward Ramprate |  |  | CLR - ERRC | RARFAUDIT_ERRC_LOAD_RESOURCES.View | MW/min | LD_RES_RAMPRATES_ERRC | DOWNWARD_RAMPRATE_ERRC | Zero or negative ramp rate values are not allowed. If Load Resource Type is 'CLR/UFR' then verify that LowReasonableRampRateLimit <= Emergency Dn ramp rate <= HighReasonableRampRateLimit CLR Normal Downward Ramp Rate <= CLR Emergency Downward Ramp Rate. Zero or negative ramp rate values are not allowed. No null values are allowed, required for each CLR. | C | Numeric | B,DVB | Lin Xu/kiittipong | MMS,NMMS |  | N/A | N/A |  |  | N/A
Generation | Protection - GEN |  |  | Protection - GEN |  |  | Not in table | Not in table | Not all the fields need to be complete. Only the fields that have Data.
Generation | GENERATOR DETAILS |  |  | Protection - GEN |  |  | Not in table | Not in table
Generation | Unit Name |  |  | Protection - GEN |  | List | GENERATION | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | Y
Generation | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | Protection - GEN |  | Automatic | GENERATION | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | Y
Generation | PLANT VOLTAGE PROTECTION |  |  | Protection - GEN |  |  | Not in table | Not in table
Generation | Breaker Interruption Time |  |  | Protection - GEN |  | cycles | GENERATION | BREAKER_INTERRUP | 1) this field is required 2) Data type must be Integer | R | Integer | B | Planning Team |  |  | N | Y
Generation | Instantaneous Undervoltage Trip |  |  | Protection - GEN |  | p.u. | GENERATION | UVOLT_TRIP_INSTANT | 1. Optional 2. Value must be numeric > 0 3. Value should be <= 396 | O | Float | B | Planning Team |  |  | N | Y |  |  |  | Glossary needs to define what "Instantaneous" is
Generation | Under voltage 1 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | p.u. | GENERATION | UVOLT_TRIP_VOLT1 | 1. Required Conditional, warning if missing 2. Value must be numeric >= 0 | R C | Float | B | Planning Team
Generation | Under voltage Trip Time 1 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | sec | GENERATION | UVOLT_TRIP_TIME1 | 1. Required Conditional, warning if missing 2. Value must be numeric >= 0 | R C | Float |  | Planning Team
Generation | Under voltage 2 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | p.u. | GENERATION | UVOLT_TRIP_VOLT2 | 1. Optional Conditional,required if Undervoltage Trip 2 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
Generation | Under voltage Trip Time 2 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | sec | GENERATION | UVOLT_TRIP_TIME2 | 1. Optional Conditional, required if Undervoltage Trip 2 is set 2. Value must be numeric > Undervoltage Trip 1 Time | O C | Float |  | Planning Team
Generation | Under voltage 3 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | p.u. | GENERATION | UVOLT_TRIP_VOLT3 | 1. Optional Conditional, required if Undervoltage Trip 3 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
Generation | Under voltage Trip Time 3 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | sec | GENERATION | UVOLT_TRIP_TIME3 | 1. Optional Conditional, required if Undervoltage Trip 3 is set 2. Value must be numeric > Undervoltage Trip 2 Time | O C | Float |  | Planning Team
Generation | Under voltage 4 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | p.u. | GENERATION | UVOLT_TRIP_VOLT4 | 1. Optional Conditional, required if Undervoltage Trip 4 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
Generation | Under voltage Trip Time 4 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | sec | GENERATION | UVOLT_TRIP_TIME4 | 1. Optional Conditional, required if Undervoltage Trip 4 is set 2. Value must be numeric > Undervoltage Trip 3 Time | O C | Float |  | Planning Team
Generation | Instantaneous Overvoltage Trip |  |  | Protection - GEN |  | p.u. | GENERATION | OVOLT_TRIP_INSTANT | 1. Optional 2. Value must be numeric > 0 3. Value should be <= 396 | O | Float | B | Planning Team |  |  | N | Y |  |  |  | Glossary needs to define what "Instantaneous" is
Generation | Overvoltage 1 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | p.u. | GENERATION | OVOLT_TRIP_VOLT1 | 1. Required Conditional, warning if missing 2. Value must be numeric >= 0 | R C | Float | B | Planning Team
Generation | Overvoltage Trip Time 1 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | sec | GENERATION | OVOLT_TRIP_TIME1 | 1. Required Conditional, warning if missing 2. Value must be numeric >= 0 | R C | Float | B | Planning Team
Generation | Overvoltage 2 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | p.u. | GENERATION | OVOLT_TRIP_VOLT2 | 1. Optional Conditional, required if Overvoltage Trip 2 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
Generation | Overvoltage Trip Time 2 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | sec | GENERATION | OVOLT_TRIP_TIME2 | 1. Optional Conditional, required if Overvoltage Trip 2 is set 2. Value must be numeric >= 0 and < Overvoltage Trip 1 Time | O C | Float | B | Planning Team
Generation | Overvoltage 3 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | p.u. | GENERATION | OVOLT_TRIP_VOLT3 | 1. Optional Conditional, required if Overvoltage Trip 3 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
Generation | Overvoltage Trip Time 3 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | sec | GENERATION | OVOLT_TRIP_TIME3 | 1. Optional Conditional, required if Overvoltage Trip 3 is set 2. Value must be numeric >= 0 and < Overvoltage Trip 2 Time | O C | Float | B | Planning Team
Generation | Overvoltage 4 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | p.u. | GENERATION | OVOLT_TRIP_VOLT4 | 1. Optional Conditional, required if Overvoltage Trip 4 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
Generation | Overvoltage Trip Time 4 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | sec | GENERATION | OVOLT_TRIP_TIME4 | 1. Optional Conditional, required if Overvoltage Trip 4 is set 2. Value must be numeric >= 0 and < Overvoltage Trip 3 Time | O C | Float | B | Planning Team
Generation | PLANT FREQUENCY PROTECTION |  |  | Protection - GEN |  |  | Not in table | Not in table
Generation | Instantaneous Underfrequency Trip |  | Updated validation rule 05/01/2017 | Protection - GEN |  | Hz | GENERATION | UFREQ_TRIP_INSTANT | 1. Optional 2. Value must be numeric and <= 57.5 | O | Numeric |  | Planning Team | [7 empty] | Glossary needs to define what "Instantaneous" is
Generation | Underfrequency 1 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | Hz | GENERATION | UFREQ_TRIP_HZ1 | 1. Optional, required if Under frequency Trip 1 Time is set 2. Value must be numeric <= 59.4 3. If Instantaneous Underfrequency Trip is set, value must be > Instantaneous Under frequency Trip | O C | Numeric |  | Planning Team
Generation | Underfrequency Trip Time 1 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | sec | GENERATION | UFREQ_TRIP_TIME1 | 1. Optional, required if Underfrequency Trip 1 is set 2. Value must be numeric 3. If Underfrequency Trip 1 > 58.4 and <= 59.4, value must be >= 540 4. If Underfrequency Trip 1 > 58 and <= 58.4, value must be >= 30 5. If Underfrequency Trip 1 > 57.5 and <= 58, value must be >= 2 | O C | Numeric |  | Planning Team
Generation | Underfrequency 2 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | Hz | GENERATION | UFREQ_TRIP_HZ2 | 1. Optional, required if Underfrequency Trip 2 Time is set 2. Value must be numeric < Underfrequency Trip 1 3. If Instantaneous Underfrequency Trip is set, value must be > Instantaneous Under frequency Trip | O C | Numeric |  | Planning Team
Generation | Underfrequency Trip Time 2 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | sec | GENERATION | UFREQ_TRIP_TIME2 | 1. Optional, required if Underfrequency Trip 2 is set 2. Value must be numeric 3. If Underfrequency Trip 2 > 58.4 and <= 59.4, value must be >= 540 4. If Underfrequency Trip 2 > 58 and <= 58.4, value must be >= 30 5. If Underfrequency Trip 2 > 57.5 and <= 58, value must be >= 2 | O C | Numeric |  | Planning Team
Generation | Underfrequency 3 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | Hz | GENERATION | UFREQ_TRIP_HZ3 | 1. Optional, required if Underfrequency Trip 3 Time is set 2. Value must be numeric and < Underfrequency Trip 2 3. If Instantaneous Underfrequency Trip is set, value must be > Instantaneous Under frequency Trip | O C | Numeric |  | Planning Team
Generation | Underfrequency Trip Time 3 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | sec | GENERATION | UFREQ_TRIP_TIME3 | 1. Optional, required if Underfrequency Trip 3 is set 2. Value must be numeric 3. If Underfrequency Trip 3 > 58.4 and <= 59.4, value must be >= 540 4. If Underfrequency Trip 3 > 58 and <= 58.4, value must be >= 30 5. If Underfrequency Trip 3 > 57.5 and <= 58, value must be >= 2 | O C | Numeric |  | Planning Team
Generation | Underfrequency 4 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | Hz | GENERATION | UFREQ_TRIP_HZ4 | 1. Optional, required if Underfrequency Trip 4 Time is set 2. Value must be numeric < Underfrequency Trip 3 3. If Instantaneous Underfrequency Trip is set, value must be > Instantaneous Under frequency Trip | O C | Numeric |  | Planning Team
Generation | Underfrequency Trip Time 4 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | sec | GENERATION | UFREQ_TRIP_TIME4 | 1. Optional, required if Underfrequency Trip 4 is set 2. Value must be numeric >= 0 3. If Underfrequency Trip 4 > 58.4 and <= 59.4, value must be >= 540 4. If Underfrequency Trip 4 > 58 and <= 58.4, value must be >= 30 5. If Underfrequency Trip 4 > 57.5 and <= 58, value must be >= 2 | O C | Numeric |  | Planning Team
Generation | Instantaneous Overfrequency Trip |  | Updated validation rule 05/01/2017 | Protection - GEN |  | Hz | GENERATION | OFREQ_TRIP_INSTANT | 1. Optional 2. Value must be >= 61.8 | O | Float |  | Planning Team | [7 empty] | Glossary needs to define what "Instantaneous" is
Generation | Overfrequency 1 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | Hz | GENERATION | OFREQ_TRIP_HZ1 | 1. Optional, required if Overfrequency Trip 1 Time is set 2. Value must be numeric >= 60.6 3. If Instantaneous Overfrequency Trip is set, value must be < Instantaneous Overfrequency Trip | O C | Numeric |  | Planning Team
Generation | Overfrequency Trip Time 1 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | sec | GENERATION | OFREQ_TRIP_TIME1 | 1. Optional, required if Overfrequency Trip 1 is set 2. Value must be numeric 3. If Overfrequency Trip 1 >= 60.6 and < 61.6, value must be >= 540 4. If Overfrequency Trip 1 >= 61.6 and < 61.8, value must be >= 30 | O C | Numeric |  | Planning Team
Generation | Overfrequency 2 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | Hz | GENERATION | OFREQ_TRIP_HZ2 | 1. Optional, required if Overfrequency Trip 2 Time is set 2. Value must be numeric > Overfrequency Trip 1 3. If Instantaneous Overfrequency Trip is set, value must be < Instantaneous Overfrequency Trip | O C | Numeric |  | Planning Team
Generation | Overfrequency Trip Time 2 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | sec | GENERATION | OFREQ_TRIP_TIME2 | 1. Optional, required if Overfrequency Trip 2 is set 2. Value must be numeric 3. If Overfrequency Trip 2 >= 60.6 and < 61.6 then value must be >= 540 4. If Overfrequency Trip 2 >= 61.6 and < 61.8 then value must be >= 30 | O C | Numeric |  | Planning Team
Generation | Overfrequency 3 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | Hz | GENERATION | OFREQ_TRIP_HZ3 | 1. Required, required if Overfrequency Trip 3 Time is set 2. Value must be numeric > Overfrequency Trip 2 3. If Instantaneous Overfrequency Trip is set, value must be < Instantaneous Overfrequency Trip | O C | Numeric |  | Planning Team
Generation | Overfrequency Trip Time 3 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | sec | GENERATION | OFREQ_TRIP_TIME3 | 1. Optional, required if Overfrequency Trip 3 is set 2. Value must be numeric 3. If Overfrequency Trip 3 >= 60.6 and < 61.6 then value must be >= 540 4. If Overfrequency Trip 3 >= 61.6 and < 61.8 then value must be >= 30 | O C | Numeric |  | Planning Team
Generation | Overfrequency 4 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | Hz | GENERATION | OFREQ_TRIP_HZ4 | 1. Optional, required if Overfrequency Trip 4 Time is set 2. Value must be numeric > Overfrequency Trip 3 3. If Instantaneous Overfrequency Trip is set, value must be < Instantaneous Overfrequency Trip | O C | Numeric |  | Planning Team
Generation | Overfrequency Trip Time 4 |  | Updated validation rule 05/01/2017 | Protection - GEN |  | sec | GENERATION | OFREQ_TRIP_TIME4 | 1 Optional, required if Overfrequency Trip 4 is set 2. Value must be numeric 3. If Overfrequency Trip 4 >= 60.6 and < 61.6, value must be >= 540 4. If Overfrequency Trip 4 >= 61.6 and < 61.8, value be >= 30 | O C | Numeric |  | Planning Team
CC | Protection - CC |  |  | Protection - CC |  |  | Not in table | Not in table | Not all the fields need to be complete. Only the fields that have Data. Upto 3 trains per site can be registered |  |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
CC | GENERATOR DETAILS |  |  | Protection - CC |  |  | Not in table | Not in table
CC | Unit Name | Do not show Message on Audit or Delta |  | Protection - CC |  | List | CCUNIT | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | Y
CC | SITE_CODE |  |  | Protection - CC |  | Automatic | CCUNIT | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | A | Character |  |  |  |  | N | N |  |  |  | This is filled automatically in the form, why is there any validation?
CC | Resource Name (Unit Code/mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | Protection - CC |  | Automatic | CCUNIT | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | Y |  |  |  | This is filled automatically in the form, why is there any validation?
CC | PLANT VOLTAGE PROTECTION |  |  | Protection - CC |  |  | Not in table | Not in table
CC | Breaker Interruption Time |  |  | Protection - CC |  | cycles | CCUNIT | BREAKER_INTERRUP | 1) this field is required 2) Data type must be Integer | R | Integer | B | Planning Team |  |  | N | Y
CC | Instantaneous Undervoltage Trip |  |  | Protection - CC |  | p.u. | CCUNIT | UVOLT_TRIP_INSTANT | 1. Optional 2. Value must be numeric > 0 3. Value should be <= 396 | O | Float | B | Planning Team |  |  | N | Y |  |  |  | Glossary needs to define what "Instantaneous" is
CC | Under voltage 1 |  | Updated validation rule 05/01/2017 | Protection - CC |  | p.u. | CCUNIT | UVOLT_TRIP_VOLT1 | 1. Required Conditional, warning if missing 2. Value must be numeric >= 0 | R C | Float | B | Planning Team
CC | Under voltage Trip Time 1 |  | Updated validation rule 05/01/2017 | Protection - CC |  | sec | CCUNIT | UVOLT_TRIP_TIME1 | 1. Required Conditional, warning if missing 2. Value must be numeric >= 0 | R C | Float |  | Planning Team
CC | Under voltage 2 |  | Updated validation rule 05/01/2017 | Protection - CC |  | p.u. | CCUNIT | UVOLT_TRIP_VOLT2 | 1. Optional Conditional,required if Undervoltage Trip 2 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
CC | Under voltage Trip Time 2 |  | Updated validation rule 05/01/2017 | Protection - CC |  | sec | CCUNIT | UVOLT_TRIP_TIME2 | 1. Optional Conditional, required if Undervoltage Trip 2 is set 2. Value must be numeric > Undervoltage Trip 1 Time | O C | Float |  | Planning Team
CC | Under voltage 3 |  | Updated validation rule 05/01/2017 | Protection - CC |  | p.u. | CCUNIT | UVOLT_TRIP_VOLT3 | 1. Optional Conditional, required if Undervoltage Trip 3 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
CC | Under voltage Trip Time 3 |  | Updated validation rule 05/01/2017 | Protection - CC |  | sec | CCUNIT | UVOLT_TRIP_TIME3 | 1. Optional Conditional, required if Undervoltage Trip 3 is set 2. Value must be numeric > Undervoltage Trip 2 Time | O C | Float |  | Planning Team
CC | Under voltage 4 |  | Updated validation rule 05/01/2017 | Protection - CC |  | p.u. | CCUNIT | UVOLT_TRIP_VOLT4 | 1. Optional Conditional, required if Undervoltage Trip 4 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
CC | Under voltage Trip Time 4 |  | Updated validation rule 05/01/2017 | Protection - CC |  | sec | CCUNIT | UVOLT_TRIP_TIME4 | 1. Optional Conditional, required if Undervoltage Trip 4 is set 2. Value must be numeric > Undervoltage Trip 3 Time | O C | Float |  | Planning Team
CC | Instantaneous Overvoltage Trip |  |  | Protection - CC |  | p.u. | CCUNIT | OVOLT_TRIP_INSTANT | 1. Optional 2. Value must be numeric > 0 3. Value should be <= 396 | O | Float | B | Planning Team |  |  | N | Y |  |  |  | Glossary needs to define what "Instantaneous" is
CC | Overvoltage 1 |  | Updated validation rule 05/01/2017 | Protection - CC |  | p.u. | CCUNIT | OVOLT_TRIP_VOLT1 | 1. Required Conditional, warning if missing 2. Value must be numeric >= 0 | R C | Float | B | Planning Team
CC | Overvoltage Trip Time 1 |  | Updated validation rule 05/01/2017 | Protection - CC |  | sec | CCUNIT | OVOLT_TRIP_TIME1 | 1. Required Conditional, warning if missing 2. Value must be numeric >= 0 | R C | Float | B | Planning Team
CC | Overvoltage 2 |  | Updated validation rule 05/01/2017 | Protection - CC |  | p.u. | CCUNIT | OVOLT_TRIP_VOLT2 | 1. Optional Conditional, required if Overvoltage Trip 2 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
CC | Overvoltage Trip Time 2 |  | Updated validation rule 05/01/2017 | Protection - CC |  | sec | CCUNIT | OVOLT_TRIP_TIME2 | 1. Optional Conditional, required if Overvoltage Trip 2 is set 2. Value must be numeric >= 0 and < Overvoltage Trip 1 Time | O C | Float | B | Planning Team
CC | Overvoltage 3 |  | Updated validation rule 05/01/2017 | Protection - CC |  | p.u. | CCUNIT | OVOLT_TRIP_VOLT3 | 1. Optional Conditional, required if Overvoltage Trip 3 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
CC | Overvoltage Trip Time 3 |  | Updated validation rule 05/01/2017 | Protection - CC |  | sec | CCUNIT | OVOLT_TRIP_TIME3 | 1. Optional Conditional, required if Overvoltage Trip 3 is set 2. Value must be numeric >= 0 and < Overvoltage Trip 2 Time | O C | Float | B | Planning Team
CC | Overvoltage 4 |  | Updated validation rule 05/01/2017 | Protection - CC |  | p.u. | CCUNIT | OVOLT_TRIP_VOLT4 | 1. Optional Conditional, required if Overvoltage Trip 4 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
CC | Overvoltage Trip Time 4 |  | Updated validation rule 05/01/2017 | Protection - CC |  | sec | CCUNIT | OVOLT_TRIP_TIME4 | 1. Optional Conditional, required if Overvoltage Trip 4 is set 2. Value must be numeric >= 0 and < Overvoltage Trip 3 Time | O C | Float | B | Planning Team
CC | PLANT FREQUENCY PROTECTION |  |  | Protection - CC |  |  | Not in table | Not in table
CC | Instantaneous Underfrequency Trip |  | Updated validation rule 05/01/2017 | Protection - CC |  | Hz | CCUNIT | UFREQ_TRIP_INSTANT | 1. Optional 2. Value must be numeric and <= 57.5 | O | Numeric |  | Planning Team | [7 empty] | Glossary needs to define what "Instantaneous" is
CC | Underfrequency 1 |  | Updated validation rule 05/01/2017 | Protection - CC |  | Hz | CCUNIT | UFREQ_TRIP_HZ1 | 1. Optional, required if Under frequency Trip 1 Time is set 2. Value must be numeric <= 59.4 3. If Instantaneous Underfrequency Trip is set, value must be > Instantaneous Under frequency Trip | O C | Numeric |  | Planning Team
CC | Underfrequency Trip Time 1 |  | Updated validation rule 05/01/2017 | Protection - CC |  | sec | CCUNIT | UFREQ_TRIP_TIME1 | 1. Optional, required if Underfrequency Trip 1 is set 2. Value must be numeric 3. If Underfrequency Trip 1 > 58.4 and <= 59.4, value must be >= 540 4. If Underfrequency Trip 1 > 58 and <= 58.4, value must be >= 30 | O C | Numeric |  | Planning Team
CC | Underfrequency 2 |  | Updated validation rule 05/01/2017 | Protection - CC |  | Hz | CCUNIT | UFREQ_TRIP_HZ2 | 1. Optional, required if Underfrequency Trip 2 Time is set 2. Value must be numeric < Underfrequency Trip 1 3. If Instantaneous Underfrequency Trip is set, value must be > Instantaneous Under frequency Trip | O C | Numeric |  | Planning Team
CC | Underfrequency Trip Time 2 |  | Updated validation rule 05/01/2017 | Protection - CC |  | sec | CCUNIT | UFREQ_TRIP_TIME2 | 1. Optional, required if Underfrequency Trip 2 is set 2. Value must be numeric 3. If Underfrequency Trip 2 > 58.4 and <= 59.4, value must be >= 540 4. If Underfrequency Trip 2 > 58 and <= 58.4, value must be >= 30 5. If Underfrequency Trip 2 > 57.5 and <= 58, value must be >= 2 | O C | Numeric |  | Planning Team
CC | Underfrequency 3 |  | Updated validation rule 05/01/2017 | Protection - CC |  | Hz | CCUNIT | UFREQ_TRIP_HZ3 | 1. Optional, required if Underfrequency Trip 3 Time is set 2. Value must be numeric and < Underfrequency Trip 2 3. If Instantaneous Underfrequency Trip is set, value must be > Instantaneous Under frequency Trip | O C | Numeric |  | Planning Team
CC | Underfrequency Trip Time 3 |  | Updated validation rule 05/01/2017 | Protection - CC |  | sec | CCUNIT | UFREQ_TRIP_TIME3 | 1. Optional, required if Underfrequency Trip 3 is set 2. Value must be numeric 3. If Underfrequency Trip 3 > 58.4 and <= 59.4, value must be >= 540 4. If Underfrequency Trip 3 > 58 and <= 58.4, value must be >= 30 5. If Underfrequency Trip 3 > 57.5 and <= 58, value must be >= 2 | O C | Numeric |  | Planning Team
CC | Underfrequency 4 |  | Updated validation rule 05/01/2017 | Protection - CC |  | Hz | CCUNIT | UFREQ_TRIP_HZ4 | 1. Optional, required if Underfrequency Trip 4 Time is set 2. Value must be numeric < Underfrequency Trip 3 3. If Instantaneous Underfrequency Trip is set, value must be > Instantaneous Under frequency Trip | O C | Numeric |  | Planning Team
CC | Underfrequency Trip Time 4 |  | Updated validation rule 05/01/2017 | Protection - CC |  | sec | CCUNIT | UFREQ_TRIP_TIME4 | 1. Optional, required if Underfrequency Trip 4 is set 2. Value must be numeric >= 0 3. If Underfrequency Trip 4 > 58.4 and <= 59.4, value must be >= 540 4. If Underfrequency Trip 4 > 58 and <= 58.4, value must be >= 30 5. If Underfrequency Trip 4 > 57.5 and <= 58, value must be >= 2 | O C | Numeric |  | Planning Team
CC | Instantaneous Overfrequency Trip |  | Updated validation rule 05/01/2017 | Protection - CC |  | Hz | CCUNIT | OFREQ_TRIP_INSTANT | 1. Optional 2. Value must be >= 61.8 | O | Float |  | Planning Team | [7 empty] | Glossary needs to define what "Instantaneous" is
CC | Overfrequency 1 |  | Updated validation rule 05/01/2017 | Protection - CC |  | Hz | CCUNIT | OFREQ_TRIP_HZ1 | 1. Optional, required if Overfrequency Trip 1 Time is set 2. Value must be numeric >= 60.6 3. If Instantaneous Overfrequency Trip is set, value must be < Instantaneous Overfrequency Trip | O C | Numeric |  | Planning Team |  |  | N | Y
CC | Overfrequency Trip Time 1 |  | Updated validation rule 05/01/2017 | Protection - CC |  | sec | CCUNIT | OFREQ_TRIP_TIME1 | 1. Optional, required if Overfrequency Trip 1 is set 2. Value must be numeric 3. If Overfrequency Trip 1 >= 60.6 and < 61.6, value must be >= 540 4. If Overfrequency Trip 1 >= 61.6 and < 61.8, value must be >= 30 | O C | Numeric |  | Planning Team
CC | Overfrequency 2 |  | Updated validation rule 05/01/2017 | Protection - CC |  | Hz | CCUNIT | OFREQ_TRIP_HZ2 | 1. Optional, required if Overfrequency Trip 2 Time is set 2. Value must be numeric > Overfrequency Trip 1 3. If Instantaneous Overfrequency Trip is set, value must be < Instantaneous Overfrequency Trip | O C | Numeric |  | Planning Team
CC | Overfrequency Trip Time 2 |  | Updated validation rule 05/01/2017 | Protection - CC |  | sec | CCUNIT | OFREQ_TRIP_TIME2 | 1. Optional, required if Overfrequency Trip 2 is set 2. Value must be numeric 3. If Overfrequency Trip 2 >= 60.6 and < 61.6 then value must be >= 540 4. If Overfrequency Trip 2 >= 61.6 and < 61.8 then value must be >= 30 | O C | Numeric |  | Planning Team
CC | Overfrequency 3 |  | Updated validation rule 05/01/2017 | Protection - CC |  | Hz | CCUNIT | OFREQ_TRIP_HZ3 | 1. Required, required if Overfrequency Trip 3 Time is set 2. Value must be numeric > Overfrequency Trip 2 3. If Instantaneous Overfrequency Trip is set, value must be < Instantaneous Overfrequency Trip | O C | Numeric |  | Planning Team
CC | Overfrequency Trip Time 3 |  | Updated validation rule 05/01/2017 | Protection - CC |  | sec | CCUNIT | OFREQ_TRIP_TIME3 | 1. Optional, required if Overfrequency Trip 3 is set 2. Value must be numeric 3. If Overfrequency Trip 3 >= 60.6 and < 61.6 then value must be >= 540 4. If Overfrequency Trip 3 >= 61.6 and < 61.8 then value must be >= 30 | O C | Numeric |  | Planning Team
CC | Overfrequency 4 |  | Updated validation rule 05/01/2017 | Protection - CC |  | Hz | CCUNIT | OFREQ_TRIP_HZ4 | 1. Optional, required if Overfrequency Trip 4 Time is set 2. Value must be numeric > Overfrequency Trip 3 3. If Instantaneous Overfrequency Trip is set, value must be < Instantaneous Overfrequency Trip | O C | Numeric |  | Planning Team
CC | Overfrequency Trip Time 4 |  | Updated validation rule 05/01/2017 | Protection - CC |  | sec | CCUNIT | OFREQ_TRIP_TIME4 | 1 Optional, required if Overfrequency Trip 4 is set 2. Value must be numeric 3. If Overfrequency Trip 4 >= 60.6 and < 61.6, value must be >= 540 4. If Overfrequency Trip 4 >= 61.6 and < 61.8, value be >= 30 | O C | Numeric |  | Planning Team
Wind | Protection - Wind |  |  | Protection - RENEWABLE |  |  | Not in table | Not in table | Not all the fields need to be complete. Only the fields that have Data.
Wind | GENERATOR DETAILS |  |  | Protection - RENEWABLE |  |  | Not in table | Not in table
Wind | Unit Name | Do not show Message on Audit or Delta |  | Protection - RENEWABLE |  | List | RENEWABLE | UNIT_NAME | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | Y
Wind | SITE_CODE |  |  | Protection - RENEWABLE |  | Automatic | RENEWABLE | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | A | Character
Wind | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | Protection - RENEWABLE |  | Automatic | RENEWABLE | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | Y |  |  |  | This is filled automatically in the form, why is there any validation?
Wind | PLANT UNDERVOLTAGE PROTECTION |  |  | Protection - RENEWABLE |  |  | Not in table | Not in table
Wind | Breaker Interruption Time |  |  | Protection - RENEWABLE |  | cycles | RENEWABLE | BREAKER_INTERRUP | 1) this field is required 2) Data type must be Integer | R | Integer | B | Planning Team |  |  | N | Y
Wind | Instantaneous Undervoltage Trip |  |  | Protection - RENEWABLE |  | p.u. | RENEWABLE | UVOLT_TRIP_INSTANT | 1. Optional 2. Value must be numeric > 0 3. Value should be <= 396 | O | Float | B | Planning Team |  |  | N | Y |  |  |  | Glossary needs to define what "Instantaneous" is
Wind | Under voltage 1 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | p.u. | RENEWABLE | UVOLT_TRIP_VOLT1 | 1. Required Conditional, warning if missing 2. Value must be numeric >= 0 | R C | Float | B | Planning Team
Wind | Under voltage Trip Time 1 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | UVOLT_TRIP_TIME1 | 1. Required Conditional, warning if missing 2. Value must be numeric >= 0 | R C | Float |  | Planning Team
Wind | Under voltage 2 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | p.u. | RENEWABLE | UVOLT_TRIP_VOLT2 | 1. Optional Conditional,required if Undervoltage Trip 2 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
Wind | Under voltage Trip Time 2 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | UVOLT_TRIP_TIME2 | 1. Optional Conditional, required if Undervoltage Trip 2 is set 2. Value must be numeric > Undervoltage Trip 1 Time | O C | Float |  | Planning Team
Wind | Under voltage 3 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | p.u. | RENEWABLE | UVOLT_TRIP_VOLT3 | 1. Optional Conditional, required if Undervoltage Trip 3 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
Wind | Under voltage Trip Time 3 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | UVOLT_TRIP_TIME3 | 1. Optional Conditional, required if Undervoltage Trip 3 is set 2. Value must be numeric > Undervoltage Trip 2 Time | O C | Float |  | Planning Team
Wind | Under voltage 4 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | p.u. | RENEWABLE | UVOLT_TRIP_VOLT4 | 1. Optional Conditional, required if Undervoltage Trip 4 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
Wind | Under voltage Trip Time 4 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | UVOLT_TRIP_TIME4 | 1. Optional Conditional, required if Undervoltage Trip 4 is set 2. Value must be numeric > Undervoltage Trip 3 Time | O C | Float |  | Planning Team
Wind | Instantaneous Overvoltage Trip |  |  | Protection - RENEWABLE |  | p.u. | RENEWABLE | OVOLT_TRIP_INSTANT | 1. Optional 2. Value must be numeric > 0 3. Value should be <= 396 | O | Float | B | Planning Team |  |  | N | Y |  |  |  | Glossary needs to define what "Instantaneous" is
Wind | Overvoltage 1 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | p.u. | RENEWABLE | OVOLT_TRIP_VOLT1 | 1. Required Conditional, warning if missing 2. Value must be numeric >= 0 | R C | Float | B | Planning Team
Wind | Overvoltage Trip Time 1 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | OVOLT_TRIP_TIME1 | 1. Required Conditional, warning if missing 2. Value must be numeric >= 0 | R C | Float | B | Planning Team
Wind | Overvoltage 2 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | p.u. | RENEWABLE | OVOLT_TRIP_VOLT2 | 1. Optional Conditional, required if Overvoltage Trip 2 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
Wind | Overvoltage Trip Time 2 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | OVOLT_TRIP_TIME2 | 1. Optional Conditional, required if Overvoltage Trip 2 is set 2. Value must be numeric >= 0 and < Overvoltage Trip 1 Time | O C | Float | B | Planning Team
Wind | Overvoltage 3 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | p.u. | RENEWABLE | OVOLT_TRIP_VOLT3 | 1. Optional Conditional, required if Overvoltage Trip 3 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
Wind | Overvoltage Trip Time 3 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | OVOLT_TRIP_TIME3 | 1. Optional Conditional, required if Overvoltage Trip 3 is set 2. Value must be numeric >= 0 and < Overvoltage Trip 2 Time | O C | Float | B | Planning Team
Wind | Overvoltage 4 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | p.u. | RENEWABLE | OVOLT_TRIP_VOLT4 | 1. Optional Conditional, required if Overvoltage Trip 4 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
Wind | Overvoltage Trip Time 4 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | OVOLT_TRIP_TIME4 | 1. Optional Conditional, required if Overvoltage Trip 4 is set 2. Value must be numeric >= 0 and < Overvoltage Trip 3 Time | O C | Float | B | Planning Team
Wind | PLANT OVERFREQUENCY PROTECTION |  |  | Protection - RENEWABLE |  |  | Not in table | Not in table
Wind | Instantaneous Underfrequency Trip |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | Hz | RENEWABLE | UFREQ_TRIP_INSTANT | UFREQ_TRIP_INSTANT 1. Optional 2. Value must be numeric and <= 57.5 | O | Numeric |  | Planning Team |  |  | N | Y |  |  |  | Glossary needs to define what "Instantaneous" is
Wind | Underfrequency 1 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | Hz | RENEWABLE | UFREQ_TRIP_HZ1 | 1. Optional, required if Under frequency Trip 1 Time is set 2. Value must be numeric <= 59.4 3. If Instantaneous Underfrequency Trip is set, value must be > Instantaneous Under frequency Trip | O C | Numeric |  | Planning Team |  |  | N | Y
Wind | Underfrequency Trip Time 1 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | UFREQ_TRIP_TIME1 | 1. Optional, required if Underfrequency Trip 1 is set 2. Value must be numeric 3. If Underfrequency Trip 1 > 58.4 and <= 59.4, value must be >= 540 4. If Underfrequency Trip 1 > 58 and <= 58.4, value must be >= 30 5. If Underfrequency Trip 1 > 57.5 and <= 58, value must be >= 2 | O C | Numeric |  | Planning Team
Wind | Underfrequency 2 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | Hz | RENEWABLE | UFREQ_TRIP_HZ2 | 1. Optional, required if Underfrequency Trip 2 Time is set 2. Value must be numeric < Underfrequency Trip 1 3. If Instantaneous Underfrequency Trip is set, value must be > Instantaneous Under frequency Trip | O C | Numeric |  | Planning Team
Wind | Underfrequency Trip Time 2 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | UFREQ_TRIP_TIME2 | 1. Optional, required if Underfrequency Trip 2 is set 2. Value must be numeric 3. If Underfrequency Trip 2 > 58.4 and <= 59.4, value must be >= 540 4. If Underfrequency Trip 2 > 58 and <= 58.4, value must be >= 30 5. If Underfrequency Trip 2 > 57.5 and <= 58, value must be >= 2 | O C | Numeric |  | Planning Team
Wind | Underfrequency 3 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | Hz | RENEWABLE | UFREQ_TRIP_HZ3 | 1. Optional, required if Underfrequency Trip 3 Time is set 2. Value must be numeric and < Underfrequency Trip 2 3. If Instantaneous Underfrequency Trip is set, value must be > Instantaneous Under frequency Trip | O C | Numeric |  | Planning Team
Wind | Underfrequency Trip Time 3 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | UFREQ_TRIP_TIME3 | 1. Optional, required if Underfrequency Trip 3 is set 2. Value must be numeric 3. If Underfrequency Trip 3 > 58.4 and <= 59.4, value must be >= 540 4. If Underfrequency Trip 3 > 58 and <= 58.4, value must be >= 30 5. If Underfrequency Trip 3 > 57.5 and <= 58, value must be >= 2 | O C | Numeric |  | Planning Team
Wind | Underfrequency 4 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | Hz | RENEWABLE | UFREQ_TRIP_HZ4 | 1. Optional, required if Underfrequency Trip 4 Time is set 2. Value must be numeric < Underfrequency Trip 3 3. If Instantaneous Underfrequency Trip is set, value must be > Instantaneous Under frequency Trip | O C | Numeric |  | Planning Team
Wind | Underfrequency Trip Time 4 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | UFREQ_TRIP_TIME4 | 1. Optional, required if Underfrequency Trip 4 is set 2. Value must be numeric >= 0 3. If Underfrequency Trip 4 > 58.4 and <= 59.4, value must be >= 540 4. If Underfrequency Trip 4 > 58 and <= 58.4, value must be >= 30 5. If Underfrequency Trip 4 > 57.5 and <= 58, value must be >= 2 | O C | Numeric |  | Planning Team
Wind | Instantaneous Overfrequency Trip |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | Hz | RENEWABLE | OFREQ_TRIP_INSTANT | 1. Optional 2. Value must be >= 61.8 | O | Float |  | Planning Team | [7 empty] | Glossary needs to define what "Instantaneous" is
Wind | Overfrequency 1 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | Hz | RENEWABLE | OFREQ_TRIP_HZ1 | 1. Optional, required if Overfrequency Trip 1 Time is set 2. Value must be numeric >= 60.6 3. If Instantaneous Overfrequency Trip is set, value must be < Instantaneous Overfrequency Trip | O C | Numeric |  | Planning Team
Wind | Overfrequency Trip Time 1 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | OFREQ_TRIP_TIME1 | 1. Optional, required if Overfrequency Trip 1 is set 2. Value must be numeric 3. If Overfrequency Trip 1 >= 60.6 and < 61.6, value must be >= 540 4. If Overfrequency Trip 1 >= 61.6 and < 61.8, value must be >= 30 | O C | Numeric |  | Planning Team
Wind | Overfrequency 2 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | Hz | RENEWABLE | OFREQ_TRIP_HZ2 | 1. Optional, required if Overfrequency Trip 2 Time is set 2. Value must be numeric > Overfrequency Trip 1 3. If Instantaneous Overfrequency Trip is set, value must be < Instantaneous Overfrequency Trip | O C | Numeric |  | Planning Team
Wind | Overfrequency Trip Time 2 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | OFREQ_TRIP_TIME2 | 1. Optional, required if Overfrequency Trip 2 is set 2. Value must be numeric 3. If Overfrequency Trip 2 >= 60.6 and < 61.6 then value must be >= 540 4. If Overfrequency Trip 2 >= 61.6 and < 61.8 then value must be >= 30 | O C | Numeric |  | Planning Team
Wind | Overfrequency 3 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | Hz | RENEWABLE | OFREQ_TRIP_HZ3 | 1. Required, required if Overfrequency Trip 3 Time is set 2. Value must be numeric > Overfrequency Trip 2 3. If Instantaneous Overfrequency Trip is set, value must be < Instantaneous Overfrequency Trip | O C | Numeric |  | Planning Team
Wind | Overfrequency Trip Time 3 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | OFREQ_TRIP_TIME3 | 1. Optional, required if Overfrequency Trip 3 is set 2. Value must be numeric 3. If Overfrequency Trip 3 >= 60.6 and < 61.6 then value must be >= 540 4. If Overfrequency Trip 3 >= 61.6 and < 61.8 then value must be >= 30 | O C | Numeric |  | Planning Team
Wind | Overfrequency 4 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | Hz | RENEWABLE | OFREQ_TRIP_HZ4 | 1. Optional, required if Overfrequency Trip 4 Time is set 2. Value must be numeric > Overfrequency Trip 3 3. If Instantaneous Overfrequency Trip is set, value must be < Instantaneous Overfrequency Trip | O C | Numeric |  | Planning Team
Wind | Overfrequency Trip Time 4 |  | Updated validation rule 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | OFREQ_TRIP_TIME4 | 1 Optional, required if Overfrequency Trip 4 is set 2. Value must be numeric 3. If Overfrequency Trip 4 >= 60.6 and < 61.6, value must be >= 540 4. If Overfrequency Trip 4 >= 61.6 and < 61.8, value be >= 30 | O C | Numeric |  | Planning Team
Wind | TURBINE VRT CAPABILITY |  |  | Protection - RENEWABLE |  |  | Not in table
Wind | Does the Resource Have the Manufacturer's Technical Document / Simulation Results / Test Result, Etc. Describing The Turbine Technology & Vrt OPTIons Purchased With Turbine, If Any |  |  | Protection - RENEWABLE |  |  | Not in table | Not in table | Select from the list: Y or N | R
Wind | Do Personnel (onsite Operator/engineer Etc.) Have Control To Enable/disable Or Change The Settings For Voltage Ride-through |  |  | Protection - RENEWABLE |  |  | Not in table | Not in table | Select from the list: Y or N | R | Dropdown List
Wind | Does The Resource Use Dynamic Reactive Devices (svc/statcom, Etc.) At The Wind Farm? - (note: Capacitor Banks Used For Conventional Reactive Support Cannot Be Considered As Dynamic Reactive Devices) - If Yes, Please Provide Supporting Documentation. (manufacturer's Technical Document, Pss/e Model Etc.) |  |  | Protection - RENEWABLE |  |  | Not in table | Not in table | 1) This field is required 2) Data type must 'Y' or 'N' 3) Generate an Warning if blank, if 'Y', test results must be attached | C | Dropdown List | B,DVB | [8 empty] | Not supported in glossary
Wind | Does the Resource Have the Turbine Voltage & Frequency Protection Settings As Per Manufacturer - Technical Document And/or Spec Sheet |  |  | Protection - RENEWABLE |  |  | Not in table | Not in table | 1) This field is required 2) Data type must 'Y' or 'N' 3) Generate an Warning if blank, if 'Y', test results must be attached | C | Dropdown List | B,DVB | [8 empty] | Not supported in glossary
Wind | Does The Resource Have Plant Voltage Protection? If Yes, Please Provide Supporting Documentation. |  |  | Protection - RENEWABLE |  |  | Not in table | Not in table | Select from the list: Y or N |  | Dropdown List | [9 empty] | Not supported in glossary
Wind | Does The Resource Have Feeder Voltage Protection? If Yes, Please Provide Supporting Documentation. |  |  | Protection - RENEWABLE |  |  | Not in table | Not in table | Select from the list: Y or N |  | Dropdown List | [9 empty] | Not supported in glossary
Solar Photovoltaic (PV) | Protection - Solar Photovoltaic (PV) |  |  | Protection - RENEWABLE |  |  | Not in table | Not in table | Not all the fields need to be complete. Only the fields that have Data.
Solar Photovoltaic (PV) | GENERATOR DETAILS |  |  | Protection - RENEWABLE |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | Unit Name | Do not show Message on Audit or Delta | Added 05/01/2017 | Protection - RENEWABLE |  | List | RENEWABLE | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | Y
Solar Photovoltaic (PV) | SITE |  | Added 05/01/2017 | Protection - RENEWABLE |  | Automatic | RENEWABLE | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters |  | Character
Solar Photovoltaic (PV) | Resource Name (Unit Code/Mnemonic) |  | Added 05/01/2017 | Protection - RENEWABLE |  | Automatic | RENEWABLE | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | Y
Solar Photovoltaic (PV) | PLANT UNDERVOLTAGE PROTECTION |  |  | Protection - RENEWABLE |  |  | Not in table | Not in table | 1) this field is required 2) Data type must be Integer
Solar Photovoltaic (PV) | Breaker Interruption Time |  | Added 05/01/2017 | Protection - RENEWABLE |  | cycles | RENEWABLE | BREAKER_INTERRUP | 1) this field is required 2) Data type must be Integer | R | Integer | B | Planning Team |  |  | N | Y
Solar Photovoltaic (PV) | Instantaneous Undervoltage Trip |  | Added 05/01/2017 | Protection - RENEWABLE |  | p.u. | RENEWABLE | UVOLT_TRIP_INSTANT | 1. Optional 2. Value must be numeric > 0 3. Value should be <= 396 | O | Float | B | Planning Team |  |  | N | Y
Solar Photovoltaic (PV) | Under voltage 1 |  | Added 05/01/2017 | Protection - RENEWABLE |  | p.u. | RENEWABLE | UVOLT_TRIP_VOLT1 | 1. Required, warning if missing 2. Value must be numeric >= 0 | R C | Float | B | Planning Team
Solar Photovoltaic (PV) | Under voltage Trip Time 1 |  | Added 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | UVOLT_TRIP_TIME1 | 1. Required, warning if missing 2. Value must be numeric >= 0 | R C | Float |  | Planning Team
Solar Photovoltaic (PV) | Under voltage 2 |  | Added 05/01/2017 | Protection - RENEWABLE |  | p.u. | RENEWABLE | UVOLT_TRIP_VOLT2 | 1. Optional, required if Undervoltage Trip 2 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
Solar Photovoltaic (PV) | Under voltage Trip Time 2 |  | Added 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | UVOLT_TRIP_TIME2 | 1. Optional, required if Undervoltage Trip 2 is set 2. Value must be numeric > Undervoltage Trip 1 Time | O C | Float |  | Planning Team
Solar Photovoltaic (PV) | Under voltage 3 |  | Added 05/01/2017 | Protection - RENEWABLE |  | p.u. | RENEWABLE | UVOLT_TRIP_VOLT3 | 1. Optional, required if Undervoltage Trip 3 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
Solar Photovoltaic (PV) | Under voltage Trip Time 3 |  | Added 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | UVOLT_TRIP_TIME3 | 1. Optional, required if Undervoltage Trip 3 is set 2. Value must be numeric > Undervoltage Trip 2 Time | O C | Float |  | Planning Team
Solar Photovoltaic (PV) | Under voltage 4 |  | Added 05/01/2017 | Protection - RENEWABLE |  | p.u. | RENEWABLE | UVOLT_TRIP_VOLT4 | 1. Optional, required if Undervoltage Trip 4 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
Solar Photovoltaic (PV) | Under voltage Trip Time 4 |  | Added 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | UVOLT_TRIP_TIME4 | 1. Optional, required if Undervoltage Trip 4 is set 2. Value must be numeric > Undervoltage Trip 3 Time | O C | Float |  | Planning Team
Solar Photovoltaic (PV) | Instantaneous Overvoltage Trip |  | Added 05/01/2017 | Protection - RENEWABLE |  | p.u. | RENEWABLE | OVOLT_TRIP_INSTANT | 1. Optional 2. Value must be numeric > 0 3. Value should be <= 396 | O C | Float | B | Planning Team |  |  | N | Y
Solar Photovoltaic (PV) | Overvoltage 1 |  | Added 05/01/2017 | Protection - RENEWABLE |  | p.u. | RENEWABLE | OVOLT_TRIP_VOLT1 | 1. Required, warning if missing 2. Value must be numeric >= 0 | R C | Float | B | Planning Team
Solar Photovoltaic (PV) | Overvoltage Trip Time 1 |  | Added 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | OVOLT_TRIP_TIME1 | 1. Required, warning if missing 2. Value must be numeric >= 0 | R C | Float | B | Planning Team
Solar Photovoltaic (PV) | Overvoltage 2 |  | Added 05/01/2017 | Protection - RENEWABLE |  | p.u. | RENEWABLE | OVOLT_TRIP_VOLT2 | 1. Optional, required if Overvoltage Trip 2 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
Solar Photovoltaic (PV) | Overvoltage Trip Time 2 |  | Added 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | OVOLT_TRIP_TIME2 | 1. Optional, required if Overvoltage Trip 2 is set 2. Value must be numeric >= 0 and < Overvoltage Trip 1 Time | O C | Float | B | Planning Team
Solar Photovoltaic (PV) | Overvoltage 3 |  | Added 05/01/2017 | Protection - RENEWABLE |  | p.u. | RENEWABLE | OVOLT_TRIP_VOLT3 | 1. Optional, required if Overvoltage Trip 3 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
Solar Photovoltaic (PV) | Overvoltage Trip Time 3 |  | Added 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | OVOLT_TRIP_TIME3 | 1. Optional, required if Overvoltage Trip 3 is set 2. Value must be numeric >= 0 and < Overvoltage Trip 2 Time | O C | Float | B | Planning Team
Solar Photovoltaic (PV) | Overvoltage 4 |  | Added 05/01/2017 | Protection - RENEWABLE |  | p.u. | RENEWABLE | OVOLT_TRIP_VOLT4 | 1. Optional, required if Overvoltage Trip 4 Time is set 2. Value must be numeric >= 0 | O C | Float | B | Planning Team
Solar Photovoltaic (PV) | Overvoltage Trip Time 4 |  | Added 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | OVOLT_TRIP_TIME4 | 1. Optional, required if Overvoltage Trip 4 is set 2. Value must be numeric >= 0 and < Overvoltage Trip 3 Time | O C | Float | B | Planning Team
Solar Photovoltaic (PV) | PLANT OVERFREQUENCY PROTECTION |  |  | Protection - RENEWABLE |  |  | Not in table | Not in table
Solar Photovoltaic (PV) | Instantaneous Underfrequency Trip |  | Added 05/01/2017 | Protection - RENEWABLE |  | Hz | RENEWABLE | UFREQ_TRIP_INSTANT | 1. Optional 2. Value must be numeric and <= 57.5 | O | Numeric |  | Planning Team |  |  | N | Y
Solar Photovoltaic (PV) | Underfrequency 1 |  | Added 05/01/2017 | Protection - RENEWABLE |  | Hz | RENEWABLE | UFREQ_TRIP_HZ1 | 1. Optional, required if Under frequency Trip 1 Time is set 2. Value must be numeric <= 59.4 3. If Instantaneous Underfrequency Trip is set, value must be > Instantaneous Under frequency Trip | O C | Numeric |  | Planning Team |  |  | N | Y
Solar Photovoltaic (PV) | Underfrequency Trip Time 1 |  | Added 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | UFREQ_TRIP_TIME1 | 1. Optional, required if Underfrequency Trip 1 is set 2. Value must be numeric 3. If Underfrequency Trip 1 > 58.4 and <= 59.4, value must be >= 540 4. If Underfrequency Trip 1 > 58 and <= 58.4, value must be >= 30 5. If Underfrequency Trip 1 > 57.5 and <= 58, value must be >= 2 | O C | Numeric |  | Planning Team
Solar Photovoltaic (PV) | Underfrequency 2 |  | Added 05/01/2017 | Protection - RENEWABLE |  | Hz | RENEWABLE | UFREQ_TRIP_HZ2 | 1. Optional, required if Underfrequency Trip 2 Time is set 2. Value must be numeric < Underfrequency Trip 1 3. If Instantaneous Underfrequency Trip is set, value must be > Instantaneous Under frequency Trip | O C | Numeric |  | Planning Team
Solar Photovoltaic (PV) | Underfrequency Trip Time 2 |  | Added 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | UFREQ_TRIP_TIME2 | 1. Optional, required if Underfrequency Trip 2 is set 2. Value must be numeric 3. If Underfrequency Trip 2 > 58.4 and <= 59.4, value must be >= 540 4. If Underfrequency Trip 2 > 58 and <= 58.4, value must be >= 30 5. If Underfrequency Trip 2 > 57.5 and <= 58, value must be >= 2 | O C | Numeric |  | Planning Team
Solar Photovoltaic (PV) | Underfrequency 3 |  | Added 05/01/2017 | Protection - RENEWABLE |  | Hz | RENEWABLE | UFREQ_TRIP_HZ3 | 1. Optional, required if Underfrequency Trip 3 Time is set 2. Value must be numeric and < Underfrequency Trip 2 3. If Instantaneous Underfrequency Trip is set, value must be > Instantaneous Under frequency Trip | O C | Numeric |  | Planning Team
Solar Photovoltaic (PV) | Underfrequency Trip Time 3 |  | Added 05/01/2017 | Protection - RENEWABLE |  |  |  | UFREQ_TRIP_TIME3 | 1. Optional, required if Underfrequency Trip 3 is set 2. Value must be numeric 3. If Underfrequency Trip 3 > 58.4 and <= 59.4, value must be >= 540 4. If Underfrequency Trip 3 > 58 and <= 58.4, value must be >= 30 5. If Underfrequency Trip 3 > 57.5 and <= 58, value must be >= 2 | O C | Numeric |  | Planning Team
Solar Photovoltaic (PV) | Underfrequency 4 |  | Added 05/01/2017 | Protection - RENEWABLE |  | Hz | RENEWABLE | UFREQ_TRIP_HZ4 | 1. Optional, required if Underfrequency Trip 4 Time is set 2. Value must be numeric < Underfrequency Trip 3 3. If Instantaneous Underfrequency Trip is set, value must be > Instantaneous Under frequency Trip | O C | Numeric |  | Planning Team
Solar Photovoltaic (PV) | Underfrequency Trip Time 4 |  | Added 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | UFREQ_TRIP_TIME4 | 1. Optional, required if Underfrequency Trip 4 is set 2. Value must be numeric >= 0 3. If Underfrequency Trip 4 > 58.4 and <= 59.4, value must be >= 540 4. If Underfrequency Trip 4 > 58 and <= 58.4, value must be >= 30 5. If Underfrequency Trip 4 > 57.5 and <= 58, value must be >= 2 | O C | Numeric |  | Planning Team
Solar Photovoltaic (PV) | Instantaneous Overfrequency Trip |  | Added 05/01/2017 | Protection - RENEWABLE |  | Hz | RENEWABLE | OFREQ_TRIP_INSTANT | 1. Optional 2. Value must be >= 61.8 | O | Float |  | Planning Team |  |  | N | Y
Solar Photovoltaic (PV) | Overfrequency 1 |  | Added 05/01/2017 | Protection - RENEWABLE |  | Hz | RENEWABLE | OFREQ_TRIP_HZ1 | 1. Optional, required if Overfrequency Trip 1 Time is set 2. Value must be numeric >= 60.6 3. If Instantaneous Overfrequency Trip is set, value must be < Instantaneous Overfrequency Trip | O C | Numeric |  | Planning Team
Solar Photovoltaic (PV) | Overfrequency Trip Time 1 |  | Added 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | OFREQ_TRIP_TIME1 | 1. Optional, required if Overfrequency Trip 1 is set 2. Value must be numeric 3. If Overfrequency Trip 1 >= 60.6 and < 61.6, value must be >= 540 4. If Overfrequency Trip 1 >= 61.6 and < 61.8, value must be >= 30 | O C | Numeric |  | Planning Team
Solar Photovoltaic (PV) | Overfrequency 2 |  | Added 05/01/2017 | Protection - RENEWABLE |  | Hz | RENEWABLE | OFREQ_TRIP_HZ2 | 1. Optional, required if Overfrequency Trip 2 Time is set 2. Value must be numeric > Overfrequency Trip 1 3. If Instantaneous Overfrequency Trip is set, value must be < Instantaneous Overfrequency Trip | O C | Numeric |  | Planning Team
Solar Photovoltaic (PV) | Overfrequency Trip Time 2 |  | Added 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | OFREQ_TRIP_TIME2 | 1. Optional, required if Overfrequency Trip 2 is set 2. Value must be numeric 3. If Overfrequency Trip 2 >= 60.6 and < 61.6 then value must be >= 540 4. If Overfrequency Trip 2 >= 61.6 and < 61.8 then value must be >= 30 | O C | Numeric |  | Planning Team
Solar Photovoltaic (PV) | Overfrequency 3 |  | Added 05/01/2017 | Protection - RENEWABLE |  | Hz | RENEWABLE | OFREQ_TRIP_HZ3 | 1. Required, required if Overfrequency Trip 3 Time is set 2. Value must be numeric > Overfrequency Trip 2 3. If Instantaneous Overfrequency Trip is set, value must be < Instantaneous Overfrequency Trip | O C | Numeric |  | Planning Team
Solar Photovoltaic (PV) | Overfrequency Trip Time 3 |  | Added 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | OFREQ_TRIP_TIME3 | 1. Optional, required if Overfrequency Trip 3 is set 2. Value must be numeric 3. If Overfrequency Trip 3 >= 60.6 and < 61.6 then value must be >= 540 4. If Overfrequency Trip 3 >= 61.6 and < 61.8 then value must be >= 30 | O C | Numeric |  | Planning Team
Solar Photovoltaic (PV) | Overfrequency 4 |  | Added 05/01/2017 | Protection - RENEWABLE |  | Hz | RENEWABLE | OFREQ_TRIP_HZ4 | 1. Optional, required if Overfrequency Trip 4 Time is set 2. Value must be numeric > Overfrequency Trip 3 3. If Instantaneous Overfrequency Trip is set, value must be < Instantaneous Overfrequency Trip | O C | Numeric |  | Planning Team |  |  | N | Y
Solar Photovoltaic (PV) | Overfrequency Trip Time 4 |  | Added 05/01/2017 | Protection - RENEWABLE |  | sec | RENEWABLE | OFREQ_TRIP_TIME4 | 1 Optional, required if Overfrequency Trip 4 is set 2. Value must be numeric 3. If Overfrequency Trip 4 >= 60.6 and < 61.6, value must be >= 540 4. If Overfrequency Trip 4 >= 61.6 and < 61.8, value be >= 30 | O C | Numeric |  | Planning Team
Solar Photovoltaic (PV) | Collector System - Renewable | Corrected Tab name 03/26/2012 |  | Collector System - RENEWABLE |  |  | Not in table | Not in table |  |  |  |  | Model Administration
Wind | GENERATOR DETAILS | Corrected Tab name 03/26/2012 |  | Collector System - RENEWABLE |  |  | Not in table | Not in table |  |  |  |  | Model Administration
Wind | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code 05/17/2012 Update #3 validation Added field in form 03/26/2012 |  | Collector System - RENEWABLE |  | Automatic | COLLECTOR_SYS | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Model Administration | Lodestar,NMMS |  | N | Y |  |  |  | This is filled automatically in the form, why is there any validation?
Wind | COLLECTION SYSTEM DETAILED MODEL | Corrected Tab name 03/26/2012 |  | Collector System - RENEWABLE |  |  | Not in table | Not in table |  |  |  |  | Model Administration
Wind | Cable Type | 05/15/2012 changed validation #3 to an ERROR message. Corrected Tab name 03/26/2012 | ADDED 06/27/2012 | Collector System - RENEWABLE | CollectorSystem.View |  | COLLECTOR_SYS | CABLE_TYPE | 1) This field is required 2) Data type must string 3) Generate an error if blank | R | String | B,DVB | Model Administration |  |  | N | Y
Wind | Voltage Level kV | 05/15/2012 changed validation #3 to an ERROR message. | ADDED 06/27/2012 | Collector System - RENEWABLE | CollectorSystem.View | kv | COLLECTOR_SYS | VT_LEVEL_KV | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | T R | Float | B/DVE | Model Administration |  |  | N | Y
Wind | POSITIVE SEQUENCE DATA | Corrected Tab name 03/26/2012 |  | Collector System - RENEWABLE |  |  | Not in table | Not in table |  |  |  |  | Model Administration
Wind | R/kft | 05/15/2012 changed validation #3 to an ERROR message. | ADDED 06/27/2012 | Collector System - RENEWABLE | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_R_KFT | 1) This field is required 2) Data type must float 3) Generate an error if blank | R | Float | B,DVB | Model Administration |  |  | N | Y
Wind | X/kft | 05/15/2012 changed validation #3 to an ERROR message. | ADDED 06/27/2012 | Collector System - RENEWABLE | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_X_KFT | 1) This field is required 2) Data type must float 3) Generate an error if blank | R | String | B,DVB | Model Administration |  |  | N | Y
Wind | Charging Bc/kft | 05/15/2012 changed validation #3 to an ERROR message. | ADDED 06/27/2012 | Collector System - RENEWABLE | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_CHRG_BC_KFT | 1) This field is required 2) Data type must float 3) Generate an error if blank | R | Float | B,DVB | Model Administration |  |  | N | Y
Wind | ZERO SEQUENCE DATA | Corrected Tab name 03/26/2012 |  | Collector System - RENEWABLE |  |  | Not in table | Not in table |  |  |  |  | Model Administration
Wind | R0/kft | 05/15/2012 changed validation #3 to an ERROR message. | ADDED 06/27/2012 | Collector System - RENEWABLE | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | ZERO_R0_KFT | 1) This field is required 2) Data type must float 3) Generate an error if blank | R | Float | B,DVB | Model Administration |  |  | N | Y
Wind | X0/kft | 05/15/2012 changed validation #3 to an ERROR message. | ADDED 06/27/2012 | Collector System - RENEWABLE | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | ZERO_X0_KFT | 1) This field is required 2) Data type must float 3) Generate an error if blank | R | Float | B,DVB | Model Administration |  |  | N | Y
Wind | Collector System-Renew Seg Data | Corrected Tab name 03/26/2012 |  | Collector System-Renew Seg Data |  |  | Not in table | Not in table |  |  |  |  | Model Administration
Wind | GENERATOR DETAILS | Corrected Tab name 03/26/2012 |  | Collector System-Renew Seg Data |  |  | Not in table | Not in table |  |  |  |  | Model Administration
Wind | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code 05/17/2012 Update #3 validation Added field in form 03/26/2012 |  | Collector System-Renew Seg Data |  | Automatic | CABLE_SEG_DATA | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Model Administration | Lodestar,NMMS |  | N | Y |  |  |  | This is filled automatically in the form, why is there any validation?
Wind | Cable Type | Corrected Tab name 03/26/2012 |  | Collector System-Renew Seg Data |  |  | Not in table | Not in table |  |  |  |  | Model Administration
Wind | Cable Type | 05/15/2012 changed validation #3 to an ERROR message. | ADDED 06/27/2012 | Collector System-Renew Seg Data | CollectorSystem_SegData.View | List | CABLE_SEG_DATA | CABLE_TYPE | 1) This field is required 2) Data type must string 3) Generate an error if blank | R | String | B,DVB | Model Administration |  |  | N | Y
Wind | WIND SEGAMENT DETAILS | Corrected Tab name 03/26/2012 |  | Collector System-Renew Seg Data |  |  | Not in table | Not in table |  |  |  |  | Model Administration
Wind | From | 08/27/2012 Changed # 2 validation 05/15/2012 changed validation #3 to an ERROR message. | 08/27/12 Corrected to allow Alpha/Numeric values ADDED 06/27/2012 | Collector System-Renew Seg Data | CollectorSystem_SegData.View | alpha/numeric | CABLE_SEG_DATA | CABLE_SEG_DATA_FROM | 1) This field is required 2) Data type must alpha/numeric but may include underscore and dashes, hyphen, slash, and spaces, "¦" and "#" 3) Generate an error if blank | R |  | B,DVB | Model Administration |  |  | N | Y
Wind | To | 08/27/2012 Changed # 2 validation 05/15/2012 changed validation #3 to an ERROR message. | 08/27/12 Corrected to allow Alpha/Numeric values ADDED 06/27/2012 | Collector System-Renew Seg Data | CollectorSystem_SegData.View | alpha/numeric | CABLE_SEG_DATA | CABLE_SEG_DATA_TO | 1) This field is required 2) Data type must alpha/numeric but may include underscore and dashes, hyphen, slash, and spaces, "¦" and "#" 3) Generate an error if blank | R |  | B,DVB | Model Administration |  |  | N | Y
Wind | Circuit Number | 08/27/2012 Changed # 2 validation 05/15/2012 changed validation #3 to an ERROR message. | 08/27/12 Corrected to allow Alpha/Numeric values ADDED 06/27/2012 | Collector System-Renew Seg Data | CollectorSystem_SegData.View | alpha/numeric | CABLE_SEG_DATA | CIRCT_NUM | 1) This field is required 2) Data type must alpha/numeric but may include underscore and dashes, hyphen, slash, and spaces, "¦" and "#" 3) Generate an error if blank | R |  | B,DVB | Model Administration |  |  | N | Y
Wind | Voltage Level | 05/15/2012 changed validation #3 to an ERROR message. | ADDED 06/27/2012 | Collector System-Renew Seg Data | CollectorSystem_SegData.View | kV | CABLE_SEG_DATA | VT_LEVL | 1) This field is required 2) Data type must alpha/numeric but may include underscore and dashes, hyphen, slash, and spaces, "¦" and "#" 3) Generate an error if blank | T R | Float | B/DVE | Model Administration |  |  | N | Y
Wind | Cable Segment Length | 05/15/2012 changed validation #3 to an ERROR message. | ADDED 06/27/2012 | Collector System-Renew Seg Data | CollectorSystem_SegData.View | in kft | CABLE_SEG_DATA | CABLE_SEG_LENTH | 1) This field is required 2) Data type must alpha/numeric but may include underscore and dashes, hyphen, slash, and spaces, "¦" and "#" 3) Generate an error if blank | R | Float | B,DVB | Model Administration |  |  | N | Y
Wind | Number of Turbines on cable segment | 05/15/2012 changed validation #3 to an ERROR message. | ADDED 06/27/2012 | Collector System-Renew Seg Data | CollectorSystem_SegData.View | Integer | CABLE_SEG_DATA | NUM_TURBIN_ON_CABLE_SEG | 1) This field is required 2) Data type must alpha/numeric but may include underscore and dashes, hyphen, slash, and spaces, "¦" and "#" 3) Generate an error if blank | R | Integer | B,DVB | Model Administration |  |  | N | Y
Wind | UNIT_CABLE_FROM_TO_CIRCUIT Hidden Field on Form | 12/10/13 Add field for Reporting purpose | 12/10/13 Add field for Reporting purpose | Collector System-Renew Seg Data | CollectorSystem_SegData.View | Automatic | CABLE_SEG_DATA | UNIT_CABLE_FROM_TO_CIRCUIT | Concantenate (Unit_Code_CABLE_TYPE_CABLE_SEG_DATA_FROM_CABLE_SEG_DATA_TO_CIRCT_NUM) | R A
Solar Photovoltaic (PV) | Collector System - Renewable | Corrected Tab name 03/26/2012 |  | Collector System - RENEWABLE |  |  | Not in table | Not in table |  |  |  |  | Model Administration
Solar Photovoltaic (PV) | GENERATOR DETAILS | Corrected Tab name 03/26/2012 |  | Collector System - RENEWABLE |  |  | Not in table | Not in table |  |  |  |  | Model Administration
Solar Photovoltaic (PV) | Resource Name (Unit Code/Mnemonic) |  | Added 05/01/2017 | Collector System - RENEWABLE |  | Automatic | COLLECTOR_SYS | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Model Administration | Lodestar,NMMS |  | N | Y
Solar Photovoltaic (PV) | COLLECTION SYSTEM DETAILED MODEL | Corrected Tab name 03/26/2012 |  | Collector System - RENEWABLE |  |  | Not in table | Not in table |  |  |  |  | Model Administration
Solar Photovoltaic (PV) | Cable Type |  | Added 05/01/2017 | Collector System - RENEWABLE |  |  | COLLECTOR_SYS | CABLE_TYPE | 1) This field is required 2) Data type must string 3) Generate an error if blank | R | String | B,DVB | Model Administration |  |  | N | Y
Solar Photovoltaic (PV) | Voltage Level kV |  | Added 05/01/2017 | Collector System - RENEWABLE |  | kv | COLLECTOR_SYS | VT_LEVEL_KV | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | R | Float | B/DVE | Model Administration |  |  | N | Y
Solar Photovoltaic (PV) | POSITIVE SEQUENCE DATA | Corrected Tab name 03/26/2012 |  | Collector System - RENEWABLE |  |  | Not in table | Not in table |  |  |  |  | Model Administration
Solar Photovoltaic (PV) | R/kft |  | Added 05/01/2017 | Collector System - RENEWABLE |  | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_R_KFT | 1) This field is required 2) Data type must float 3) Generate an error if blank | R | Float | B,DVB | Model Administration |  |  | N | Y
Solar Photovoltaic (PV) | X/kft |  | Added 05/01/2017 | Collector System - RENEWABLE |  | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_X_KFT | 1) This field is required 2) Data type must float 3) Generate an error if blank | R | String | B,DVB | Model Administration |  |  | N | Y
Solar Photovoltaic (PV) | Charging Bc/kft |  | Added 05/01/2017 | Collector System - RENEWABLE |  | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_CHRG_BC_KFT | 1) This field is required 2) Data type must float 3) Generate an error if blank | R | Float | B,DVB | Model Administration |  |  | N | Y
Solar Photovoltaic (PV) | ZERO SEQUENCE DATA |  |  | Collector System - RENEWABLE |  |  | Not in table | Not in table |  |  |  |  | Model Administration
Solar Photovoltaic (PV) | R0/kft |  | Added 05/01/2017 | Collector System - RENEWABLE |  | (p.u. on 100 MVA base) | COLLECTOR_SYS | ZERO_R0_KFT | 1) This field is required 2) Data type must float 3) Generate an errorif blank | R | Float | B,DVB | Model Administration |  |  | N | Y
Solar Photovoltaic (PV) | X0/kft |  | Added 05/01/2017 | Collector System - RENEWABLE |  | (p.u. on 100 MVA base) | COLLECTOR_SYS | ZERO_X0_KFT | 1) This field is required 2) Data type must float 3) Generate an error if blank | R | Float | B,DVB | Model Administration |  |  | N | Y
Solar Photovoltaic (PV) | Collector System-Renew Seg Data | Corrected Tab name 03/26/2012 |  | Collector System-Renew Seg Data |  |  | Not in table | Not in table |  |  |  |  | Model Administration
Solar Photovoltaic (PV) | GENERATOR DETAILS | Corrected Tab name 03/26/2012 |  | Collector System-Renew Seg Data |  |  | Not in table | Not in table |  |  |  |  | Model Administration
Solar Photovoltaic (PV) | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code 05/17/2012 Update #3 validation Added field in form 03/26/2012 |  | Collector System-Renew Seg Data |  | Automatic | CABLE_SEG_DATA | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Model Administration | Lodestar,NMMS |  | N | Y
Solar Photovoltaic (PV) | Cable Type | Corrected Tab name 03/26/2012 |  | Collector System-Renew Seg Data |  |  | Not in table | Not in table |  |  |  |  | Model Administration
Solar Photovoltaic (PV) | Cable Type |  | Added 05/01/2017 | Collector System-Renew Seg Data |  | List | CABLE_SEG_DATA | CABLE_TYPE | 1) This field is required 2) Data type must string 3) Generate an error if blank | R | String | B,DVB | Model Administration |  |  | N | Y
Solar Photovoltaic (PV) | Solar Photovoltaic (PV) SEGAMENT DETAILS | Corrected Tab name 03/26/2012 |  | Collector System-Renew Seg Data |  |  | Not in table | Not in table |  |  |  |  | Model Administration
Solar Photovoltaic (PV) | From |  | Added 05/01/2017 | Collector System-Renew Seg Data |  | alpha/numeric | CABLE_SEG_DATA | CABLE_SEG_DATA_FROM | 1) This field is required 2) Data type must alpha/numeric but may include underscore and dashes, hyphen, slash, and spaces, "¦" and "#" 3) Generate an error if blank | R |  | B,DVB | Model Administration |  |  | N | Y
Solar Photovoltaic (PV) | To |  | Added 05/01/2017 | Collector System-Renew Seg Data |  | alpha/numeric | CABLE_SEG_DATA | CABLE_SEG_DATA_TO | 1) This field is required 2) Data type must alpha/numeric but may include underscore and dashes, hyphen, slash, and spaces, "¦" and "#" 3) Generate an error if blank | R |  | B,DVB | Model Administration |  |  | N | Y
Solar Photovoltaic (PV) | Circuit Number |  | Added 05/01/2017 | Collector System-Renew Seg Data |  | alpha/numeric | CABLE_SEG_DATA | CIRCT_NUM | 1) This field is required 2) Data type must alpha/numeric but may include underscore and dashes, hyphen, slash, and spaces, "¦" and "#" 3) Generate an error if blank | R |  | B,DVB | Model Administration |  |  | N | Y
Solar Photovoltaic (PV) | Voltage Level |  | Added 05/01/2017 | Collector System-Renew Seg Data |  | kV | CABLE_SEG_DATA | VT_LEVL | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69,138, 230 or 345 3) The value must be > 0. | R | Float | B/DVE | Model Administration |  |  | N | Y
Solar Photovoltaic (PV) | Cable Segment Length |  | Added 05/01/2017 | Collector System-Renew Seg Data |  | in kft | CABLE_SEG_DATA | CABLE_SEG_LENTH | 1) This field is required 2) Data type must float 3) Generate an error if blank | R | Float | B,DVB | Model Administration |  |  | N | Y
Solar Photovoltaic (PV) | Number of Turbines on cable segment |  | Added 05/01/2017 | Collector System-Renew Seg Data |  | Integer | CABLE_SEG_DATA | NUM_TURBIN_ON_CABLE_SEG | 1) This field is required 2) Data type must integer 3) Generate an error if blank | R | Integer | B,DVB | Model Administration |  |  | N | Y
Solar Photovoltaic (PV) | UNIT_CABLE_FROM_TO_CIRCUIT Hidden Field on Form |  | Added 05/01/2017 | Collector System-Renew Seg Data |  | Automatic | CABLE_SEG_DATA | UNIT_CABLE_FROM_TO_CIRCUIT | Concantenate (Unit_Code_CABLE_TYPE_CABLE_SEG_DATA_FROM_CABLE_SEG_DATA_TO_CIRCT_NUM) | R A
Transmission | Line Data | Corrected Tab name 03/26/2012 |  | Line Data |  | Not in table | Not in table | Not in table
Transmission | DESCRIPTION OF CHANGE |  |  | Line Data |  | List | LINE | CHANGE_DESCRIPTION | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T R | Alpha | B | Joel Koepke |  |  | N | N
Transmission | LINE (ANY LENGTH) DETAILS |  |  | Line Data |  |  | Not in table | Not in table
Transmission | Line Name |  |  | Line Data |  | enter all caps | LINE | ERCOT_LINE_NAME | 1) This field is required 2) This field may not have any special characters, except an underscore "_" and a dash "-" 3) Warn if > 14 characters. Warning! ERCOT Line Name () should not be > 14 characters long or the name will be truncated in the model which requires uniqueness. 4) Line Name can not be duplicated in a Station | T R | Alpha | B | Joel Koepke |  |  | N | N
Transmission | Line Voltage Level |  | Updated: 1/2016 | Line Data |  | kV | LINE | LINE_VOLT_LVL | 1) This field is required. 2) If the value >= 69kv it must be 69, 230,138, or 345 3) The value must be < 345 4) The value must be > 1 | T R | Float | B/DVE | Joel Koepke |  |  | N | Y
Transmission | Resistance in P.U. (100 MVA Base) |  |  | Line Data |  | p.u. | LINE | RESISTANCE+C1333B1333:I1333A1333:I1333 | 1) Field is required If value is less than 0.00001 then Warning! Resistance should be more than 0.00001 or set to be 0.0 (zero-impedance line) 2) If Line Data - Line Voltage Level = 69kV, value must be <= 1.5 If Line Data - Line Voltage Level = 138kV or higher kV, value must be <= 0.5 WARN if value is outside of these conditions 4) Zero Impedance Lines/Series Compensators cannot exist in parallel with other zero-impedance paths due to a system limitation. 5) If Zero Impedance Lines/SeriesCompensator, produce a warning if line ratings are entered as => 99999. If Zero Impedance Lines are between two substations, produce a warning if line ratings are entered as 9999. Warning! Invalid MVA Rating | T R | Float | B | Joel Koepke |  |  | N | Y
Transmission | Reactance in P.U. (100 MVA Base) |  |  | Line Data |  | p.u. | LINE | REACTANCE | 1) Field is required If value is < 0.0001 and Internal Line = 'Y' then Warning! Reactance should be less than 0.0001 If value is < 0.0001 and Internal Line = 'N' then Warning! Reactance should be less than 0.0001 If Line Data - Line Voltage Level = 69kV, value must be <=1.0 If Line Data - Line Voltage Level = 138kV, value must be <=0.1 If Line Data - Line Voltage Level = 345kV, value must be <=.05 WARN if value is outside of these conditions 3)Error if Reactance value is > 1. Error! Reactance (value) > 1.0. Reactance should be expressed in terms of per unit (e.g. not percentage). 4) If the Zero Impedance Lines are contained within a single substation, then they should be removed from the Line tab and the updated connections should be shown in the Breaker/Switch tab. "ERROR! Internal zero impedance lines should be modeled on the breaker/switch tab" | T R | Float | B | Joel Koepke |  |  | N | Y
Transmission | Charging Susceptance in PU (100 MVA Base) |  |  | Line Data |  | p.u. | LINE | CHARGING_SUSC | 1) Field is required 2) Value must be >= 0 If Line Data - Line Voltage Level = 69kV, value must be >=.00001<=0.3 If Line Data - Line Voltage Level = 138kV, value must be >=.00001<=0.5 If Line Data - Line Voltage Level = 345kV, value must be >=.00001<=2.2. Generate a Warning if Rule fails 3) If the Zero Impedance Lines are contained within a single substation, then they should be removed from the Line tab and the updated connections should be shown in the Breaker/Switch tab. ERROR! Internal zero impedance lines should be modeled on the breaker/switch tab. | T R | Float | B | Joel Koepke |  |  | N | Y
Transmission | Zero Sequence Line Resistance In P.u. (100mva Base) | 10/08/2012 Validation rule Change CR 46762 | ADDED 06/27/2012 | Line Data | Line_Information.View | p.u. | LINE | ZERO_SEQ_LINE_RESISTANCE_PU | 1) This field is required and Data type is numeric 2) Generate a Warning if the per unit value entered is not >= 0.0 and <= 100.0 | R | [5 empty] | N | Y
Transmission | Zero Sequence Line Reactance In P.u. (100mva Base) | 10/08/2012 Validation rule Change CR 46762 | ADDED 06/27/2012 | Line Data | Line_Information.View | p.u. | LINE | ZERO_SEQ_LINE_REACTANCE_PU | 1) This field is required and Data type is numeric 2) Generate a Warning if the per unit value entered is not >= 0.0 and <= 100.0 | R | [5 empty] | N | Y
Transmission | Zero Sequence Charging Susceptance In P.u. (100mva Base) | 10/08/2012 Validation rule Change CR 46762 3/8/2012 | ADDED 06/27/2012 | Line Data | Line_Information.View | p.u. | LINE | ZERO_ SEQ_ CHRG_ SUSECPTANCE_PU | 1) This field is required and Data type is numeric 2) Generate a Warning if the per unit value entered is not >= 0.0 and <= 100.0 | R | [5 empty] | N | Y
Transmission | DC Resistance |  | Added 05/01/2017 | Line Data |  | Ohms/Phase | LINE | DC_RES | 1) This field is required and Data type is numeric 2) Generate an Error if the value entered is not >= 0.0 and <= [Resistance in P.U. (100 MVA Base)] * {[Line Voltage Level] ^2} / 100 | R | [7 empty] | R | R
Transmission | Type (overhead / underground) | Removed Validation #3 per planing group. |  | Line Data |  | List | LINE | TYPE | 1) Field is required 2) Value must be at from the following list: OVERHEAD, UNDERGROUND, BOTH | T R | Alpha | B | Joel Koepke |  |  | N | N
Transmission | Segment Length |  |  | Line Data |  | miles | LINE | SEGMENT_LENGTH | 1) Field is required 2) Value must > 0 3) Formula on Line Data - Segment Length: The formula to determine the length of a line based on the Reactance (X) and the Charging Susceptance (Chg) is 486 * SQRT(X_pu * Chg_pu). Generate a Warning when Segment length is not within the 25% variation of the calculated value. 4) Update the Warning message to include the text " This is applicable for Overhead lines only" | T R | Float | B | Joel Koepke |  |  | N | Y
Transmission | TO STATION |  |  | Line Data |  |  | Not in table | Not in table
Transmission | EROCT STATION TO - Station Code Mnemonic |  |  | Line Data |  | enter all caps | LINE | ERCOT_CODE_TO | 1) This field is Optional 2) Warn if left blank 3) This field must match ERCOT records (unless new) .Substation Code invalid message should be warning only if the PUN flag is 'yes'. 4.If the Internal Line Flag is 'Y', then the TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic can be same. If the internal Line Flag is 'N', TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic should be distinct . Error message should be "'Error! TO and FROM Station Code ( ) should not be duplicated if Internal Line Flag = "N". 5) If the internal Line Flag is 'N', ,FROM Station Code Mnemonic cannot be listed as a TO Station Code Mnemonic on any other lines. The Warning would occur on the secondary side (eg: they had DIESEL on the FROM station on the first line, and DIESEL on the TO Station on the second line then the TO station would produce the Warning) or (eg: DIESEL is on the TO station on the 3rd line and DIESEL on the FROM station on the 4th line then the FROM station would produce the Warning). | T R | Alpha | B/DVE | Joel Koepke |  |  | N | N
Transmission | Internal Line |  |  | Line Data |  | Y/N | LINE | INTERNAL_LINE_TO_FLG | 1) This field is required 2) Value must be of the following: 'Y', 'N' | T C | Alpha | B |  |  |  | N | Y
Transmission | TSP Name |  |  | Line Data |  | List | LINE | TSPNAME_TO | 1) This field is conditionally required if TO STATION - Internal Line - 'N' 2) This field must match ERCOT records (drop down in RARF) | T C | Alpha | B/DVE | Joel Koepke |  |  | N | N
Transmission | Connected Device 1 thru 10 |  |  | Line Data |  | enter all caps | LINE_DEVICES | DEVICE_NAME | 1) This field is required 2) May not be >= than 17 characters. Warning! Device Name () should not be > 17 characters long or the name will be truncated in the model which requires uniqueness. 3) May not have duplicates within the TO or FROM Station 4) May not contain special characters except for an underscore "_" and a dash "-" | T R/C | Alpha | B/DVE | Joel Koepke |  |  | N | N
Transmission | Bus Number (PTI Bus Number) | 06/14/2012 Updated Validation #2 to increase to 999,999 |  | Line Data |  | # | LINE | BUS_NUM_TO | 1) This field is optional 2) This field must be between 1 - 999,999 | T O | Integer | B/DVE | Joel Koepke |  |  | N | N
Transmission | Weather Zone / Weather Station (used for Dynamic Ratings) |  |  | Line Data |  | List | LINE | WEATHERZONE_TO | 1) This field is conditionally required if "Line Rating (Static or Dynamic)" = 'DYNAMIC' 2) Value must be from the following list: COAST, EAST, FAR_WEST, NORTH, NORTH_C, SOUTH_C, SOUTHERN, WEST, KABI, KAUS, KBRO, KCRP, KDFW, KGLS, KIAH, KJCT, KLRD, KLFK, KMAF, KMWL, KSJT, KSAT, KTYR, KVCT, KACT, KSPS, KINK, KPRX | T C | Alpha | B/DVE | Joel Koepke |  |  | N | N
Transmission | FROM Station |  |  | Line Data |  |  | Not in table | Not in table
Transmission | ERCOT FROM Station Code Mnemonic |  |  | Line Data |  | enter all caps | LINE | ERCOT_CODE_FROM | 1) This field is required 2) Must match ERCOT records (unless new) 3) Value must be <= 8 characters .Warning! Station Code () should not be > 8 characters long or the name will be truncated in the model which requires uniqueness. 4. If the Internal Line Flag is 'Y', then the TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic can be same. If the internal Line Flag is 'N', TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic should be distinct. Error message should be "'Error! TO and FROM Station Code ( ) should not be duplicated if Internal Line Flag = "N". 5) If the internal Line Flag is 'N', ,FROM Station Code Mnemonic cannot be listed as a TO Station Code Mnemonic on any other lines. The Warning would occur on the secondary side (eg: they had DIESEL on the FROM station on the first line, and DIESEL on the TO Station on the second line then the TO station would produce the Warning) or (eg: DIESEL is on the TO station on the 3rd line and DIESEL on the FROM station on the 4th line then the FROM station would produce the Warning). | T R | Alpha | B/DVE |  |  |  | N | N
Transmission | Connected Device 1 thru 10 |  |  | Line Data |  | enter all caps | LINE_DEVICES | DEVICE_NAME | 1) This field is required 2) May not have duplicates within the TO or FROM Station 3) May not contain special characters except for an underscore "_" and a dash "-" 4) May not be > than 17 characters. Warning! Device Name () should not be > 17 characters long or the name will be truncated in the model which requires uniqueness. | T R/C | Alpha | B/DVE | Joel Koepke |  |  | N | N
Transmission | Bus Number (PTI Bus Number) | 06/14/2012 Updated Validation #2 to increase to 999,999 |  | Line Data |  | integer | LINE | BUSNUMBR_FROM | 1) This field is optional 2) This field must be between 1 - 999,999 3) Warn if left blank | T R | Integer | B/DVE | Joel Koepke |  |  | N | N
Transmission | Weather Zone / Weather Station (used for Dynamic Ratings) |  |  | Line Data |  | # | LINE | WEATHERZONE_FROM | 1) This field is conditionally required if "Line Rating (Static or Dynamic)" = 'DYNAMIC' 2) Value must be from the following list: COAST, EAST, FAR_WEST, NORTH, NORTH_C, SOUTH_C, SOUTHERN, WEST, KABI, KAUS, KBRO, KCRP, KDFW, KGLS, KIAH, KJCT, KLRD, KLFK, KMAF, KMWL, KSJT, KSAT, KTYR, KVCT, KACT, KSPS, KINK, KPRX | T C | Alpha | B/DVE | Joel Koepke |  |  | N | N
Transmission | Line Code |  |  | Line Data |  | List Automatic | LINE | LINE_CODE | Concantenate (Site Code_Substation Code_ERCOT_LINE_NAME) | R A | [5 empty] | N | N
Transmission | COMMENTS |  |  | Line Data |  |  | LINE | COMMENTS_LINE | [7 empty] | N | N
Transmission | EFFECTIVE DATE: |  |  | Line Data |  | mm/dd/yyyy | LINE | EFF_DATE | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T R | Date | B/DVB | Scott/Woody/Angie |  |  | N | N
Transmission | Line Temperture |  |  | Line Temperture |  |  | Not in table | Not in table
Transmission | DESCRIPTION OF CHANGE | Added 03/26/2012 | ADDED 06/27/2012 | Line Temperture | Line_TempDetails.View | List | LINE_TEMP | CHANGE_DESCRIPTION | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T C | Alpha | B | Joel Koepke |  |  | N | N
Transmission | Line Name |  |  | Line Temperture |  | Automatic | LINE_TEMP | ERCOT_LINE_NAME | 1) This field is required 2) This field may not have any special characters, except an underscore "_" and a dash "-" 3) Warn if > 14 characters. Warning! ERCOT Line Name () should not be > 14 characters long or the name will be truncated in the model which requires uniqueness. 4) Line Name can not be duplicated in a Station | A | Character |  |  |  |  | N | Y
Transmission | Line Code | 06/13/2012 This field seems to be mapped incorrectly. The Line name field is populating this field. |  | Line Temperture |  | Automatic | LINE_TEMP | LINE_CODE | Concantenate (Site Code_Substation Code_ERCOT_LINE_NAME) | A | Character |  |  |  |  | N | N
Transmission | Line Rating |  |  | Line Temperture |  | Static or Dynamic | LINE_TEMP | LINE_RATING | 1) Field is required 2) Field must be from the following list: STATIC, DYNAMIC | T R | Alpha | B | Joel Koepke |  |  | N | N
Transmission | Nominal |  |  | Line Temperture |  |  | Not in table | Not in table
Transmission | Continuous Rating |  |  | Line Temperture |  | MVA | LINE | CONTINUOUS_RTG | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be <= Nominal (Static) - 2-hr Emergency Rating 3) Value must be <= Nominal (Static) - 15-min Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - Continuous Rating AND value must be >= 115 °F Continuous Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T R | Integer | B/DVE | Joel Koepke |  |  | N | Y
Transmission | 2-hr Emergency Rating |  |  | Line Temperture |  | MVA | LINE | EMGCY_RTG_2HR | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be >= Nominal (Static) - Continuous Rating 3) Value must be <= Nominal (Static) - 15-min Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 2-hr Emergency Rating AND value must be >= 115 °F 2-hr Emergency Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T R | Integer | B/DVE | Joel Koepke |  |  | N | Y
Transmission | 15-min Rating |  |  | Line Temperture |  | MVA | LINE | RTG_15MIN | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be >= Nominal (Static) - Continuous Rating 3) Value must be >= Nominal (Static) - 2-hr Emergency Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 15-min Rating AND value must be >= 115 °F 15-min Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T R | Integer | B/DVE | Joel Koepke |  |  | N | Y
Transmission | Conductor 2-hour Rating | 05/03/2012 Add new field to Line Table also needs to be mapped. Field already existed in form. 03/09/2012 Updated Validation | ADDED 06/27/2012 | Line Temperture | Line_TempDetails.View | MVA | LINE | PLANNING_RATE_C | This field is required Numeric value Must be >= Nominal Emergency Rating (2HR Rating) | R | Model Adminstration |  |  |  |  | N | Y
Transmission | Relay loadability limit |  | Added 05/01/2017 | Line Temperture |  | MVA | LINE | RELAY_LOAD_LMT | 1) This field is required regardless of STATIC or DYNAMIC 2) Generate a Warning if Value < 15-Minute Rating | T R | [7 empty] | R | R
Transmission | Line Temperture |  |  | Line Temperture |  |  | Not in table | Not in table | Degree of Temperature
Transmission | 20 °F - Continuous Rating - 115 °F Continuous Rating |  |  | Line Temperture |  | MVA | LINE_TEMP | CONTINUOUS_RTG | 1) These field are conditionally required. If Line Rating (Static or Dynamic) = Dynamic this field is required 2) Line Rating (Static or Dynamic) = Static, this field must be blank 3) If required, these values must be <= the subsequent dynamic rating. For example: 20 °F - Continuous Rating >= 25 °F - Continuous Rating 25 °F - Continuous Rating >= 30 °F - Continuous Rating 4) If required, within each temp rating, the following must apply Continuous Rating <= 2-hr Emergency Rating <= 15-min rating | T C | Integer | B/DVE | Joel Koepke |  |  | N | N
Transmission | 20 °F - 2-hr Emergency Rating - 115 °F 2-hr Emergency Rating |  |  | Line Temperture |  | MVA | LINE_TEMP | EMGCY_RTG_2HR | 1) These field are conditionally required. If Line Rating (Static or Dynamic) = Dynamic this field is required 2) Line Rating (Static or Dynamic) = Static, this field must be blank 3) If required, these values must be >= the subsequent dynamic rating. For example: 20 °F - 2-hr Emergency Rating >= 25 °F - 2-hr Emergency Rating 25 °F - 2-hr Emergency Rating >= 30 °F - 2-hr Emergency Rating 4) If required, within each temp rating, the following must apply Continuous Rating <= 2-hr Emergency Rating <= 15-min rating | T C | Integer | B/DVE | Joel Koepke |  |  | N | N
Transmission | 20 °F - 15-min Rating - 115 °F 15-min Rating |  |  | Line Temperture |  | MVA | LINE_TEMP | RTG_15MIN | 1) These field are conditionally required. If Line Rating (Static or Dynamic) = Dynamic this field is required 2) Line Rating (Static or Dynamic) = Static, this field must be blank 3) If required, these values must be >= the subsequent dynamic rating. For example: 20 °F - 2-hr 15-min Rating >= 25 °F - 15-min Rating 25 °F - 2-hr 15-min Rating >= 30 °F - 15-min Rating 4) If required, within each temp rating, the following must apply Continuous Rating <= 2-hr Emergency Rating <= 15-min rating | T C | Integer | B/DVE | Joel Koepke |  |  | N | N
Transmission | 20 °F - Planning Rate C - 115 °F - Planning Rate C | 05/03/2012 Updated validation rule 03/09/2012 Updated Validation | ADDED 06/27/2012 | Line Temperture | Line_TempDetails.View | MVA | LINE_TEMP | PLANNING_RATE_C | 1)Numeric value 2) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be >=Tempature Emergency Rating (2HR Rating) else (if Line Rating (Static or Dynamic) = Static, this field must be blank). | T C | Float |  | Planning Team |  |  | N | N
Transmission | SUBSTATION DETAILS |  |  | Substation Data |  |  | Not in table | Not in table
Transmission | SUBSTATION DETAILS |  |  | Substation Data |  |  | Not in table | Not in table |  |  |  |  | Model Administration
Transmission | SubStation Code |  | Added 05/01/2017 | Substation Data |  | Automatic | Substation | SUBSTATION_CODE | 1) This field is required 2) Must match ERCOT records. Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters 5) substation code should be in Upper case letters. Generate an error if the rule fails | T R | Character
Transmission | Station Long Name |  | Added 05/01/2017 | Substation Data |  | All Caps | Substation | STATION_LNG_NAME | 1) This field is required 2) substation code should be in Upper case letters. Generate an error if the rule fails | T R
Transmission | Voltage Level |  | Added 05/01/2017 | Substation Data |  | List | Substation | VT_LEVL | 1) This field is required 2) Must be from this list <60, 69 ,138 or 345 NOTE: If RARF validation rule is not possible, then check will occur in Network Modeling review: Each Transmission Voltage Level (> 60kV) listed on other tabs (equipment) must have a row per Voltage Level here of Normal & Emergency Voltage Limit Sets. | T R
Transmission | SubStation Code |  | Added 05/01/2017 | Substation Data |  | Automatic | Substation | STATION_CODE | This field is a concatenation of Sitecode_Substation_CODE_VT_LEVL. | T R | Character
Transmission | Station Grounding Resistance |  | Added 05/01/2017 | Substation Data |  | Ohms | Substation | SUB_GRD_RES | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if < 0.0 or >15.0 | T R
Transmission | Latitude of Center of Station |  | Added 05/01/2017 | Substation Data |  | decimal degrees (N) | Substation | LAT_CENTER_PLT | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if Latitude < 25.0 or > 37.0. | T R
Transmission | Longitude of Center of Station |  | Added 05/01/2017 | Substation Data |  | decimal degrees (W) | Substation | LONG_CENTER_PLT | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if <93 or > 107 . | T R
Transmission | Normal Voltage Limit - Max p.u. above 60 kV |  | Added 05/01/2017 | Substation Data |  | p.u. | Substation | NOMINAL_MAX | 1) This field is required 2) Generate an Error if blank and [voltage] <> "<60 kV". 3)Generate Warning if <0.8 or > 1.2 | T R
Transmission | Normal Voltage Limit - Min. p.u. Base above 60 kV |  | Added 05/01/2017 | Substation Data |  | p.u. | Substation | NOMINAL_MIN | 1) This field is required 2) Generate an Error if blank and [voltage] <> "<60 kV" 3)Generate Warning if <0.8 or > 1.2 | T R
Transmission | EmergencyVoltage Limit - Max p.u. above 60 kV |  | Added 05/01/2017 | Substation Data |  | p.u. | Substation | EMERGENCY_VLT_LMT_MAX | 1) This field is required 2) Generate an Error if blank and [voltage] <> "<60 kV" 3)Generate Warning if <0.8 or > 1.2 | T R
Transmission | Emergency Voltage Limit - Min. p.u. Base above 60 kV |  | Added 05/01/2017 | Substation Data |  | p.u. | Substation | EMERGENCY_VLT_LMT_MIN | 1) This field is required 2) Generate an Error if blank and [voltage] <> "<60 kV" 3)Generate Warning if <0.8 or > 1.2 | T R
Transmission | MOST LIMITING SERIES ELEMENT |  |  | Most Limiting Series Element |  |  | Not in table | Not in table
Transmission | MOST LIMITING SERIES ELEMENT DATA |  |  | Most Limiting Series Element |  |  | Not in table | Not in table
Transmission | Most Limiting Series Element Device |  | Added 05/01/2017 | Most Limiting Series Element |  | All Caps | MST_LMT_SERS_ELMT | DEVICE_NAME | NOTE: If RARF validation rule is not possible, then check will occur in Network Modeling review: Each Transmission Voltage Level (> 60kV) listed on other tabs (equipment) must have a row per Resource-owned Line modeled and Resource-owned transmission-level breaker/switch controlling non-Resource-owned Line. 2) Warn if > 29 characters. Warning! ERCOT MLSE Name () should not be > 29 characters long or the name will be truncated in the model which requires uniqueness. | T R | [6 empty] | R | R | R
Transmission | Device restricted by the MLSE |  | Added 05/01/2017 | Most Limiting Series Element |  | All Caps | MST_LMT_SERS_ELMT | DEV_REST_MLSE | NOTE: If RARF validation rule is not possible, then check will occur in Network Modeling review: Each Transmission Voltage Level (> 60kV) Resource-owned Line modeled must have a MLSE assigned or alternatively a Resource's MLSE may be assigned to a referenced TSP-owned Line. 2) This field may not have any special characters, except an underscore "_" and a dash "-" 3) Warn if > 14 characters. Warning! ERCOT Line Name () should not be > 14 characters long or the name will be truncated in the model which requires uniqueness. 4) Line Name can not be duplicated in MLSE entries | T R | [6 empty] | R | R | R
Transmission | MLSE Code |  | Added 05/01/2017 | Most Limiting Series Element |  | Automatic | MST_LMT_SERS_ELMT | MLSE_CODE | StationName_{MLSE}Device_Name | T R | Character | [5 empty] | R | R | R |  | Glossary has this field as"R", but it should be "A"
Transmission | 2-hr Emergency Rating |  | Added 05/01/2017 | Most Limiting Series Element |  | MVA | MST_LMT_SERS_ELMT | EMGCY_RTG_2HR | 1) Value must be >= MLSE's Normal Rating 2) Value must be <= MLSE's 15-min Rating | T R | [6 empty] | R | R | R
Transmission | 15-min Rating |  | Added 05/01/2017 | Most Limiting Series Element |  | MVA | MST_LMT_SERS_ELMT | RTG_15MIN | 1) Value must be >= MLSE's Normal Rating 2) Value must be >= MLSE's 2-hr Emergency Rating | T R | [6 empty] | R | R | R
Transmission | Normal Rating |  | Added 05/01/2017 | Most Limiting Series Element |  | MVA | MST_LMT_SERS_ELMT | NORMAL_RTG | RARF format Note: This MVA rating to be listed prior to 2-hr Emergency Rating 1) Value must be <= MLSE's 2-hr Emergency Rating 2) Value must be <= MLSE's 15-min Rating | T R | [6 empty] | R | R | R
Transmission | Breaker_Switch Data |  |  | Breaker Switch Data |  |  | Not in table | Not in table
Transmission | DESCRIPTION OF CHANGE |  |  | Breaker Switch Data |  | List | BREAKER_SWITCH | CHANGE_DESCRIPTION | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T C | Alpha | B | Joel Koepke |  |  | N | N
Transmission | BREAKER / SWITCH |  |  | Breaker Switch Data |  |  | Not in table | Not in table
Transmission | Switch Name |  |  | Breaker Switch Data |  | enter all caps | BREAKER_SWITCH | SWITCH_NAME | 1) This field is required 2) Value may contain no special characters except an underscore "_" and a dash "-" 3) Must be <=14 characters. Warning! Switch Name () should not be >14 characters long or the name will be truncated in the model which requires uniqueness. 4) Switch Name can not be duplicated in a station | T R | Alpha | B | Joel Koepke |  |  | N | N
Transmission | ERCOT Station Code Mnemonic |  |  | Breaker Switch Data |  | enter all caps | BREAKER_SWITCH | SUBSTATION_CODE | 1) This field is required 2) Must match ERCOT records (unless new). Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters. Warning! Station Code () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) substation code should be in Upper case letters. Generate an error if the rule fails | T R | Alpha | B | Joel Koepke |  |  | N | N
Transmission | Switch Code |  | UPDATED 03/2012 | Breaker Switch Data |  | Automatic | BREAKER_SWITCH | BREAKER_CODE | Concantenate (Site Code_Substation Code_Switch Name) | A | Character |  |  |  |  | N | N
Transmission | Is this a Fault Isolating Device (e.g. Circuit Breaker) |  |  | Breaker Switch Data |  | Y/N | BREAKER_SWITCH | FAULT_ISO_DEV_FLG | 1) This is a required field 2) Values must from the following list: 'Y', 'N' | T R | Alpha | B | Joel Koepke |  |  | N | Y
Transmission | Normal Operating Status (when in-service) |  |  | Breaker Switch Data |  | Oper/Closed | BREAKER_SWITCH | NORM_OP_STATUS | 1) This field is required 2) Value must be from the following list: 'OPEN', 'CLOSED' 3) Generate a warning when the Normal Operating Status is 'OPEN' | T R | Alpha | B | Joel Koepke |  |  | N | Y
Transmission | Voltage Level |  | Updated: 1/2016 | Breaker Switch Data |  | kV | BREAKER_SWITCH | VOLT_LVL | 1) This field is required. 2) If the value >= 69kv it must be 69, 138, 230 or 345 3) The value may not exceed 345 4) The value must be > 0 | T R | Float | B/DVE | Joel Koepke |  |  | N | Y
Transmission | Static Ratings for Planning |  |  | Breaker Switch Data |  |  | Not in table | Not in table
Transmission | Continuous Rating | 10/30/2012 change all errors to warnings | ADDED 06/27/2012 | Breaker Switch Data | Breaker_Switch.View | MVA | BREAKER_SWITCH | CONTINUOUS_RTG | 1) Value must be <= Nominal (Static) - 2-hr Emergency Rating 2) Value must be <= Nominal (Static) - 15-min Rating 3) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - Continuous Rating AND value must be >= 115 °F Continuous Rating 4) Produce an warning when invalid MVA ratings are entered as 9999. WARNING! Invalid MVA Rating between substations. | T R | Integer | B/DVE | Planning Team |  |  | N | Y
Transmission | 2-hr Emergency Rating | 10/30/2012 change all errors to warnings | ADDED 06/27/2012 | Breaker Switch Data | Breaker_Switch.View | MVA | BREAKER_SWITCH | EMGCY_RTG_2HR | 1) Value must be >= Nominal (Static) - Continuous Rating 2) Value must be <= Nominal (Static) - 15-min Rating 3) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 2-hr Emergency Rating AND value must be >= 115 °F 2-hr Emergency Rating 4) Produce an warning when invalid MVA ratings are entered as 9999. WARNING! Invalid MVA Rating between substations. | T R | Integer | B/DVE | Planning Team |  |  | N | Y
Transmission | 15 Min Rating | 10/30/2012 change all errors to warnings | ADDED 06/27/2012 | Breaker Switch Data | Breaker_Switch.View | MVA | BREAKER_SWITCH | RTG_15MIN | 1) Value must be >= Nominal (Static) - Continuous Rating 2) Value must be >= Nominal (Static) - 2-hr Emergency Rating 3) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 15-min Rating AND value must be >= 115 °F 15-min Rating 4) Produce an Warning when invalid MVA ratings are entered as 9999. WARNING! Invalid MVA Rating between substations. | T R | Integer | B/DVE | Planning Team |  |  | N | Y
Transmission | Side 1 / Side 2 - Directly connected device name(s) |  |  | Breaker Switch Data |  | enter all caps | BREAKER_SWITCH_SIDE | DEVICE_NAME | 1) This field is required 2) Value may contain no special characters except an underscore "_" and a dash "-" 3) Must be <=17 characters. Must be <=17 characters. Warning! Device Names () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. 4) At least one connected device is required on each side of the Breaker/Switch. Generate an error if at least one connected device is missing on both sides Generate a Warning when at least one connected device is missing on any one side. | T R/C | Alpha | B | Joel Koepke |  |  | N | N
Transmission | COMMENTS |  |  | Breaker Switch Data |  |  | BREAKER_SWITCH | COMMENTS_BRKSWITCH |  | O | [5 empty] | N | N
Transmission | EFFECTIVE DATE: |  |  | Breaker Switch Data |  | mm/dd/yyyy | BREAKER_SWITCH | EFF_DATE | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T R | Date | Scott/Woody/Angie |  |  |  | N | N
Transmission | Capacitor or Reactor Data |  |  | Capacitor and Reactor Data |  |  | Not in table | Not in table
Transmission | DESCRIPTION OF CHANGE |  |  | Capacitor and Reactor Data |  | List | CAPREACT | CHANGE_DESCRIPTION | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T C | Alpha | B | Joel Koepke |  |  | N | N
Transmission | Capacitor or Reactor |  |  | Capacitor and Reactor Data |  | List | CAPREACT | CAPACITOR_REACTOR_FLG | 1) This field is required 2) Value must be from the following list: 'C', 'R' | T R | Alpha | B | Joel Koepke |  |  | N | Y
Transmission | Device Name | 11/27/2012 Removed Validation #4 |  | Capacitor and Reactor Data |  | enter all caps | CAPREACT | DEVICE_NAME | 1) This field is required 2) Value may contain no special characters except an underscore "_" and a dash "-" 3) Must be <=14 characters. Warning! Device Name () should not be >14 characters long or the name will be truncated in the model which requires uniqueness. 4) Device Name can not be duplicated in a Station | T R | Alpha | B | Joel Koepke |  |  | N | N
Transmission | ERCOT Station Code Mnemonic |  | UPDATED 03/2012 | Capacitor and Reactor Data |  | enter all caps | CAPREACT | SUBSTATION_CODE | 1) This field is required 2) Must match ERCOT records (unless new).Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3)This field may not have any special characters, except an underscore "_" and a dash "-" 4) Value must be <= 8 characters. Warning! Station Code () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) substation code should be in Upper case letters. Generate an error if the rule fails | T R | Alpha | B | Joel Koepke |  |  | N | N
Transmission | Device Code |  | UPDATED 03/2012 | Capacitor and Reactor Data |  | Automatic | CAPREACT | DEVICE_CODE | Concantenate (Site Code_Substation Code_Device Code) | A | Character |  |  |  |  | N | N
Transmission | Capacitor or Reactor |  |  | Capacitor and Reactor Data |  | List | CAPREACT | CAPACITOR_REACTOR_FLG | 1) This field is required 2) Value must be from the following list: 'C', 'R' | T R | Alpha | B | Joel Koepke |  |  | N | Y
Transmission | Nominal MvAR |  |  | Capacitor and Reactor Data |  | MVAR | CAPREACT | NOMINAL_MVAR | 1) This field is required 2) If the Capacitor or Reactor field is 'C' , the value should be > 0 , if it is 'R', value should be < 0 | T R | Float | B | Joel Koepke |  |  | N | Y
Transmission | Voltage Level Kv |  | Updated: 1/2016 | Capacitor and Reactor Data |  | kV | CAPREACT | VOLT_LVL_KV | 1) This field is required. 2) If the value >= 69kv it must be 69, 138, 230 or 345 3) The value may not exceed 345 4) The value must be > 0 | T R | Float | B/DVE | Joel Koepke |  |  | N | Y
Transmission | Coil DC resistance |  | Added 05/01/2017 | Capacitor and Reactor Data |  | Ohms/Phase | CAPREACT | DC_RES | 1) This field is required and Data type is numeric 2) If not “99999”, then value entered must be > 0 and <= 25.0 | T R | [7 empty] | R | R
Transmission | Grounding DC resistance |  | Added 05/01/2017 | Capacitor and Reactor Data |  | Ohms | CAPREACT | GRD_DC_RES | 1) This field is required and Data type is numeric 2) If not “99999”, then value entered must be >= 0 and <= 0.5 | T R | [7 empty] | R | R
Transmission | Bus Number (PTI Bus Number) | 06/14/2012 Updated Validation #2 to increase to 999,999 |  | Capacitor and Reactor Data |  | # | CAPREACT | PTI_BUSNUM | 1) This field is optional 2) This field must be between 1 - 999,999 | T O | Float | B | Joel Koepke |  |  | N | N
Transmission | Automatic Voltage Regulation |  |  | Capacitor and Reactor Data |  | Y/N | CAPREACT | AUTO_VOLT_FLG | 1) This field is required 2) Value must be from the following list: 'Y', 'N' | T R | Alpha | B | Joel Koepke |  |  | N | Y
Transmission | Voltage Level of Busbar being regulated |  | Updated: 1/2016 | Capacitor and Reactor Data |  | kV | CAPREACT | BUSBAR_VOLT | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) If the value >= 69kv it must be 69,138, 230 or 345 3) The value may not exceed 345 4) The value must be > 0 | T C | Float | B/DVE | Joel Koepke |  |  | N | Y
Transmission | Desired Regulating voltage |  |  | Capacitor and Reactor Data |  | kV | CAPREACT | DES_REG_VOLT | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) The value may not exceed 345. (REMOVED) 3) The value must be > 0 4) The value must >= Minimum Regulating Voltage 5) The value must <=Maximum Regulating Voltage 6) Value should be within the range of 10% of the base kV..anything beyond should be a Warning. | T C | Float | B/DVE | Joel Koepke |  |  | N | Y
Transmission | Minimum Regulating Voltage |  |  | Capacitor and Reactor Data |  | kv | CAPREACT | MIN_REG_VOLT | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) The value may not exceed 345(REMOVED) 3) The value must be > 0 4) The value must be <= Maximum Regulating Voltage 5) Warning if value exceeds 50% from Maximum Regulating Voltage 6) Value should be within the range of 10% of the base kV..anything beyond should be a Warning. | T C | Float | B/DVE | Joel Koepke |  |  | N | Y
Transmission | Maximum Regulating Voltage |  |  | Capacitor and Reactor Data |  | kv | CAPREACT | MAX_REG_VOLT | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 3) The value must be > 0 4) The value must be >= Minimum Regulating Voltage 5) Warning if value exceeds 50% from Minimum Regulating Voltage 6) Value should be within the range of 10% of the base kV..anything beyond should be a Warning. | T C | Float | B/DVE | Joel Koepke |  |  | N | Y
Transmission | Device Name(s) - that this reactive device is directly connected to | 11/27/2012 Removed Validation #4 |  | Capacitor and Reactor Data |  | enter all caps | CAPREACT_DEVICE | CONNECTED_DEVICE_NAME | 1) This field is optional 2) May not contain special characters except for an underscore "_" and a dash "-" 3) ) May not be > than 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. 4)This field should be unique. Every Device entry needs to have a unique “Device Name(s) – that this reactive device is directly connected to". No two capacitors should have the same controlling breaker or switch. 4) 'Connected Device in Capacitor Reactor should have a Controlling Breaker/Switch in Breaker/switch Tab. Audit report should generate an error if the rule fails. For all other equipment that is not a Capacitor/Reactor, they can have connectivity references to transformers, lines, etc. However, for the Capacitor/Reactors, the EMS needs to have a controlling switch modeled, else they would always be "On | T R/C | Alpha | B/DVE | Joel Koepke |  |  | N | N
Transmission | COMMENTS |  |  | Capacitor and Reactor Data |  |  | CAPREACT | COMMENTS_CAPREACT | [7 empty] | N | N
Transmission | EFFECTIVE DATE: |  |  | Capacitor and Reactor Data |  | mm/dd/yyyy | CAPREACT | EFF_DATE | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T R | Date | B/DVB | Scott/Woody/Angie |  |  | N | N
Transmission | Static Var Compensator Data |  |  | Static Var Compensator Data |  |  | Not in table | Not in table
Transmission | DESCRIPTION OF CHANGE |  |  | Static Var Compensator Data |  | List | STATIC_VAR_COMP | CHANGE_DESCRIPTION | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T R | Alpha | B | Joel Koepke |  |  | N | N
Transmission | STATIC VAR COMPENSATOR |  |  | Static Var Compensator Data |  |  | Not in table | Not in table
Transmission | SVC Name |  |  | Static Var Compensator Data |  | enter all caps | STATIC_VAR_COMP | SVC_NAME | 1) This field is required 2) May not be > than 14 characters..Warning! SVC Name () should not be >14 characters long or the name will be truncated in the model which requires uniqueness. 3) May not contain special characters except for an underscore "_" and a dash "-" 4) Device Name can not be duplicated in a Station | T R | Alpha | B | Joel Koepke |  |  | N | N
Transmission | ERCOT Station Name (Station Code or Station Mnemonic) |  |  | Static Var Compensator Data |  | enter all caps | STATIC_VAR_COMP | SUBSTATION_CODE | 1) This field is required 2) Must match ERCOT records (unless new).Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) Must be <= 8 characters. Warning! Station Name () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. | T R | Alpha | B/DVE | Joel Koepke |  |  | N | N
Transmission | SVC CODE |  | UPDATED 03/2012 | Static Var Compensator Data |  | Automatic | STATIC_VAR_COMP | SVC_CODE | Concantenate (Site Code_Substation Code_SVC Name) |  | Character |  |  |  |  | N | N
Transmission | SVC Base Voltage Level |  | Updated: 1/2016 | Static Var Compensator Data |  | kV | STATIC_VAR_COMP | SVC_BASE_VOLT | 1) This field is required 2) If the value >= 69kv it must be 69, 138, 230 or 345 3) The value may not exceed 345 4) The value must be > 0 | T R | Float | B/DVE | Joel Koepke |  |  | N | Y
Transmission | Fixed Mvar (var injection At Nominal Voltage) | 11/26/2012 update validation 2 | UPDATED 03/2012 | Static Var Compensator Data |  | MVAR | STATIC_VAR_COMP | FIXED_MVAR | 1) This field is required 2. Value must be numeric | T R | Float | B/DVE | Joel Koepke/Planning 11/08/11 |  |  | N | Y
Transmission | Minimum Admittance Limits (on a 1MVA basis which = MVAR capability) | 2/10/2016 Updated Field Name 10/09/2012 Changed field name on form and label | UPDATED 03/2012 | Static Var Compensator Data |  | p.u. | STATIC_VAR_COMP | MIN_ADM_LIMIT | 1) This field is required 2) Value must be <= Maximum Admittance | T R | Float | B/DVE | Joel Koepke/Planning 11/08/11 |  |  | N | Y
Transmission | Maximum Admittance Limits (on a 1MVA basis which = MVAR capability) | 2/10/2016 Updated Field Name 10/09/2012 Changed field name on form and label | UPDATED 03/2012 | Static Var Compensator Data |  | p.u. | STATIC_VAR_COMP | MAX_ADM_LIMIT | 1) This field is required 2) Value must be >= Minimum Admittance | T R | Float | B/DVE | Joel Koepke/Planning 11/08/11 |  |  | N | Y
Transmission | Minimum Steady State Reactive Power Limits |  |  | Static Var Compensator Data |  | MVAR | STATIC_VAR_COMP | MIN_STD_STATE_REACT | 1) This field is required 2) Value must be <= Maximum Steady State Reactive Power Limits | T R | Float | B/DVE | Joel Koepke |  |  | N | Y
Transmission | Maximum Steady State Reactive Power Limits |  |  | Static Var Compensator Data |  | MVAR | STATIC_VAR_COMP | MAX_STD_STATE_REACT | 1) This field is required 2) Value must be >= Minimum Steady State Reactive Power Limits | T R | Float | B/DVE | Joel Koepke |  |  | N | Y
Transmission | Minimum Threshold (post Contingency) Reactive Power Limits |  |  | Static Var Compensator Data |  | MVAR | STATIC_VAR_COMP | MIN_THRESH_REACT | 1) This field is required 2) Value must be <= Maximum Threshold (post contingency) Reactive Power Limits | T R | Float | B/DVE | Joel Koepke |  |  | N | Y
Transmission | Maximum Threshold (post Contingency) Reactive Power Limits |  | UPDATED 03/2012 | Static Var Compensator Data |  | MVAR | STATIC_VAR_COMP | MAX_THRESH_REACT | 1) This field is required 2) Value must be <= Maximum Steady State Reactive Power Limits | T R | Float | B/DVE | Joel Koepke/Planning 11/08/11 |  |  | N | Y
Transmission | Minimum Voltage Threshold |  | UPDATED 03/2012 | Static Var Compensator Data |  | kV | STATIC_VAR_COMP | MIN_VOLT_THRESH | 1) This field is required 2) Value must be <= Maximum Voltage Threshold (100 MVA Base) 3) The value may not exceed 370 3) The value must be > 0 4) Warn if Max / Min exceed 50% of one another | T R | Float | B/DVE | Joel Koepke/Planning 11/08/11 |  |  | N | Y
Transmission | Maximum Voltage Threshold |  | UPDATED 03/2012 | Static Var Compensator Data |  | kV | STATIC_VAR_COMP | MAX_VOLT_THRESH | 1) This field is required 2) Value must be >= Minimum Voltage Threshold (100 MVA Base) 3) The value may not exceed 370 4) The value must be > 0 5) Warn if Max / Min exceed 50% of one another | T R | Float | B/DVE | Joel Koepke/Planning 11/08/11 |  |  | N | Y
Transmission | Device Name(s) - that this reactive device is directly connected to |  |  | Static Var Compensator Data |  | enter all caps | STATIC_VAR_COMP_DEVICES | SWITCH_DEVICE_NAME | 1) This field is optional 2) May not contain special characters except for an underscore "_" and a dash "-" 3) May not be > than 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. | T R | Alpha | B | Joel Koepke |  |  | N | N
Transmission | COMMENTS |  |  | Static Var Compensator Data |  |  | STATIC_VAR_COMP | COMMENTS_STATIC VAR_COMP | [7 empty] | N | N
Transmission | EFFECTIVE DATE: |  |  | Static Var Compensator Data |  | mm/dd/yyyy | STATIC_VAR_COMP | EFF_DATE | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T R | Date | B/DVB | Scott/Woody/Angie |  |  | N | N
Transmission | Series Device Data |  |  | Series Device Data |  |  | Not in table | Not in table
Transmission | DESCRIPTION OF CHANGE |  |  | Series Device Data |  | List | SERIES_DEVICE_DATA | CHANGE_DESCRIPTION | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T R | Alpha | B | Joel Koepke |  |  | N | N
Transmission | SERIES DEVICE DATA |  |  | Series Device Data |  |  | Not in table | Not in table
Transmission | Series Device Name |  |  | Series Device Data |  | enter all caps | SERIES_DEVICE_DATA | SD_NAME | 1) This field is required 2) No special characters except and underscore 3) Warn if >= 14 characters. First 14 characters must be unique. Warning! Series Device Name() should not be >= 14 characters long or the name will be truncated in the model which requires uniqueness. 4) Device Name can not be duplicated in a Station | T R | Alpha | B | Joel Koepke |  |  | N | N
Transmission | Ercot Station Code Mnemonic |  |  | Series Device Data |  | enter all caps | SERIES_DEVICE_DATA | SUBSTATION_CODE | 1) This field is required 2) Must match ERCOT records (unless new).Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters. Warning! Station Code () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. | T R | Alpha | B | Joel Koepke |  |  | N | N
Transmission | SD Code |  | UPDATED 03/2012 | Series Device Data |  | Automatic | SERIES_DEVICE_DATA | SD_CODE | Concantenate (Site Code_Substation Code_SD Name) | A | Character |  |  |  |  | N | N
Transmission | Voltage Level |  | Updated: 1/2016 | Series Device Data |  | kV | SERIES_DEVICE_DATA | VOLATGE | 1) This field is required 2) If the value >= 69kv it must be 69, 138, 230 or 345 3) The value may not exceed 345 4) The value must be > 0 | T R | Float | B/DVE | Joel Koepke |  |  | N | Y
Transmission | Resistance |  |  | Series Device Data |  | p.u. | SERIES_DEVICE_DATA | RESISTANCE | 1) This value is required 2) Value must be > 0 | T R | Float | B | Joel Koepke |  |  | N | Y
Transmission | Reactance |  |  | Series Device Data |  | p.u. | SERIES_DEVICE_DATA | REACTANCE | 1) This value is required 2) Value may be negative. Allow negative Reactance (to represent Series Capacitors) 3)Error if Reactance value is > 1. Error! Reactance (value) > 1.0. Reactance should be expressed in terms of per unit (e.g. not percentage). | T R | Float | B | Joel Koepke |  |  | N | Y
Transmission | Continuous Rating |  |  | Series Device Data |  | MVA | SERIES_DEVICE_DATA | CONTINUOUS_RTG | 1) This field is required 2) Value must be <= 2-hr Emergency Rating 3) Value must be <= 15-min Rating | T R | Float | B/DVE | Joel Koepke |  |  | N | Y
Transmission | 2-hr Emergency Rating |  |  | Series Device Data |  | MVA | SERIES_DEVICE_DATA | EMGCY_RTG_2HR | 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be <=15-min Rating | T R | Float | B/DVE | Joel Koepke |  |  | N | Y
Transmission | 15-min Rating |  |  | Series Device Data |  | MVA | SERIES_DEVICE_DATA | RTG_15MIN | 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be >= 2-hr Emergency Rating | T R | Float | B/DVE | Joel Koepke |  |  | N | Y
Transmission | DC Resistance |  | Added 05/01/2017 | Series Device Data |  | Ohms/Phase | SERIES_DEVICE_DATA | DC_RES | 1) This field is required and Data type is numeric 2) Generate an Error if the value entered is not >= 0.0 and <= [Resistance] * {[Voltage Level] ^2} / 100 | R | [6 empty] | R | R
Transmission | Side 1 |  |  | Series Device Data |  |  | Not in table | Not in table
Transmission | Side 1 - Connected Switching Device Name(s) |  |  | Series Device Data |  | enter all caps | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | 1) This field is required 2) May not have duplicates within the TO or FROM Station. Warning Only 3) May not contain special characters except for an underscore "_" and a dash "-" 4) May not be > than 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. | T R/C | Alpha | B | Joel Koepke |  |  | N | N
Transmission | Side 1 - Bus Number (PTI Bus Number) | 06/14/2012 Updated Validation #2 to increase to 999,999 |  | Series Device Data |  | # | SERIES_DEVICE_DATA | SIDE1_PTI_BUS_NUM | 1) This field is optional 2) This field must be between 1 - 999,999 | T O | Integer | B/DVE | Joel Koepke |  |  | N | N
Transmission | Side 2 |  |  | Series Device Data |  |  | Not in table | Not in table
Transmission | Side 2 - Connected Switching Device Name(s) |  |  | Series Device Data |  | enter all caps | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | 1) This field is required 2) May not have duplicates within the TO or FROM Station 3) May not contain special characters except for an underscore "_" and a dash "-" 4) May not be > than 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. | T R/C | Alpha | B | Joel Koepke |  |  | N | N
Transmission | Side 2 - Bus Number (PTI Bus Number) | 06/14/2012 Updated Validation #2 to increase to 999,999 |  | Series Device Data |  | # | SERIES_DEVICE_DATA | SIDE2_PTI_BUS_NUM | 1) This field is optional 2) This field must be between 1 - 999,999 | T O | Integer | B/DVE | Joel Koepke |  |  | N | N
Transmission | COMMENTS |  |  | Series Device Data |  |  | SERIES_DEVICE_DATA | SD_COMMENTS | [7 empty] | N | N
Transmission | EFFECTIVE DATE: |  |  | Series Device Data |  | mm/dd/yyyy | SERIES_DEVICE_DATA | EFF_DATE | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T R | Date | B/DVB | Scott/Woody/Angie |  |  | N | N
Transmission | Transformer Data |  |  | Transformer Data |  |  | Not in table | Not in table
Transmission | DESCRIPTION OF CHANGE |  |  | Transformer Data |  | List | TRANSFORMER | CHANGE_DESCRIPTION | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T C | Alpha | B | Joel Koepke |  |  | N | N
Transmission | TRANSFORMER DETAILS |  |  | Transformer Data |  |  | Not in table | Not in table
Transmission | Transformer Name |  |  | Transformer Data |  | enter all caps | TRANSFORMER | TRANSFORMER_NAME | 1) This field is required 2) May not contain special characters except for an underscore "_" and a dash "-" 3) Warn if >= 14 characters. First 14 characters must be unique. Warning! Transformer Name () should not be >14 characters long or the name will be truncated in the model which requires uniqueness. 4) l Device name must be unique for each Device code for a substation in a SITE | T R | Alpha | B | Joel Koepke |  |  | N | N
Transmission | ERCOT Station Name (Station Code or Station Mnemonic) |  |  | Transformer Data |  | enter all caps | TRANSFORMER | SUBSTATION_CODE | 1) This field is required 2) Must match ERCOT records. Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters. Warning! Station Name () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) substation code should be in Upper case letters. Generate an error if the rule fails | T R | Alpha | B | Joel Koepke |  |  | N | N
Transmission | Transformer Code |  | UPDATED 03/2012 | Transformer Data |  | Automatic | TRANSFORMER | TRANSFORMER_CODE | Concantenate (Site Code_Substation Code_Transformer Name) | A | Character |  |  |  |  | N | N
Transmission | Transformer Test Report Attached? |  |  | Transformer Data |  | Y/N | Not in table | Not in table | Select from the list: Y or N | R | Dropdown List |  | Model Adminstration
Transmission | Is this transformer in Master / Follower of Current Balancing configuration? |  |  | Transformer Data |  | Y/N | TRANSFORMER | MASTER_FOLLOW_FLG | 1) This field is required 2) Value must be in the following list: 'Y', 'N' | T R | Alpha | B |  |  |  | N | N
Transmission | Master Name (can be same as this transformer) |  |  | Transformer Data |  | enter all caps | TRANSFORMER | MASTER_NAME | 1) This field is conditionally required if Transformer Data - Is this transformer in Master / Follower of Current Balancing configuration? = 'Y' 2) Warn if >= 14 characters. First 14 characters must be unique. Warning! Master Name () should not be >=14 characters long or the name will be truncated in the model which requires uniqueness. 3) May not contain special characters except for an underscore "_" and a dash "-" 4) Either the Master Name or the Follower Name MUST = Transformer Data - Transformer Name | T C | Alpha | B/DVE |  |  |  | N | N
Transmission | Follower Name (can be same as this transformer) |  |  | Transformer Data |  | enter all caps | TRANSFORMER | FOLLOWER_NAME | 1) This field is conditionally required if Transformer Data - Is this transformer in Master / Follower of Current Balancing configuration? = 'Y' 2) May not contain special characters except for an underscore "_" and a dash "-" 3) Either the Master Name or the Follower Name MUST = Transformer Data - Transformer Name 4) Warn if >= 14 characters. First 14 characters must be unique. Warning! Follower Name () should not be >=14 characters long or the name will be truncated in the model which requires uniqueness. | T C | Alpha | B/DVE |  |  |  | N | N
Transmission | Generation Step-Up Transformer? |  |  | Transformer Data |  | Y/N | TRANSFORMER | GSU_TRANSFORMER_FLG | 1) This field is required 2) Value must be in the following list: 'Y', 'N' | T R | Alpha | B | Joel Koepke |  |  | N | Y
Transmission | Zero Sequence Data - Winding Connection Code (1-5) | 2/16/2016 Updated Field Name 05/15/2012 Updated Validation to Required. 04/24/2012 Change Column name on RARF Form and removed p.u. lable | ADDED 06/27/2012 | Transformer Data | Transformer_Info.View | p.u. | TRANSFORMER | ZERO_SEQ_DATA_WINDING_CON_CODE | 1) This field is Required 2) Data type must be string | T R | real | B,DVB | Model Adminstration |  |  | N | Y
Transmission | Zero Sequence Grounding Resistance For An Impedance Grounded Transformer In P.u. (100 Mva Base) | 10/04/2012 Change rule #2 and remove rule #3 | ADDED 06/27/2012 | Transformer Data | Transformer_Info.View | p.u. | TRANSFORMER | ZERO_SEQ_GRUND_RESISTANCE_IMPEDANCE_GRUND_TRANS_PU | 1) This field is required and Data type is numeric 2) Value must be greater than or equal to 0.0 and less than or equal to 99999.0 | R |  |  | Model Adminstration |  |  | N | Y
Transmission | Zero Sequence Grounding Reactance For An Impedance Grounded Transformer In P.u. (100 Mva Base) | 10/04/2012 Change rule #2 and remove rule #3 | ADDED 06/27/2012 | Transformer Data | Transformer_Info.View | p.u. | TRANSFORMER | ZERO_SEQ_GRUND_REACTANCE_IMPEDANCE_GRUND_TRANS_PU | 1) This field is required and Data type is numeric 2) Value must be greater than or equal to 0.0 and less than or equal to 99999.0 | R |  |  | Model Adminstration |  |  | N | Y
Transmission | Zero Sequence Resistance In P.u. (100 Mva Base) | 07/25/2013 Add validation #3 10/08/2012 Updated Validation rule CR46802 | ADDED 06/27/2012 | Transformer Data | Transformer_Info.View | p.u. | TRANSFORMER | ZERO_SEQ_TRANS_RESISTANCE_PU | 1) This field is required and Data type is numeric 2) Generate a Warning if the per unit value entered is not >= 0.0 and <= 100.0 | R |  |  | Model Adminstration |  |  | N | Y
Transmission | Zero Sequence Reactance In P.u. (100 Mva Base) | 07/25/2013 Add validation #3 10/08/2012 Updated Validation rule CR46802 | ADDED 06/27/2012 | Transformer Data | Transformer_Info.View | p.u. | TRANSFORMER | ZERO_SEQ_TRANS_REACTANCE_PU | 1) This field is required and Data type is numeric 2) Generate a Warning if the per unit value entered is not >= 0.0 and <= 100.0 | R |  |  | Model Adminstration |  |  | N | Y
Transmission | Positive Sequence Resistance (100 MVA Base) | 07/25/2013 Add validation #3 10/08/2012 Updated Validation rule CR46802 | UPDATED 03/2012 | Transformer Data |  | p.u. | TRANSFORMER | SERIES_ RESIST | ) This field is required and Data type is numeric 2) Generate a Warning if the per unit value entered is not > 0.0 and <= 2.0 3) Error If series_resist < 0 and Low_NoLoad !=1 4) Warning if Low_NoLoad != 1 and Resistance/Reactance ratio > 1 5) Error if Resistance value has precision less than 3 decimal places 6) Warning if Resistance value has precision less than 5 decimal places | R |  |  | Model Adminstration |  |  | N | Y
Transmission | Positive Sequence Reactance (100 MVA Base) | 07/25/2013 Add validation #3 10/08/2012 Updated Validation rule CR46802 | UPDATED 03/2012 | Transformer Data |  | p.u. | TRANSFORMER | SERIES_ REACT | 1) This field is required and Data type is numeric 2) Generate a Warning if the per unit value entered is not > 0.0 and <= 2.0 3) Error If series_react < 0 and Low_NoLoad !=1 4) Error if series_react > 2.0 and Transformer MVA Continuous Rating > 5.0 5) Error if Reactance value has precision less than 3 decimal places 6) Warning if Reactance value has precision less than 5 decimal places | R |  |  | Model Adminstration |  |  | N | Y
Transmission | Continuous Rating |  |  | Transformer Data |  | MVA | TRANSFORMER | CONTINUOUS_RTG | 1) This field is required 2) Value must be <= 2-hr Emergency Rating 3) Value must be <= 15-min Rating 4) Transformer Continuous MVA Rating should be >=HRL or unit will be curtailed down to transformer rating" 5) Continuous must have valid mva rating (eg: will get an ERROR if 9999.00) | T R | Integer | B/DVE | Joel Koepke |  |  | N | Y
Transmission | 2-hr Emergency Rating |  |  | Transformer Data |  | MVA | TRANSFORMER | EMGCY_RTG_2HR | 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be <= 15-min Rating 4) 2hr-rating must have valid mva rating (9999.00 mva will produce a WARNING) | T R | Integer | B/DVE | Joel Koepke |  |  | N | Y
Transmission | 15-min Rating |  |  | Transformer Data |  | MVA | TRANSFORMER | RTG_15MIN | 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be >= 2-hr Emergency Rating 4) 15min rating must have valid mva rating(9999.00 mva will produce a WARNING), also if 2hr is 9999.00 then the only valid entry for 15min is 9999.00 or it will give an ERROR. | T R | Integer | B/DVE | Joel Koepke |  |  | N | Y
Transmission | Relay Loadability Limit |  | Added 05/01/2017 | Transformer Data |  | MVA | TRANSFORMER | REL_LOAD_LMT | 1) This field is required 2) Data type must be Numeric 3) Generate a Warning if Value < 15-Minute Rating | T R | [6 empty] | R | R | R
Transmission | Unit(s) associated with this transformer |  |  | Transformer Data |  | enter all caps | TRANSFORMER_UNITS | TRANSFORMER_UNIT_CODE | 1) This field is conditionally required - if Generation Step-up = 'Y', this is required 2) Value(s) must be <=17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. 3) Warn if the unit name is not in the Unit Info - GEN or Unit Info - CC or Unit Info - Wind 4) Generate an ERROR when Non GSU Transformers that have entered associated units. | T C | Alpha | B | Joel Koepke |  |  | N | N
Transmission | HIGH SIDE VOLTAGE INFORMATION |  |  | Transformer Data |  |  | Not in table | Not in table
Transmission | High Side Voltage Level (no-load) |  | Updated: 1/2016 | Transformer Data |  | kV | TRANSFORMER | HIGH_NOLOAD | 1) This field is required 2) If the value >= 69kv it must be 69,138, 230 or 345 3) The value may not exceed 345 4) The value must be > 0 5) The value must be >= Low Voltage Level (no-load) | T R | Float | B/DVE | Joel Koepke |  |  | N | N
Transmission | High Side PTI Bus Number | 2/10/2016 Updated Field Name 06/14/2012 Updated Validation #2 to increase to 999,999 |  | Transformer Data |  | # | TRANSFORMER | HIGH_PTI | 1) This field is optional 2) This field must be between 1 - 999,999 | T O | Integer | B |  |  |  | N | N
Transmission | High Side Voltage Connection - Wye or Delta |  |  | Transformer Data |  | List | TRANSFORMER | HIGH_CONNECTION | 1) This field is required 2) Value must be of the following: 'Wye', 'Delta' | T R | Alpha | B |  |  |  | N | Y
Transmission | High Side Voltage Connected devices (list on separate lines) |  |  | Transformer Data |  |  | TRANSFORMER_DEVICES | DEVICE_NAME | 1) This field is required a) Error: if High Side Voltage >= 60kV and Low Side Voltage >1kV b) Warn: if High Side Voltage < 60kV and Low Side Voltage = 1kV 2) No special characters except an underscore or a dash 3) Warn if >= 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. 4) connected devices listed in transformer tab should exist in the breaker switch tab. Generate an error when the rule fails | T R | Alpha | B | Joel Koepke |  |  | N | N
Transmission | High Side Manufactured Nominal Voltage |  | Updated: 1/2016 | Transformer Data |  | kV | TRANSFORMER | HIGH_MANU_VOLT | 1) This field is required 2) If value > 60kV Accepted if value (using 5%) Deviates < ¦3.45¦ kV from 69 Deviates < ¦6.9¦ kV from 138 Deviates < ¦11.5¦ kV from 230 Deviates < ¦17.25¦ kV from 345 Warn if value (using >= 5% and <10%) Deviates > = ¦3.45¦ but deviates < ¦6.9¦ from 69 Deviates >= ¦6.9¦ but deviates < 13.8 from 138 Deviates >= ¦11.5¦ but deviates < 23.0 from 230 Deviates >= ¦17.25¦ but deviates < 34.5 from 345 Error if value (using > =10%) Deviates >= ¦6.9¦ kV from 69 Deviates >= ¦13.8¦kV from 138 Deviates >= ¦11.5¦ kV from 230 Deviates >= ¦34.5¦kV from 345 3) Warn if value > 345 4) The value must be > 0 5) High Side Manufactured Nominal Voltage >= Low Side Manufactured Nominal Voltage 6) High Side Manufactured Nominal Voltage should be > Voltage at Lowest Tap Position and < Voltage at Highest Tap Position 7) Transformer High Side Manufactured Nominal Voltage should equal to Voltage at Highest Tap - Step Size voltage to reach Nominal Tap. | T R | Float | B/DVE |  |  |  | N | Y
Transmission | LOW SIDE VOLTAGE INFORMATION |  |  | Transformer Data |  |  | Not in table | Not in table
Transmission | Low Side Voltage Level (no-load) |  | Updated: 1/2016 | Transformer Data |  | kV | TRANSFORMER | LOW_NOLOAD | 1) This field is required 2) If the value >= 69kv it must be 69, 230,138, or 345 3) The value may not exceed 345 4) The value must be > 0 5) The value must be <= High Voltage Level (no-load) 6) If Generator Step-up Transformer = 'Y' AND Low Side Voltage Level (no-load) > 1kV AND Then the Low Side Voltage Level (no-load) must be equal to Unit Info - GEN / CC / WIND - Unit Generating Voltage | T R | Float | B/DVE | Joel Koepke |  |  | N | N
Transmission | Low Side PTI Bus Number | 2/10/2016 Updated Field Name 06/14/2012 Updated Validation #2 to increase to 999,999 |  | Transformer Data |  | # | TRANSFORMER | LOW_PTI | 1) This field is optional 2) This field must be between 1 - 999,999 | T O | Integer | B |  |  |  | N | N
Transmission | Low Side Voltage Connection - Wye or Delta |  |  | Transformer Data |  | List | TRANSFORMER | LOW_CONNECTION | 1) This field is required 2) Value must be of the following: 'Wye', 'Delta' | T R | Alpha | B |  |  |  | N | Y
Transmission | Low Side Voltage Connected device(s) (list on separate lines) |  |  | Transformer Data |  |  | TRANSFORMER_DEVICES | DEVICE_NAME | 1) This field is required a) Error: if High Side Voltage >= 60kV and Low Side Voltage >1kV b) Warn: if High Side Voltage < 60kV and Low Side Voltage = 1kV 2) Warn if >= 17 characters. 3) No special characters except an underscore "_" or a dash "-" 4) connected devices listed in transformer tab should exist in the breaker switch tab. Generate an error when the rule fails | T R | Alpha | B | Joel Koepke |  |  | N | N
Transmission | Low Side Manufactured Nominal Voltage |  |  | Transformer Data |  | kV | TRANSFORMER | LOW_MANU_VOLT | 1) This field is required 2) If the value >= 69kv: Accepted if value (using 5%) Deviates < ¦3.45¦ kV from 69 Deviates < ¦6.9¦ kV from 138 Deviates < ¦17.25¦ kV from 345 Warn if value (using >= 5% and <10%) Deviates > = ¦3.45¦ but deviates < ¦6.9¦ from 69 Deviates >= ¦6.9¦ but deviates < 13.8 from 138 Deviates >= ¦17.25¦ but deviates < 34.5 from 345 Error if value (using > =10%) Deviates >= ¦6.9¦ kV from 69 Deviates >= ¦13.8¦kV from 138 Deviates >= ¦34.5¦kV from 345 3) Warn if value > 345 4) The value must be > 0 5) High Side Manufactured Nominal Voltage >= Low Side Manufactured Nominal Voltage 6) Low Side Manufactured Nominal Voltage should equal (Voltage at Lowest Tap) + (Step size voltage to reach Nominal tap) | T R | Float | B/DVE |  |  |  | N | Y
Transmission | VOLTAGE REGULATION |  |  | Transformer Data |  |  | Not in table | Not in table
Transmission | On-Load Voltage Regulation | 2/10/2016 Updated Filed Name |  | Transformer Data |  | Y/N | TRANSFORMER | AUTO_VOLT_REG | 1) This field is required 2) Value must be from the following list: 'Y', 'N' 3) AVR is expected to be 'Y' when total number of tap positions >=16. Warn if "Automatic Voltage Regulation" = 'N' and Total Number of Tap Positions>=16 | T R | Alpha | B/DVE | Joel Koepke |  |  | N | Y
Transmission | Does Transformer have a On-Load Tap Changer? | 2/10/2016 Updated Filed Name |  | Transformer Data |  | Y/N | TRANSFORMER | LOADTAP_CHNGR_FLG | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) Value must be from the following list: 'Y', 'N' 3) Load Tap Changer is expected to be 'Y' when total number of tap positions >=16. Warn if "Load Tap Changer" = 'N' and Total Number of Tap Positions>=16 | T C | Alpha | B/DVE | Joel Koepke |  |  | N | Y
Transmission | Location of On-Load Tap Changer - Primary (High) or Secondary (Low) side | 2/10/2016 Updated Filed Name |  | Transformer Data |  | List | TRANSFORMER | LOCN_TAP_CHNGR | 1) This field is conditionally required if 'Does Transformer have a Load Tap Changer ?' = 'Y' 2) Value must be of the following: 'HIGH', 'LOW' 3) Load Tap Changer should be 'Y' when AVR is 'Y'. Generate an error if Load Tap Changer is 'N' and AVR = 'Y'. | T C | Alpha | B/DVE |  |  |  | N | Y
Transmission | Base Kv of Regulated Side | 3/1/2016 Updated validation rule #3 2/10/2016Updated Field Name 7/03/2012 Change field name in Data base | 3/1/2016 Updated validation rule #3 2/10/2016 Field Name Updated ADDED 06/27/2012 | Transformer Data |  | kV | TRANSFORMER | REG_KV_BASE | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) If the value >= 69kv it must be 69, 138, 230 or 345 3) The value may not exceed 345 4) The value must be > 0 5) The value must be >= Low Voltage Level (no-load) | T C | Float | B | Joel Koepke |  |  | N | N
Transmission | Target Kv of Regulated Side |  |  | Transformer Data |  | kV | TRANSFORMER | REG_KV_TARGET | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) Value must be > 0 | T C | Float | B | Joel Koepke |  |  | N | N
Transmission | Acceptable Deviation of Target Voltage in Percent | 05/03/2012 removed percent from label on form |  | Transformer Data |  |  | TRANSFORMER | ACCEPT_DEV_VOLT_TARGET | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) Value must not exceed 50% | T C | Percentage | B | Joel Koepke |  |  | N | N
Transmission | DC Resistance of Winding 1 |  | Added 05/01/2017 | Transformer Data |  | Ohms/Phase | TRANSFORMER | DC_RES_WD1 | 1) This field is required and Data type is numeric 2) Generate an Error of the value entered is not >=0.0 and <= 10.0 | T R | [7 empty] | R | R
Transmission | DC Resistance of Winding 2 |  | Added 05/01/2017 | Transformer Data |  | Ohms/Phase | TRANSFORMER | DC_RES_WD2 | 1) This field is required and Data type is numeric 2) If the Low Side Voltage <> 1kV, Generate a Error if the value entered is not >= 0.0 and <=10.0 | T R | [7 empty] | R | R
Transmission | GIC Blocking device on Winding 1 |  | Added 05/01/2017 | Transformer Data |  | Y/N | TRANSFORMER | GIC_BLK_DEC_WD1 | 1) This field is required | T R | [7 empty] | R | R
Transmission | GIC Blocking device on Winding 2 |  | Added 05/01/2017 | Transformer Data |  | Y/N | TRANSFORMER | GIC_BLK_DEC_WD2 | 1) This field is required | T R | [7 empty] | R | R
Transmission | Vector Group Identifer |  | Added 05/01/2017 | Transformer Data |  | List | TRANSFORMER | VEC_GRP_IDET | 1) This field is required | T R | [7 empty] | R | R
Transmission | Transformer Core Design Type |  | Added 05/01/2017 | Transformer Data |  | List | TRANSFORMER | NM_CRS_TRANS_CRS_DES | 1) This field is required | T R | [7 empty] | R | R
Transmission | K Factor |  | Added 05/01/2017 | Transformer Data |  | Text | TRANSFORMER | K_FACTOR | 1) This field is required and Data type is numeric 2) Value entered must be >= 0 and <= 2.5 | T R | [7 empty] | R | R
Transmission | Winding 1 Grounding DC Resistance |  | Added 05/01/2017 | Transformer Data |  | Ohms | TRANSFORMER | WD1_GRD_DC_RES | 1) This field is required and Data type is numeric 2) If not “99999”, then value entered must be >= 0 and <= 400 | T R | [7 empty] | R | R
Transmission | Winding 2 Grounding DC Resistance |  | Added 05/01/2017 | Transformer Data |  | Ohms | TRANSFORMER | WD2_GRD_DC_RES | 1) This field is required and Data type is numeric 2) If not “99999”, then value entered must be >= 0 and <= 2.5 | T R | [7 empty] | R | R
Transmission | Transformer Model |  | Added 05/01/2017 | Transformer Data |  | List | TRANSFORMER | TRANS_MDL | 1) This field is required | T R | [7 empty] | R | R
Transmission | COMMENTS |  |  | Transformer Data |  |  | TRANSFORMER | COMMENTS_TRANSFORMER |  | T R | [5 empty] | N | N
Transmission | EFFECTIVE DATE: |  |  | Transformer Data |  | mm/dd/yyyy | TRANSFORMER | EFF_DATE | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T R | Date | B/DVB | Scott/Woody/Angie |  |  | N | N
Transmission | Transformer Tap Settings |  |  | TRANSFORMER TAP SETTINGS |  |  | Not in table | Not in table
Transmission | DESCRIPTION OF CHANGE | Added 03/26/2012 | ADDED 06/27/2012 | Transformer Tap Settings | Transformer_HighTaps.View and Transformer_LowTaps.View | List | TRANSFORMER_TAP_SETTINGS | CHANGE_DESCRIPTION | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T C | Alpha | B | Joel Koepke |  |  | N | N
Transmission | Transformer Name | 6/15/2012 Added Field to form, mapping needed for the ETL and also needs to be added to DELTA and Audit | ADDED 06/27/2012 | Transformer Tap Settings |  | List | TRANSFORMER | TRANSFORMER_NAME | 1) This field is required 2) May not contain special characters except for an underscore "_" and a dash "-" 3) Warn if >= 14 characters. First 14 characters must be unique. Warning! Transformer Name () should not be >14 characters long or the name will be truncated in the model which requires uniqueness. 4) l Device name must be unique for each Device code for a substation in a SITE | T R | Alpha | B | Joel Koepke |  |  | N | N |  |  |  | Glossary in error, should be conditional
Transmission | ERCOT Station Name (Station Code or Station Mnemonic) | 6/15/2012 Added Field to form, mapping needed for the ETL and also needs to be added to DELTA and Audit | ADDED 06/27/2012 | Transformer Tap Settings |  | List | TRANSFORMER | SUBSTATION_CODE | 1) This field is required 2) Must match ERCOT records. Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters. Warning! Station Name () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) substation code should be in Upper case letters. Generate an error if the rule fails | T R | Alpha | B | Joel Koepke |  |  | N | N |  |  |  | Glossary in error, should be conditional
Transmission | Transformer Code |  | UPDATED 03/2012 | Transformer Tap Settings |  | Automatic | TRANSFORMER_TAP_SETTINGS | TRANSFORMER_CODE | Concantenate (Site Code_Substation Code_Transformer Name) | A | Character |  |  |  |  | N | N
Transmission | Primary (High) -Secondary (Low) Flag |  | UPDATED 03/2012 | Transformer Tap Settings |  | List | TRANSFORMER_TAP_SETTINGS | LOW_HIGH_FLG | 1) This field is conditioally reguired.This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be of the following: High or Low | T R | [5 empty] | N | Y |  |  |  | Glossary in error, should be conditional. Description is fine if the glossary is changed, but is currently not aligned with it.
Transmission | TAP SETTINGS |  |  | Transformer Tap Settings |  |  | Not in table | Not in table
Transmission | Tap position at Manufactured Nominal Voltage |  |  | Transformer Tap Settings |  | # | TRANSFORMER_TAP_SETTINGS | MANU_VOLT_TAP_POS | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field must be left blank if Low Voltage Level = 1 2) Note: this value may be negative 3. Value must be between Lowest and Highest Tap position 4)All tap information is required if it exists on either the LTC or Fixed side. | T R | Integer | B |  |  |  | N | Y |  |  |  | Glossary in error, should be conditional. Description is fine if the glossary is changed, but is currently not aligned with it.
Transmission | Total Number of Tap Positions |  |  | Transformer Tap Settings |  | # | TRANSFORMER_TAP_SETTINGS | TOTAL_NUM | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be >= 2 3) Warn if value >= 16 and "Automatic Voltage Regulation" = 'N' Warn if value >=16 and "Load Tap Changer" = 'N' | T R | Integer | B | Joel Koepke |  |  | N | Y |  |  |  | Glossary in error, should be conditional. Description is fine if the glossary is changed, but is currently not aligned with it.
Transmission | Normal Tap Position |  |  | Transformer Tap Settings |  | # | TRANSFORMER_TAP_SETTINGS | NORMAL_POS | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out. Note that it is valid for both, Low and High Tap settings to be filled out. Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be >= Low Tap Settings - Lowest Tap Position 3) Value must be <= Low Tap Settings - Highest Tap Position 4) Note: this value may be negative | T R | Integer | B | Joel Koepke |  |  | N | Y |  |  |  | Glossary in error, should be conditional. Description is fine if the glossary is changed, but is currently not aligned with it.
Transmission | Lowest Tap Position |  |  | Transformer Tap Settings |  | # | TRANSFORMER_TAP_SETTINGS | LOWEST_POS | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be <= Low Tap Settings - Highest Tap Position 3) Note: this value may be negative | T R | Integer | B | Joel Koepke |  |  | N | Y |  |  |  | Glossary in error, should be conditional. Description is fine if the glossary is changed, but is currently not aligned with it.
Transmission | Voltage at Lowest Tap Position |  |  | Transformer Tap Settings |  | kV | TRANSFORMER_TAP_SETTINGS | LOWEST_VOLT | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be <= Low Tap Settings - Voltage at Highest Tap Position 3) Value must be < High Tap Settings - Voltage at Lowest Tap Position 4) Value must be >= 0 | T R | Float | B | Joel Koepke |  |  | N | Y |  |  |  | Glossary in error, should be conditional. Description is fine if the glossary is changed, but is currently not aligned with it.
Transmission | Highest Tap Position |  |  | Transformer Tap Settings |  | # | TRANSFORMER_TAP_SETTINGS | HIGHEST_POS | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out. Note that it is valid for both, Low and High Tap settings to be filled out. Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be >= Low Tap Settings - Low Tap Position 3) Note: this value may be negative | T R | Integer | B | Joel Koepke |  |  | N | Y |  |  |  | Glossary in error, should be conditional. Description is fine if the glossary is changed, but is currently not aligned with it.
Transmission | Voltage at Highest Tap Position |  |  | Transformer Tap Settings |  | kV | TRANSFORMER_TAP_SETTINGS | HIGHEST_VOLT | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out. Note that it is valid for both, Low and High Tap settings to be filled out. Second Condition: This field may be left blank if Low Voltage Level = 1 2) Value must be >= Low Tap Settings - Voltage at Lowest Tap Position 3) Value must be <= High Tap Settings - Voltage at Highest Tap Position 4) Value must be >= 0 | T R | Float | B | Joel Koepke |  |  | N | Y |  |  |  | Glossary in error, should be conditional. Description is fine if the glossary is changed, but is currently not aligned with it.
Transmission | Size of each Voltage Step |  |  | Transformer Tap Settings |  | kV | TRANSFORMER_TAP_SETTINGS | STEP_VOLT | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field may be left blank if Low Voltage Level = 1 2) Value must > 0 3) Warn if < 0.002 * Low Side Voltage Level (no-load) 4) Warn if > 0.05 * Low Side Voltage Level (no-load) | T R | Float | B |  |  |  | N | Y |  |  |  | Glossary in error, should be conditional. Description is fine if the glossary is changed, but is currently not aligned with it.
Transmission | Load Data |  |  | Load Data |  |  | Not in table | Not in table
Transmission | DESCRIPTION OF CHANGE |  |  | Load Data |  | List | LOADS | CHANGE_DESCRIPTION
Transmission | Load Data |  |  | Load Data |  |  | Not in table | Not in table
Transmission | Ercot Station Code Mnemonic |  |  | Load Data |  | enter all caps | LOADS | SUBSTATION_CODE | 1) This field is required 2) Must match ERCOT records. Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters 5) substation code should be in Upper case letters. Generate an error if the rule fails | L C | Alpha | B
Transmission | Load Name |  |  | Load Data |  | enter all caps | LOADS | LOAD_NAME | 1) This field is required 2) May not contain special characters except for an underscore "_" and a dash "-" 2) Warn if >= 14 characters. First 14 characters must be unique. 3)Warning! ERCOT Load Name() should not be >= 14 characters long or the name will be truncated in the model which requires uniqueness. 4) Load Name can not be duplicated in a Station | L C | Alpha | B
Transmission | Load Code |  | UPDATED 03/2012 | Load Data |  | Automatic | LOADS | LOAD_CODE | Concantenate (Site Code_Substation Code_Lode Name | A | Character
Transmission | Load Voltage Level |  |  | Load Data |  | kV | LOADS | VOLATGE | 1) This field is required 2) Value must be >= 0 3) If the value >= 69kv it must be 69,138, or 345 | T R | Float | B
Transmission | PTI Bus Number | 06/14/2012 Updated Validation #2 to increase to 999,999 |  | Load Data |  | # | LOADS | PTI_BUS_NUM | 1) This field is optional 2) This field must be between 1 - 999,999 | T O | Integer | B
Transmission | Average Load Under Normal Operations |  |  | Load Data |  | MW | LOADS | AVG_LOAD | 1) This field is required 2) It should be >0 and generate a warning if = 0 | T R | Float | B
Transmission | Average Mvar Under Normal Operations |  |  | Load Data |  | MVAR | LOADS | AVG_MVAR | 1) This field is required 2) It should be >0 and generate a warning if = 0 | T R | Float | B
Transmission | Connected Devices |  |  | Load Data |  |  | Not in table | Not in table
Transmission | Device Name(s) - that this load is physically connected to |  |  | Load Data |  |  | LOAD_DEVICES | LOAD_DEVICE_NAME | 1) This field is required 2) No special characters except an underscore or a dash 3) Warn if >= 17 characters. First 17 characters must be unique. Warning! ERCOT Device Name() should not be >=17 characters long or the name will be truncated in the model which requires uniqueness. 4) 'Connected Device that this load is directly connected to' Field in Load Data Tab should be defined either in the Breaker/Switch Tab(if the connected device is a switch Name) or in the Transformer Tab(if the connected device is a Transformer Name). Produce an Error when connected device is missing in the Breaker_switch Tab. 'Error! Unique controlling device must also exist in the 'BREAKER_SWITCH Tab' | T R/C | Alpha | B
Transmission | Comments |  |  | Load Data |  |  | LOADS | LOAD_COMMENTS |  | O
Transmission | Effective Date: |  |  | Load Data |  | MM/DD/YYYY | LOADS | EFF_DATE | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T R | Date | B/DVB | Scott/Woody/Angie
Generation | SubSync - Gen |  |  | SubSync |  |  | Not in table | Not in table
Generation | GENERATOR DETAILS |  |  | SubSync |  |  | Not in table | Not in table
Generation | Unit Name | Do not show Message on Audit or Delta |  | SubSync |  | List | GENERATION | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | Y
Generation | SITE_CODE | SubSync |  | SubSync |  | Automatic | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | A | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | A
Generation | Resource Name (Unit Code/Mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | SubSync |  | Automatic | SUBSYNC | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | Y |  |  |  | This is filled automatically in the form, why is there any validation?
Generation | SUBSYNCHRONOUS RESONANCE |  |  | SubSync |  |  | Not in table | Not in table
Generation | Mass # | Correction 02/28/2012 |  | SubSync |  | List | SUBSYNC | MASS_NUMBER |  | C | [5 empty] | N | Y
Generation | Mass Code | Correction 02/28/2012 |  | SubSync |  | Automatic | SUBSYNC | MASS | CONCATENATE Unit_CODE_MASS | A | [5 empty] | N | Y
Generation | Name |  |  | SubSync |  |  | SUBSYNC | NAME |  | A | [5 empty] | N | Y
Generation | Mass Inertia |  |  | SubSync |  |  | SUBSYNC | MASS_INERTIA |  | C | [5 empty] | N | Y
Generation | Inertia Units |  |  | SubSync |  |  | SUBSYNC | INERTIA_UNITS |  | C | [5 empty] | N | Y
Generation | Associated Damping |  |  | SubSync |  |  | SUBSYNC | ASST_DMPG |  | C | [5 empty] | N | Y
Generation | Damping Units |  |  | SubSync |  |  | SUBSYNC | DMPG_UNITS |  | C | [5 empty] | N | Y
Generation | Stiffness Between Masses Previous and Current Masses |  |  | SubSync |  |  | SUBSYNC | STFNS_BTWN_MASSES |  | C | [5 empty] | N | Y
Generation | Stiffness Units |  |  | SubSync |  |  | SUBSYNC | STFNS_UNITS |  | C | [5 empty] | N | Y
CC | SubSync - CC |  |  | SubSync |  |  | Not in table | Not in table
CC | GENERATOR DETAILS |  |  | SubSync |  |  | Not in table | Not in table
CC | Unit Name | Do not show Message on Audit or Delta |  | SubSync |  | List | CCUNIT | UNIT_NAME | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS |  | N | Y
CC | SITE_CODE |  |  | SubSync |  | Automatic | CCUNIT | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | A | Character |  |  |  |  | N | Y |  |  |  | This is filled automatically in the form, why is there any validation?
CC | Resource Name (Unit Code/mnemonic) | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code |  | SubSync |  | Automatic | SUBSYNC | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R A | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N | Y |  |  |  | This is filled automatically in the form, why is there any validation?
CC | SUBSYNCHRONOUS RESONANCE |  |  | SubSync |  |  | Not in table | Not in table
CC | Mass # | Correction 02/28/2012 |  | SubSync |  | List | SUBSYNC | MASS_NUMBER |  | C | [5 empty] | N | Y
CC | Mass Code | Correction 02/28/2012 |  | SubSync |  | Automatic | SUBSYNC | MASS | CONCATENATE Unit_CODE_MASS | A | [5 empty] | N | Y
CC | Mass Name |  |  | SubSync |  |  | SUBSYNC | NAME |  | A | [5 empty] | N | Y
CC | Mass Inertia |  |  | SubSync |  |  | SUBSYNC | MASS_INERTIA |  | C | [5 empty] | N | Y
CC | Inertia Units |  |  | SubSync |  |  | SUBSYNC | INERTIA_UNITS |  | C | [5 empty] | N | Y
CC | Associated Damping |  |  | SubSync |  |  | SUBSYNC | ASST_DMPG |  | C | [5 empty] | N | Y
CC | Damping Units |  |  | SubSync |  |  | SUBSYNC | DMPG_UNITS |  | C | [5 empty] | N | Y
CC | Stiffness Between Masses Previous And Current Mass |  |  | SubSync |  |  | SUBSYNC | STFNS_BTWN_MASSES |  | C | [5 empty] | N | Y
CC | Stiffness Units |  |  | SubSync |  |  | SUBSYNC | STFNS_UNITS |  | C | [5 empty] | N | Y
Transmission | PUN LOAD |  |  | PUN Load |  |  | Not in table | Not in table
Transmission | Station Details |  |  | PUN Load |  |  | Not in table | Not in table
Transmission | Station Code | 03/27/2012 updated | ADDED 06/27/2012 | PUN Load | PUN_LOAD.View | enter all caps | PUN_LOAD | SUBSTATION_CODE | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Not null 3) All caps | C | [5 empty] | N | N
Transmission | Load Name | 03/27/2012 updated | ADDED 06/27/2012 | PUN Load | PUN_LOAD.View | List | PUN_LOAD | PUN_LOAD_NAME | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Value should following the following convention SiteCode_LoadName. Load Name (Load Name) should be as it appears in the ERCOT Model 3) Not Null | L C | Alpha | B |  |  |  | N | N
Transmission | Load Code | 03/27/2012 updated | ADDED 06/27/2012 | PUN Load | PUN_LOAD.View | Automatic | PUN_LOAD | PUN_LOAD_CODE | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Not null | A | Character |  |  |  |  | N | N
Transmission | 168 HR Data |  |  | PUN Load |  |  | Not in table | Not in table
Transmission | Order # |  | Added 05/01/2017 | PUN Load | PUN_LOAD.View | Automatic | PUN_LOAD | ORDER_NUM | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Not null | C A
Transmission | Hour Ending | 03/27/2012 updated | ADDED 06/27/2012 | PUN Load | PUN_LOAD.View | Automatic | PUN_LOAD | HOUR_ENDING | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Not null | A | [5 empty] | N | N
Transmission | Day of Week | 03/27/2012 updated | ADDED 06/27/2012 | PUN Load | PUN_LOAD.View | Automatic | PUN_LOAD | DAY | 1) These fields are conditionally required if "Private Network - Private Network?" = 'Y' and for each Load identified 2) Not Null | A | [5 empty] | N | N
Transmission | MW | 03/27/2012 updated | ADDED 06/27/2012 | PUN Load | PUN_LOAD.View |  | PUN_LOAD | MW | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Not null. Must be numeric. 3) Value must be >= 0 (for zero load, place a 0 in that space) | C | [5 empty] | N | N
Distributed Generation | Unit Info - DG | 04/24/2012 combined into General_Site_ESIID Information sheet |  | Unit Info - DG |  |  | Not in table | Not in table
Distributed Generation | Generator Details |  |  | Unit Info - DG |  |  | Not in table | Not in table
Distributed Generation | Unit Name | Do not show Message on Audit or Delta | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | all caps | NON_MODELED | UNIT_NAME | 1.This field is not null. Data type: Character. 2.All letters should be capital 3. Should not allow spaces | R | Character | B |  |  |  | N/A | N/A |  |  | N/A
Distributed Generation | Unit Code | 06/14/2012 Updated validation to increase to max 17 characters for Unit_Code | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | Automatic | NON_MODELED | UNIT_CODE | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS |  | N/A | N/A |  |  | N/A
Distributed Generation | Unit Dates |  |  | Unit Info - DG |  |  | Not in table | Not in table
Distributed Generation | Unit Start Date |  | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | mm/dd/yyyy | NON_MODELED | UNIT_MRD_ST_DT | This field is not null. Format should be: MM/DD/YYYY | R | Date | B |  |  |  | N/A | N/A |  |  | N/A
Distributed Generation | Unit End Date |  | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | mm/dd/yyyy | NON_MODELED | UNIT_END_DT | This field is optional. Format should be: MM/DD/YYYY | O | Date | B |  |  |  | N/A | N/A |  |  | N/A
Distributed Generation | Fuel Information |  |  | Unit Info - DG |  |  | Not in table | Not in table
Distributed Generation | Name Plate Rating | 05/01/2012 Updated LABEL to MW | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | MW | NON_MODELED | NAME_PLT_RTG_MW | 1. Not Null 2. Numeric Value | R | Numeric | B,DVB |  |  |  | N/A | N/A |  |  | N/A
Distributed Generation | Technology Type | 05/01/2012 UPDATED to match form | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | List | NON_MODELED | TECHNOLOGY_TYPE | 1. Select from drop down list: (FS) Fossil Fuel Steam , (GT) Gas Turbine, (H) Hydro, (W) Wind, (S) Solar, (X) Other 2. Not null | R | Dropdown List | B,DVB |  |  |  | N/A | N/A |  |  | N/A
Distributed Generation | Name Plate Rating |  | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | MVA | NON_MODELED | NAME_PLT_RTG_MVA | 1. Not Null 2. Numeric Value | R | Numeric | B,DVB |  |  |  | N/A | N/A |  |  | N/A
Distributed Generation | Renewable |  | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | Y/N | NON_MODELED | RENEWABLE_FLG | 1. Select from the list: Y or N 2. Not Null | R | Dropdown List | B,DVB |  |  |  | N/A | N/A |  |  | N/A
Distributed Generation | Renewable/Offset |  | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | List | NON_MODELED | RENEWABLE_OFFSET | 1. Select from the list: NA, RN, OS 2. Not Null | R | Dropdown List | B,DVB |  |  |  | N/A | N/A |  |  | N/A
Distributed Generation | If Wind, Number of Turbines |  | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | # | NON_MODELED | NUM_WIND_TURBINES | 1. Data type: Integer 2. N/A is not valid. Leave blank if unknown. | [6 empty] | N/A | N/A |  |  | N/A
Distributed Generation | Physical Unit Type |  | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | List | NON_MODELED | PHYS_UNIT_TYPE | 1. Select from drop down list: CA, CC, CE, CS, CT, FC, GT, HY, IC, NA, OT, PS, PV, ST, WT 2. Not null | R | Dropdown List | B,DVB |  |  |  | N/A | N/A |  |  | N/A
Distributed Generation | Primary Fuel Type |  | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | List | NON_MODELED | PRIM_FUELTYPE | 1. Select from drop down list: AB, BFG, BIT, BL, DFO, GEO, JF, KER, LFG, LIG, MSW, NA, NG, NUC, OBG, OBL, OBS, OG, OO, OTH, PC, PG, RFO, SLW, STM, SUB, SUN, T, TDF, WAT, WDL, WDS, WH, WND, WOC 2. Not null | R | Dropdown List | B,DVB |  |  |  | N/A | N/A |  |  | N/A
Distributed Generation | Secondary Fuel Type |  | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | List | NON_MODELED | SEC_FUELTYPE | 1. Select from drop down list: AB, BFG, BIT, BL, DFO, GEO, JF, KER, LFG, LIG, MSW, NA, NG, NUC, OBG, OBL, OBS, OG, OO, OTH, PC, PG, RFO, SLW, STM, SUB, SUN, T, TDF, WAT, WDL, WDS, WH, WND, WOC 2. Not null | R | Dropdown List | B,DVB |  |  |  | N/A | N/A |  |  | N/A
Distributed Generation | Private Network Info |  | ADDED 06/27/2012 | Unit Info - DG |  |  | Not in table | Not in table
Distributed Generation | Private Network / Cogen |  | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | Y/N | NON_MODELED | PUN_FLG | 1. Select from the list: Y or N 2. Not Null | R | Dropdown List | B,DVB |  |  |  | N/A | N/A |  |  | N/A
Distributed Generation | Amount of Self Serve for Cogen |  | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | MW | NON_MODELED | AMT_SELFSRV_COGEN | Required if Private Network / Cogen is 'Y' | R | Dropdown List | B,DVB |  |  |  | N/A | N/A |  |  | N/A
Distributed Generation | Private Network Net Interchange |  | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | MW | NON_MODELED | PRIVATE_NWK_NET_INTERCHANGE | Required if Private Network / Cogen is 'Y' | R | Dropdown List | B,DVB |  |  |  | N/A | N/A |  |  | N/A
Distributed Generation | Private Network Gross Unit MW |  | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | MW | NON_MODELED | PRIVATE_NET_GROSS_UNT_MW | Required if Private Network / Cogen is 'Y' | R | Dropdown List | B,DVB |  |  |  | N/A | N/A |  |  | N/A
Distributed Generation | Private Network Gross Unit MVAR |  | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | MVAR | NON_MODELED | PRIVATE_NET_GROSS_UNT_MVAR | Required if Private Network / Cogen is 'Y' | R | Dropdown List | B,DVB |  |  |  | N/A | N/A |  |  | N/A
Distributed Generation | Generic Info |  | ADDED 06/27/2012 | Unit Info - DG |  |  | Not in table | Not in table
Distributed Generation | Generic Fuel Category | 05/01/2012 UPDATED to match form 03/9/2012 Corrected Field name | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | List | NON_MODELED | GEN_FUEL_CAT | 1. Select from drop down list: 1) Coal and Lignite 2) Combined Cycle greater than 90 MW 3) Combined Cycle less than or equal to 90 MW 4) Diesel (and all other diesel or gas-fired Resources) 5) Gas Steam Non-reheat Boiler or Boiler without air-preheater 6) Gas Steam Reheat Boiler 7) Gas Steam Supercritical Boiler 8) Hydro 9) Nuclear 10) Other Renewable (i.e. non-hydro renewable Resources) 11) Power Storage 12) Simple Cycle greater 13) Simple Cycle less than or equal to 90 MW 2.Not null | R | Dropdown List | B,DVB |  |  |  | N/A | N/A |  |  | N/A
Distributed Generation | Generic Start-up / Operating Category | 05/01/2012 UPDATED to match form 03/9/2012 Corrected Field name | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | List | NON_MODELED | GEN_STUP_OPER_CAT | 1. Select from drop down list: 1) Base Load 2) Gas-Cyclic 3) Gas-Intermediate 4) Gas-Peaking 5) Renewable (Including Hydro) 2. Not null | R | Dropdown List | B,DVB |  |  |  | N/A | N/A |  |  | N/A
Distributed Generation | Resource Owner Data |  |  | Unit Info - DG |  |  | Not in table | Not in table
Distributed Generation | Resource Entity Name |  | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View | all caps | NON_MODELED | RE_NAME | 1. Not null 2. Do not allow any special characters except spaces and dashes. | R | Character | B,DVE |  |  |  | N/A | N/A |  |  | N/A
Distributed Generation | Resource Entity Duns Number |  | ADDED 06/27/2012 | Unit Info - DG | DG_UnitInfo.View |  | NON_MODELED | RE_DUNS | 1. Not null 2. Must match with the data existing in Siebel 3. Data type: varchar (as sometimes the value contains # with a leading zero) 4. Either a 9 or 13 digit DUNS number | R | Character | B,DVE |  |  |  | N/A | N/A |  |  | N/A
Note on F6: This column represents the name of the SQL file/view that uses the field. The name is the same for Delta and Aufit reports unless otherwise noted. The full filename convention is dbo.[RARFAUDIT or DELTA].[Source Report Name].sql
Note on B142: Concatenated mnemonic of Resource Site Code and Unit name from http://www.ercot.com/gridinfo/generation/Resource_Site_Name_to_Mnemonic_Dictionary.xls

## DATA CATALOG (hidden)
Column Name | DB Schema | Table Name | Description | Column Description | Added or Updated | Description
CHANGE_DESCRIPTION | RARF_HUB | BREAKER_SWITCH | Latest approved Breaker/Switch Equipment details. | Description of Change, indicates if new Equipment is added; Existing Equipment is deleted or Updated |  | Latest approved Breaker/Switch Equipment details.
COMMENTS_BRKRSWITCH | RARF_HUB | BREAKER_SWITCH |  | General comments on the Breaker/Switch Equipment
DATE_LOADED | RARF_HUB | BREAKER_SWITCH |  | Date when the RARF is loaded into the Database.(MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | BREAKER_SWITCH |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
EFF_DATE | RARF_HUB | BREAKER_SWITCH |  | Date when the Equipment will be effective in Model (MM/DD/YYYY Format).
FAULT_ISO_DEV_FLG | RARF_HUB | BREAKER_SWITCH |  | Indicates if it is a Fault Isolating Device (e.g. Circuit Breaker).
NORM_OP_STATUS | RARF_HUB | BREAKER_SWITCH |  | Normally Open / Normally Closed.
OP_STATUS_REQ | RARF_HUB | BREAKER_SWITCH |  | This column is not being used.
SITE_CODE | RARF_HUB | BREAKER_SWITCH |  | Unique Code for Resource Site (e.g.: CBY)
SUBSTATION_CODE | RARF_HUB | BREAKER_SWITCH |  | Unique Code for Substation in a Site (e.g.: HHGT Site has CALLAHAN AND HHGT SUBSTATIONS)
SWITCH_CODE | RARF_HUB | BREAKER_SWITCH |  | Unique Code for each Breaker/switch which is the concatenation of SITE_CODE_SUBSTATIONCODE_SWITCH NAME.
SWITCH_NAME | RARF_HUB | BREAKER_SWITCH |  | Switch Name.
VOLT_LVL | RARF_HUB | BREAKER_SWITCH |  | Nominal voltage in KV.
CONTINUOUS_RTG | RARF_HUB | BREAKER_SWITCH |  | Continuous Rating | Added 06/27/2012
EMGCY_RTG_2HR | RARF_HUB | BREAKER_SWITCH |  | 2-hr Emergency Rating | Added 06/27/2012
RTG_15MIN | RARF_HUB | BREAKER_SWITCH |  | 15 Min Rating | Added 06/27/2012
APPROVED_DATE | RARF_HUB | BREAKER_SWITCH_HIST | History Table: ALL approved and Disapproved Breaker/Switch Equipment details. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: ALL approved and Disapproved Breaker/Switch Equipment details.
CHANGE_DESCRIPTION | RARF_HUB | BREAKER_SWITCH_HIST |  | Description of Change, indicates if new Equipment is added; Existing Equipment is deleted or Updated
COMMENTS_BRKRSWITCH | RARF_HUB | BREAKER_SWITCH_HIST |  | General comments on the Breaker/Switch Equipment
DATE_LOADED | RARF_HUB | BREAKER_SWITCH_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | BREAKER_SWITCH_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
EFF_DATE | RARF_HUB | BREAKER_SWITCH_HIST |  | Date when the Equipment will be effective in Model. (MM/DD/YYYY Format).
FAULT_ISO_DEV_FLG | RARF_HUB | BREAKER_SWITCH_HIST |  | Indicates if it is a Fault Isolating Device (e.g. Circuit Breaker).
NORM_OP_STATUS | RARF_HUB | BREAKER_SWITCH_HIST |  | Normally Open / Normally Closed.
OP_STATUS_REQ | RARF_HUB | BREAKER_SWITCH_HIST |  | This column is not being used.
SITE_CODE | RARF_HUB | BREAKER_SWITCH_HIST |  | Unique Code for Resource Site (e.g.: CBY).
SUBMISSION_TYPE | RARF_HUB | BREAKER_SWITCH_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
SUBSTATION_CODE | RARF_HUB | BREAKER_SWITCH_HIST |  | Unique Code for Substation in a Site (e.g.: HHGT Site has CALLAHAN AND HHGT SUBSTATIONS)
SWITCH_CODE | RARF_HUB | BREAKER_SWITCH_HIST |  | Unique Code for each Breaker/switch which is the concatenation of SITE_CODE_SUBSTATIONCODE_SWITCH NAME.
SWITCH_NAME | RARF_HUB | BREAKER_SWITCH_HIST |  | Switch Name.
VOLT_LVL | RARF_HUB | BREAKER_SWITCH_HIST |  | Nominal voltage in KV.
CONTINUOUS_RTG | RARF_HUB | BREAKER_SWITCH_HIST |  | Continuous Rating | Added 06/27/2012
EMGCY_RTG_2HR | RARF_HUB | BREAKER_SWITCH_HIST |  | 2-hr Emergency Rating | Added 06/27/2012
RTG_15MIN | RARF_HUB | BREAKER_SWITCH_HIST |  | 15 Min Rating | Added 06/27/2012
CABLE_SEG_DATA_FROM | RARF_HUB | CABLE_SEG_DATA |  | From | Added 06/27/2012 | Latest approved Cable Segment Data details.
CABLE_SEG_DATA_TO | RARF_HUB | CABLE_SEG_DATA |  | To | Added 06/27/2012
CABLE_SEG_LENTH | RARF_HUB | CABLE_SEG_DATA |  | Cable Segment Length | Added 06/27/2012
CABLE_TYPE | RARF_HUB | CABLE_SEG_DATA |  | Cable Type | Added 06/27/2012
CIRCT_NUM | RARF_HUB | CABLE_SEG_DATA |  | Circuit Number | Added 06/27/2012
NUM_TURBIN_ON_CABLE_SEG | RARF_HUB | CABLE_SEG_DATA |  | Number of Turbines on cable segment | Added 06/27/2012
VT_LEVL | RARF_HUB | CABLE_SEG_DATA |  | Voltage Level | Added 06/27/2012
CABLE_SEG_DATA_FROM | RARF_HUB | CABLE_SEG_DATA_HIST |  | From | Added 06/27/2012 | History Table: ALL approved and Disapproved Cable Segment Data details
CABLE_SEG_DATA_TO | RARF_HUB | CABLE_SEG_DATA_HIST |  | To | Added 06/27/2012
CABLE_SEG_LENTH | RARF_HUB | CABLE_SEG_DATA_HIST |  | Cable Segment Length | Added 06/27/2012
CABLE_TYPE | RARF_HUB | CABLE_SEG_DATA_HIST |  | Cable Type | Added 06/27/2012
CIRCT_NUM | RARF_HUB | CABLE_SEG_DATA_HIST |  | Circuit Number | Added 06/27/2012
NUM_TURBIN_ON_CABLE_SEG | RARF_HUB | CABLE_SEG_DATA_HIST |  | Number of Turbines on cable segment | Added 06/27/2012
VT_LEVL | RARF_HUB | CABLE_SEG_DATA_HIST |  | Voltage Level | Added 06/27/2012
DATE_LOADED | RARF_HUB | BREAKER_SWITCH_SIDE | Latest approved Breaker/Switch Connected Devices details. | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format). |  | Latest approved Breaker/Switch Connected Devices details.
DATE_SUBMITTED | RARF_HUB | BREAKER_SWITCH_SIDE |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DEVICE_NAME | RARF_HUB | BREAKER_SWITCH_SIDE |  | Directly connected device name.
SIDE | RARF_HUB | BREAKER_SWITCH_SIDE |  | SIDE ( 1 OR 2).
SWITCH_CODE | RARF_HUB | BREAKER_SWITCH_SIDE |  | Unique Code for each Breaker/switch which is the concatenation of SITE_CODE_SUBSTATIONCODE_SWITCH NAME.
APPROVED_DATE | RARF_HUB | BREAKER_SWITCH_SIDE_HIST | History Table: ALL approved and Disapproved Breaker/Switch Equipment details. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: ALL approved and Disapproved Breaker/Switch Equipment details.
DATE_LOADED | RARF_HUB | BREAKER_SWITCH_SIDE_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | BREAKER_SWITCH_SIDE_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DEVICE_NAME | RARF_HUB | BREAKER_SWITCH_SIDE_HIST |  | Connected Device Name.
SIDE | RARF_HUB | BREAKER_SWITCH_SIDE_HIST |  | SIDE ( 1 OR 2).
SUBMISSION_TYPE | RARF_HUB | BREAKER_SWITCH_SIDE_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
SWITCH_CODE | RARF_HUB | BREAKER_SWITCH_SIDE_HIST |  | Unique Code for each Breaker/switch which is the concatenation of SITE_CODE_SUBSTATIONCODE_SWITCH NAME.
AUTO_VOLT_FLG | RARF_HUB | CAPREACT | Latest Approved Capacitor/Reactor Equipment details. | Automatic Voltage Regulation Flag (Y or N). |  | Latest Approved Capacitor/Reactor Equipment details.
BUSBAR_VOLT | RARF_HUB | CAPREACT |  | Voltage Level of Bus bar being regulated.
CAPACITOR_REACTOR_FLG | RARF_HUB | CAPREACT |  | Capacitor or Reactor (C/R),Indicate which device
CHANGE_DESCRIPTION | RARF_HUB | CAPREACT |  | Description of Change, indicates if new Equipment is added; Existing Equipment is deleted or Updated
COMMENTS_CAPREACT | RARF_HUB | CAPREACT |  | General comments on the Capacitor/Reactor Equipment
DATE_LOADED | RARF_HUB | CAPREACT |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | CAPREACT |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DES_REG_VOLT | RARF_HUB | CAPREACT |  | Desired Regulating voltage.
DEVICE_CODE | RARF_HUB | CAPREACT |  | Unique Code for each Capacitor/Reactor which is the concatenation of SITE_CODE_SUBSTATIONCODE_DEVICE_NAME.
DEVICE_NAME | RARF_HUB | CAPREACT |  | DEVICE NAME.
EFF_DATE | RARF_HUB | CAPREACT |  | Date when the Equipment will be effective in Model
MAX_REG_VOLT | RARF_HUB | CAPREACT |  | Maximum Regulating Voltage.
MIN_REG_VOLT | RARF_HUB | CAPREACT |  | Minimum Regulating Voltage.
NOMINAL_MVAR | RARF_HUB | CAPREACT |  | MVAR at nominal voltage.
PTI_BUSNUM | RARF_HUB | CAPREACT |  | ERCOT PTI bus number.
SITE_CODE | RARF_HUB | CAPREACT |  | Unique Code for Resource Site (e.g.: CBY).
SUBSTATION_CODE | RARF_HUB | CAPREACT |  | Unique Code for Substation in a Site (e.g.: HHGT Site has CALLAHAN AND HHGT SUBSTATIONS).
VOLT_LVL_KV | RARF_HUB | CAPREACT |  | Voltage Level Kv.
ZERO_SEQ_REACTANCE_INCRMENT_PU | RARF_HUB | CAPREACT |  | Zero Sequence Reactance Increment In p.u. | Added 06/27/2012
CONNECTED_DEVICE_NAME | RARF_HUB | CAPREACT_DEVICE | Latest Approved Capacitor/Reactor Equipment details. | Connected Device Name. |  | Latest Approved Capacitor/Reactor Equipment details.
DATE_LOADED | RARF_HUB | CAPREACT_DEVICE |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | CAPREACT_DEVICE |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DEVICE_CODE | RARF_HUB | CAPREACT_DEVICE |  | Unique Code for each Capacitor/Reactor which is the concatenation of SITE_CODE_SUBSTATIONCODE_DEVICE_NAME.
APPROVED_DATE | RARF_HUB | CAPREACT_DEVICE_HIST | History Table: ALL approved and Disapproved Capacitor/Reactor Equipment details. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: ALL approved and Disapproved Capacitor/Reactor Equipment details.
CONNECTED_DEVICE_NAME | RARF_HUB | CAPREACT_DEVICE_HIST |  | Connected Device Name.
DATE_LOADED | RARF_HUB | CAPREACT_DEVICE_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | CAPREACT_DEVICE_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DEVICE_CODE | RARF_HUB | CAPREACT_DEVICE_HIST |  | Unique Code for each Capacitor/Reactor which is the concatenation of SITE_CODE_SUBSTATIONCODE_DEVICE_NAME.
SUBMISSION_TYPE | RARF_HUB | CAPREACT_DEVICE_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
AUTO_VOLT_FLG | RARF_HUB | CAPREACT_HIST | History Table: ALL approved and Disapproved Capacitor/Reactor Equipment details. | Automatic Voltage Regulation Flag (Y or N). |  | History Table: ALL approved and Disapproved Capacitor/Reactor Equipment details.
BUSBAR_VOLT | RARF_HUB | CAPREACT_HIST |  | Voltage Level of Bus bar being regulated.
CAPACITOR_REACTOR_FLG | RARF_HUB | CAPREACT_HIST |  | Capacitor or Reactor (C/R),Indicate which device
CHANGE_DESCRIPTION | RARF_HUB | CAPREACT_HIST |  | Description of Change, indicates if new Equipment is added; Existing Equipment is deleted or Updated
COMMENTS_CAPREACT | RARF_HUB | CAPREACT_HIST |  | General comments on the Capacitor/Reactor Equipment
DATE_LOADED | RARF_HUB | CAPREACT_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | CAPREACT_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DES_REG_VOLT | RARF_HUB | CAPREACT_HIST |  | Desired Regulating voltage.
DEVICE_CODE | RARF_HUB | CAPREACT_HIST |  | Unique Code for each Capacitor/Reactor which is the concatenation of SITE_CODE_SUBSTATIONCODE_DEVICE_NAME.
DEVICE_NAME | RARF_HUB | CAPREACT_HIST |  | DEVICE NAME.
EFF_DATE | RARF_HUB | CAPREACT_HIST |  | Date when the Equipment will be effective in Model
MAX_REG_VOLT | RARF_HUB | CAPREACT_HIST |  | Maximum Regulating Voltage.
MIN_REG_VOLT | RARF_HUB | CAPREACT_HIST |  | Minimum Regulating Voltage.
NOMINAL_MVAR | RARF_HUB | CAPREACT_HIST |  | MVAR at nominal voltage.
PTI_BUSNUM | RARF_HUB | CAPREACT_HIST |  | ERCOT PTI bus number.
SITE_CODE | RARF_HUB | CAPREACT_HIST |  | Unique Code for Resource Site (e.g.: CBY).
SUBSTATION_CODE | RARF_HUB | CAPREACT_HIST |  | Unique Code for Substation in a Site (e.g.: HHGT Site has CALLAHAN AND HHGT SUBSTATIONS).
VOLT_LVL_KV | RARF_HUB | CAPREACT_HIST |  | Voltage Level Kv.
ZERO_SEQ_REACTANCE_INCRMENT_PU | RARF_HUB | CAPREACT_HIST |  | Zero Sequence Reactance Increment In p.u. | Added 06/27/2012
ARMATURE_Z_R_PU | RARF_HUB | CCUNIT | Latest Approved Combined Cycle unit information. | Stator impedance value (R in P.U). |  | Latest Approved Combined Cycle unit information.
ARMATURE_Z_X_PU | RARF_HUB | CCUNIT |  | Stator impedance value (X in P.U).
AUX_MVARTOTAL | RARF_HUB | CCUNIT |  | Average MVAR for Auxiliary Load.
AUX_MWTOTAL | RARF_HUB | CCUNIT |  | Average MW for Auxiliary Load.
AUXMVAR_DISCHARGE_PCT | RARF_HUB | CCUNIT |  | Generation Auxiliary Load Characteristics for MVAR Load - Discharge Lighting, percent of total MVAR load.
AUXMVAR_LARGEMTR_PCT | RARF_HUB | CCUNIT |  | Generation Auxiliary Load Characteristics for MVAR Load - Large Motor, percent of total MVAR load.
AUXMVAR_OTHER_PCT | RARF_HUB | CCUNIT |  | Generation Auxiliary Load Characteristics for MVAR Load - Other, percent of total MVAR load.
AUXMVAR_SMALLMTR_PCT | RARF_HUB | CCUNIT |  | Generation Auxiliary Load Characteristics for MVAR Load - Small Motor, percent of total MVAR load.
AUXMW_DISCHARGE_PCT | RARF_HUB | CCUNIT |  | Generation Auxiliary Load Characteristics for MW Load - Discharge Lighting, percent of total MW load.
AUXMW_LARGEMTR_PCT | RARF_HUB | CCUNIT |  | Generation Auxiliary Load Characteristics for MW Load - Large Motor, percent of total MW load.
AUXMW_OTHER_PCT | RARF_HUB | CCUNIT |  | Generation Auxiliary Load Characteristics for MW Load - Other, percent of total MW load.
AUXMW_RESISTIVE_PCT | RARF_HUB | CCUNIT |  | Generation Auxiliary Load Characteristics for MW Load - Resistive (Heating) Load, percent of total MW load.
AUXMW_SMALLMTR_PCT | RARF_HUB | CCUNIT |  | Generation Auxiliary Load Characteristics for MW Load - Small Motor, percent of total MW load.
AVG_LD_MVAR_UNIT | RARF_HUB | CCUNIT |  | Average Amount of Auxiliary Reactive Power.
AVG_LD_MW_UNIT | RARF_HUB | CCUNIT |  | Average Amount of Auxiliary Real Power.
BREAKER_INTERRUP | RARF_HUB | CCUNIT |  | Breaker Interruption Time.
COMPSTR_FLG | RARF_HUB | CCUNIT |  | This column is not being used.
COMPSTR_FORM_FLG | RARF_HUB | CCUNIT |  | This column is not being used.
DATE_LOADED | RARF_HUB | CCUNIT |  | Date when the RARF is loaded into the Database
DATE_SUBMITTED | RARF_HUB | CCUNIT |  | Date when the RARF is submitted to ERCOT for processing
DIRECT_AXIS_SUBSTNT_REACTANCE | RARF_HUB | CCUNIT |  | Direct Axis Sub transient reactance, X"di.
DIRECT_AXIS_TRANSNT_REACTANCE | RARF_HUB | CCUNIT |  | Direct Axis Transient reactance, X'di.
ERCOT_INTRCONN_PROJ_NUM | RARF_HUB | CCUNIT |  | ERCOT Interconnection Project Number.
EXCITN_FORM_FLG | RARF_HUB | CCUNIT |  | This column is not being used.
GEN_FORM_FLG | RARF_HUB | CCUNIT |  | This column is not being used.
GROSS_CAPBLTY_MVAR_UNIT | RARF_HUB | CCUNIT |  | Gross Capability (MVAR).
GROSS_CAPBLTY_MW_UNIT | RARF_HUB | CCUNIT |  | Gross Capability (MW).
HR_LMT | RARF_HUB | CCUNIT |  | High Reasonability Limit.
HR_RAMPRATE_LMT | RARF_HUB | CCUNIT |  | High Reasonability Ramp Rate limit.
HYDROCOOLED | RARF_HUB | CCUNIT |  | hydro cooled.
KVBASE | RARF_HUB | CCUNIT |  | What is the kV base that the following data is based on?.
LOAD_TRIP_FLG | RARF_HUB | CCUNIT |  | Load Trip Flag.
LOAD_TRIP_PCT | RARF_HUB | CCUNIT |  | Load Trip percent.
LR_LMT | RARF_HUB | CCUNIT |  | Low Reasonability Limit.
LR_RAMP_RATE_LMT | RARF_HUB | CCUNIT |  | Low Reasonability Ramp rate Limit.
MACHINE_IMPEDANCE_R_PU | RARF_HUB | CCUNIT |  | This column is not being used.
MACHINE_IMPEDANCE_X_PU | RARF_HUB | CCUNIT |  | This column is not being used.
MFR_CAPABILITY_CURVE_FLG | RARF_HUB | CCUNIT |  | Manufactured Capability Curve Flag.
MUTUAL_COUPLING_Z_R_PU | RARF_HUB | CCUNIT |  | This column is not being used.
MUTUAL_COUPLING_Z_X_PU | RARF_HUB | CCUNIT |  | This column is not being used.
MVABASE | RARF_HUB | CCUNIT |  | What is the MVA base that the following data is based on?.
MVAR1LAG_GEN | RARF_HUB | CCUNIT |  | Unit's Lagging reactive power output capability associated with its MW1 output, in MVAR
MVAR1LEAD_GEN | RARF_HUB | CCUNIT |  | Unit's Leading reactive power output capability associated with its MW1 output, in MVAR; input as negative number.
MVAR2LAG_GEN | RARF_HUB | CCUNIT |  | Unit's Lagging reactive power output capability associated with its MW2 output, in MVAR
MVAR2LEAD_GEN | RARF_HUB | CCUNIT |  | Unit's Leading reactive power output capability associated with its MW2 output, in MVAR; input as negative number.
MVAR3LAG_GEN | RARF_HUB | CCUNIT |  | Unit's Lagging reactive power output capability associated with its MW3 output, in MVAR
MVAR3LEAD_GEN | RARF_HUB | CCUNIT |  | Unit's Leading reactive power output capability associated with its MW3 output, in MVAR; input as negative number.
MVAR4LAG_GEN | RARF_HUB | CCUNIT |  | Unit's Lagging reactive power output capability associated with its MW4 output, in MVAR
MVAR4LEAD_GEN | RARF_HUB | CCUNIT |  | Unit's Leading reactive power output capability associated with its MW4 output, in MVAR; input as negative number.
MW1_GEN | RARF_HUB | CCUNIT |  | Reactive Capability curve - point on curve of MW output for this unit, MW1.
MW2_GEN | RARF_HUB | CCUNIT |  | Reactive Capability curve - point on curve of MW output for this unit, MW2.
MW3_GEN | RARF_HUB | CCUNIT |  | Reactive Capability curve - point on curve of MW output for this unit, MW3.
MW4_GEN | RARF_HUB | CCUNIT |  | Reactive Capability curve - point on curve of MW output for this unit, MW4.
MW5UNITYPF_GEN | RARF_HUB | CCUNIT |  | From the Reactive Capability curve - the MW output at Unity Power Factor (zero MVAR).
NAME_PLT_RTG | RARF_HUB | CCUNIT |  | Name Plate Rating of the Unit.
NEGATIVE_SEQ_Z_R_PU | RARF_HUB | CCUNIT |  | Negative Sequence Z ( R in P.U).
NEGATIVE_SEQ_Z_X_PU | RARF_HUB | CCUNIT |  | Negative Sequence Z ( X in P.U).
NET_INTERCHNG_MVAR_UNIT | RARF_HUB | CCUNIT |  | Unit's Net interchange MVAR.
NET_INTERCHNG_MW_UNIT | RARF_HUB | CCUNIT |  | Unit's Net interchange MVW.
NETMAXLAG_GEN | RARF_HUB | CCUNIT |  | Net Maximum Lagging Operating Capability (MVAR).
NETMAXLEAD_GEN | RARF_HUB | CCUNIT |  | Net Maximum Leading Operating Capability (MVAR).
OFREQ_TRIP_HZ1 | RARF_HUB | CCUNIT |  | Over frequency Protection Setting- HZ1.
OFREQ_TRIP_HZ2 | RARF_HUB | CCUNIT |  | Over frequency Protection Setting- HZ2.
OFREQ_TRIP_HZ3 | RARF_HUB | CCUNIT |  | Over frequency Protection Setting- HZ3.
OFREQ_TRIP_HZ4 | RARF_HUB | CCUNIT |  | Over frequency Protection Setting- HZ4.
OFREQ_TRIP_INSTANT | RARF_HUB | CCUNIT |  | Instantaneous Over frequency Trip.
OFREQ_TRIP_TIME1 | RARF_HUB | CCUNIT |  | Over frequency Protection Setting- TIME1.
OFREQ_TRIP_TIME2 | RARF_HUB | CCUNIT |  | Over frequency Protection Setting- TIME2.
OFREQ_TRIP_TIME3 | RARF_HUB | CCUNIT |  | Over frequency Protection Setting- TIME3.
OFREQ_TRIP_TIME4 | RARF_HUB | CCUNIT |  | Over frequency Protection Setting- TIME4.
OVER_EXCITN_LIMITER_FLG | RARF_HUB | CCUNIT |  | This column is not being used.
OVER_EXCITN_LIMITER_FORM_FLG | RARF_HUB | CCUNIT |  | This column is not being used.
OVOLT_TRIP_INSTANT | RARF_HUB | CCUNIT |  | Instantaneous voltage setting for overvoltage protection(kv).
OVOLT_TRIP_TIME1 | RARF_HUB | CCUNIT |  | Overvoltage Trip Time setting 1.
OVOLT_TRIP_TIME2 | RARF_HUB | CCUNIT |  | Overvoltage Trip Time setting 2.
OVOLT_TRIP_TIME3 | RARF_HUB | CCUNIT |  | Overvoltage Trip Time setting 3.
OVOLT_TRIP_TIME4 | RARF_HUB | CCUNIT |  | Overvoltage Trip Time setting 4.
OVOLT_TRIP_VOLT1 | RARF_HUB | CCUNIT |  | Overvoltage Trip Voltage setting 1.
OVOLT_TRIP_VOLT2 | RARF_HUB | CCUNIT |  | Overvoltage Trip Voltage setting 2.
OVOLT_TRIP_VOLT3 | RARF_HUB | CCUNIT |  | Overvoltage Trip Voltage setting 3.
OVOLT_TRIP_VOLT4 | RARF_HUB | CCUNIT |  | Overvoltage Trip Voltage setting 4.
PHYS_UNIT_TYPE | RARF_HUB | CCUNIT |  | Physical Unit Type.
POSITIVE_SEQ_Z_R_PU | RARF_HUB | CCUNIT |  | Positive Sequence Z ( R in P.U).
POSITIVE_SEQ_Z_X_PU | RARF_HUB | CCUNIT |  | Positive Sequence Z ( X in P.U).
PRIM_FUELTYPE | RARF_HUB | CCUNIT |  | Primary Fuel type for the Unit.
PSS_FLG | RARF_HUB | CCUNIT |  | This column is not being used.
PSSFORM_FLG | RARF_HUB | CCUNIT |  | This column is not being used.
ROTOR_Z_R_PU | RARF_HUB | CCUNIT |  | This column is not being used.
ROTOR_Z_X_PU | RARF_HUB | CCUNIT |  | This column is not being used.
RTG_MVAR | RARF_HUB | CCUNIT |  | Reactive Power Rating.
RTG_MW | RARF_HUB | CCUNIT |  | Real Power Rating.
SEASON_NET_MAX_EMGY_RTG_FL | RARF_HUB | CCUNIT |  | Seasonal Net Maximum Emergency Rating -Fall (MW).
SEASON_NET_MAX_EMGY_RTG_SM | RARF_HUB | CCUNIT |  | Seasonal Net Maximum Emergency Rating -Summer (MW).
SEASON_NET_MAX_EMGY_RTG_SP | RARF_HUB | CCUNIT |  | Seasonal Net Maximum Emergency Rating -Spring (MW).
SEASON_NET_MAX_EMGY_RTG_WT | RARF_HUB | CCUNIT |  | Seasonal Net Maximum Emergency Rating -Winter (MW).
SEASON_NET_MAX_SUST_RTG_FL | RARF_HUB | CCUNIT |  | Seasonal Net Maximum Sustainable Rating -Fall (MW).
SEASON_NET_MAX_SUST_RTG_SM | RARF_HUB | CCUNIT |  | Seasonal Net Maximum Sustainable Rating -Summer (MW).
SEASON_NET_MAX_SUST_RTG_SP | RARF_HUB | CCUNIT |  | Seasonal Net Maximum Sustainable Rating -Spring (MW).
SEASON_NET_MAX_SUST_RTG_WT | RARF_HUB | CCUNIT |  | Seasonal Net Maximum Sustainable Rating -Winter (MW).
SEASON_NET_MIN_EMGY_RTG_FL | RARF_HUB | CCUNIT |  | Seasonal Net Minimum Emergency Rating -Fall (MW).
SEASON_NET_MIN_EMGY_RTG_SM | RARF_HUB | CCUNIT |  | Seasonal Net Minimum Emergency Rating -Summer (MW).
SEASON_NET_MIN_EMGY_RTG_SP | RARF_HUB | CCUNIT |  | Seasonal Net Minimum Emergency Rating -Spring (MW).
SEASON_NET_MIN_EMGY_RTG_WT | RARF_HUB | CCUNIT |  | Seasonal Net Minimum Emergency Rating -Winter (MW).
SEASON_NET_MIN_SUST_RTG_FL | RARF_HUB | CCUNIT |  | Seasonal Net Minimum Sustainable Rating -Fall (MW).
SEASON_NET_MIN_SUST_RTG_SM | RARF_HUB | CCUNIT |  | Seasonal Net Minimum Sustainable Rating - Summer (MW).
SEASON_NET_MIN_SUST_RTG_SP | RARF_HUB | CCUNIT |  | Seasonal Net Minimum Sustainable Rating - Spring (MW).
SEASON_NET_MIN_SUST_RTG_WT | RARF_HUB | CCUNIT |  | Seasonal Net Minimum Sustainable Rating - Winter (MW).
SEC_FUELTYPE | RARF_HUB | CCUNIT |  | Secondary Fuel Type.
SITE_CODE | RARF_HUB | CCUNIT |  | Unique Code for Resource Site (e.g.: CBY)
TURB_GOVNR_FORM_FLG | RARF_HUB | CCUNIT |  | This column is not being used.
TURBINE_RTG | RARF_HUB | CCUNIT |  | Turbine Rating.
UFREQ_TRIP_HZ1 | RARF_HUB | CCUNIT |  | Under frequency Protection Setting- HZ1.
UFREQ_TRIP_HZ2 | RARF_HUB | CCUNIT |  | Under frequency Protection Setting- HZ2.
UFREQ_TRIP_HZ3 | RARF_HUB | CCUNIT |  | Under frequency Protection Setting- HZ3.
UFREQ_TRIP_HZ4 | RARF_HUB | CCUNIT |  | Under frequency Protection Setting- HZ4.
UFREQ_TRIP_INSTANT | RARF_HUB | CCUNIT |  | Instantaneous Under frequency Trip.
UFREQ_TRIP_TIME1 | RARF_HUB | CCUNIT |  | Under frequency Protection Setting- TIME1.
UFREQ_TRIP_TIME2 | RARF_HUB | CCUNIT |  | Under frequency Protection Setting- TIME2.
UFREQ_TRIP_TIME3 | RARF_HUB | CCUNIT |  | Under frequency Protection Setting- TIME3.
UFREQ_TRIP_TIME4 | RARF_HUB | CCUNIT |  | Under frequency Protection Setting- TIME4.
UNDER_EXCITN_LIMITER_FLG | RARF_HUB | CCUNIT |  | This column is not being used.
UNDER_EXCITN_LIMITER_FORM_FLG | RARF_HUB | CCUNIT |  | This column is not being used.
UNIT_CODE | RARF_HUB | CCUNIT |  | Concatenated Mnemonic of Resource Site Code and Unit name (e.g CBY_CBYG1).
UNIT_END_DT | RARF_HUB | CCUNIT |  | Unit Termination Date( MM/DD/YYYY ).
UNIT_KV | RARF_HUB | CCUNIT |  | Unit Generating Voltage.
UNIT_NAME | RARF_HUB | CCUNIT |  | Unit Name.
UNIT_START_DT | RARF_HUB | CCUNIT |  | Unit Commercial Operations Date. It is the date on which Generator declares that the construction of the Plant has been substantially completed, Trial Operation of the Plant has been completed, and the Plant is ready for dispatch. Format is MM/DD/YYYY.
UVOLT_TRIP_INSTANT | RARF_HUB | CCUNIT |  | Instantaneous Under voltage Trip.
UVOLT_TRIP_TIME1 | RARF_HUB | CCUNIT |  | Under Voltage Protection Setting- TIME1.
UVOLT_TRIP_TIME2 | RARF_HUB | CCUNIT |  | Under Voltage Protection Setting- TIME2.
UVOLT_TRIP_TIME3 | RARF_HUB | CCUNIT |  | Under Voltage Protection Setting- TIME3.
UVOLT_TRIP_TIME4 | RARF_HUB | CCUNIT |  | Under Voltage Protection Setting- TIME4.
UVOLT_TRIP_VOLT1 | RARF_HUB | CCUNIT |  | Under Voltage Protection Setting- VOLT1.
UVOLT_TRIP_VOLT2 | RARF_HUB | CCUNIT |  | Under Voltage Protection Setting- VOLT2.
UVOLT_TRIP_VOLT3 | RARF_HUB | CCUNIT |  | Under Voltage Protection Setting- VOLT3.
UVOLT_TRIP_VOLT4 | RARF_HUB | CCUNIT |  | Under Voltage Protection Setting- VOLT4.
ZERO_SEQ_Z_R_PU | RARF_HUB | CCUNIT |  | Zero Sequence Z ( R in P.U).
ZERO_SEQ_Z_X_PU | RARF_HUB | CCUNIT |  | zero Sequence Z ( X in P.U).
AUX_LOAD_PWR_FACT | RARF_HUB | CCUNIT |  | Auxiliary Load Power Factor | Added 06/27/2012
DESIGN_MAX_AMB_TEMP | RARF_HUB | CCUNIT |  | Design Max Ambient Temperature | Added 06/27/2012
DESIGN_MIN_AMB_TEMP | RARF_HUB | CCUNIT |  | Design Min Ambient Temperature | Added 06/27/2012
DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED | RARF_HUB | CCUNIT |  | Direct Axis Subtransient Reactance, X"dv (saturated) | Added 06/27/2012
DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED | RARF_HUB | CCUNIT |  | Direct Axis Transient Reactance, X'dv (saturated) | Added 06/27/2012
DOES_ZERO_SEQ_EXIST | RARF_HUB | CCUNIT |  | Does Zero Sequence Z exist? | Added 06/27/2012
GOV_DEAD_BND | RARF_HUB | CCUNIT |  | Governor Dead-band | Added 06/27/2012
GOV_DROOP | RARF_HUB | CCUNIT |  | Governor Droop Setting | Added 06/27/2012
NEGATIVE_SEQ_Z_R_PU | RARF_HUB | CCUNIT |  | Negative Sequence Z (saturated) | Added 06/27/2012
NEGATIVE_SEQ_Z_X_PU | RARF_HUB | CCUNIT |  | Negative Sequence Z (saturated) | Added 06/27/2012
POSITIVE_SEQ_Z_R_PU | RARF_HUB | CCUNIT |  | Positive Sequence Z (saturated) | Added 06/27/2012
POSITIVE_SEQ_Z_X_PU | RARF_HUB | CCUNIT |  | Positive Sequence Z (saturated) | Added 06/27/2012
PTI_BUS_NUM | RARF_HUB | CCUNIT |  | PTI Bus Number | Added 06/27/2012
REACT_CAPB_DATA_GROSS_VAL | RARF_HUB | CCUNIT |  | Reactive Capability Data Provided is Gross Values? | Added 06/27/2012
REACT_CAPB_NDCRC_TEST_DATA | RARF_HUB | CCUNIT |  | Reactive Capability Data Provided is from NDCRC Test Data? | Added 06/27/2012
REACT_CAPB_NDCRC_TEST_DATA_DT | RARF_HUB | CCUNIT |  | If Reactive Capability Data Provided Is From NDCRC test Data Then Enter The Date On Which The Test Was Performed. | Added 06/27/2012
SGIA_SIG_DT | RARF_HUB | CCUNIT |  | Standard Generation Interconnection Agreement (SGIA) Signature Date | Added 06/27/2012
SUBSTAT_CODE_SUB_MNEMONIC | RARF_HUB | CCUNIT |  | SubStation Code/SubStation Mnemonic | Added 06/27/2012
TRANS_ONLY_DT | RARF_HUB | CCUNIT |  | Transmission Only Date (POI) | Added 06/27/2012
UNIT_MRD_ST_DT | RARF_HUB | CCUNIT |  | Unit Start Date (Model Ready Date) | Added 06/27/2012
VOL_LEV | RARF_HUB | CCUNIT |  | Voltage Level | Added 06/27/2012
ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU | RARF_HUB | CCUNIT |  | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Added 06/27/2012
ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU | RARF_HUB | CCUNIT |  | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Added 06/27/2012
ZERO_SEQ_Z_R_PU | RARF_HUB | CCUNIT |  | Zero Sequence Z (saturated) | Added 06/27/2012
ZERO_SEQ_Z_X_PU | RARF_HUB | CCUNIT |  | Zero Sequence Z (saturated) | Added 06/27/2012
CONFIG_CODE | RARF_HUB | CCUNIT_CONFIGURATION | Latest Approved combined Cycle Configurations Details. | Unique Code for Each Configuration in a Combined Cycle Train. |  | Latest Approved combined Cycle Configurations Details.
CONFIG_TYPE | RARF_HUB | CCUNIT_CONFIGURATION |  | Configuration Type: Primary(X) or Alternate (A).
DATE_LOADED | RARF_HUB | CCUNIT_CONFIGURATION |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | CCUNIT_CONFIGURATION |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
ID | RARF_HUB | CCUNIT_CONFIGURATION |  | Configuration ID.
SITE_CODE | RARF_HUB | CCUNIT_CONFIGURATION |  | Unique Code for Resource Site (e.g.: CBY).
UNIT_CODE | RARF_HUB | CCUNIT_CONFIGURATION |  | Concatenated Mnemonic of Resource Site Code and Unit name (e.g CBY_CBYG1).
CONFIG_NO | RARF_HUB | CCUNIT_CONFIGURATION |  | Configuration # | Added 06/27/2012
APPROVED_DATE | RARF_HUB | CCUNIT_CONFIGURATION_HIST | History Table: All approved and Disapproved combined Cycle Configurations Details. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved and Disapproved combined Cycle Configurations Details.
CONFIG_CODE | RARF_HUB | CCUNIT_CONFIGURATION_HIST |  | Unique Code for Each Configuration in a Combined Cycle Train.
CONFIG_TYPE | RARF_HUB | CCUNIT_CONFIGURATION_HIST |  | Configuration Type: Primary(X) or Alternate (A).
DATE_LOADED | RARF_HUB | CCUNIT_CONFIGURATION_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | CCUNIT_CONFIGURATION_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
ID | RARF_HUB | CCUNIT_CONFIGURATION_HIST |  | Configuration ID.
SITE_CODE | RARF_HUB | CCUNIT_CONFIGURATION_HIST |  | Unique Code for Resource Site (e.g.: CBY).
SUBMISSION_TYPE | RARF_HUB | CCUNIT_CONFIGURATION_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
UNIT_CODE | RARF_HUB | CCUNIT_CONFIGURATION_HIST |  | Concatenated Mnemonic of Resource Site Code and Unit name (e.g CBY_CBYG1).
CONFIG_NO | RARF_HUB | CCUNIT_CONFIGURATION_HIST |  | Configuration # | Added 06/27/2012
APPROVED_DATE | RARF_HUB | CCUNIT_HIST | History Table: All approved and Disapproved combined Cycle unit information. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved and Disapproved combined Cycle unit information.
ARMATURE_Z_R_PU | RARF_HUB | CCUNIT_HIST |  | Stator impedance value (R in P.U).
ARMATURE_Z_X_PU | RARF_HUB | CCUNIT_HIST |  | Stator impedance value (X in P.U).
AUX_MVARTOTAL | RARF_HUB | CCUNIT_HIST |  | Average MVAR for Auxiliary Load.
AUX_MWTOTAL | RARF_HUB | CCUNIT_HIST |  | Average MW for Auxiliary Load.
AUXMVAR_DISCHARGE_PCT | RARF_HUB | CCUNIT_HIST |  | Generation Auxiliary Load Characteristics for MVAR Load - Discharge Lighting, percent of total MVAR load.
AUXMVAR_LARGEMTR_PCT | RARF_HUB | CCUNIT_HIST |  | Generation Auxiliary Load Characteristics for MVAR Load - Large Motor, percent of total MVAR load.
AUXMVAR_OTHER_PCT | RARF_HUB | CCUNIT_HIST |  | Generation Auxiliary Load Characteristics for MVAR Load - Other, percent of total MVAR load.
AUXMVAR_SMALLMTR_PCT | RARF_HUB | CCUNIT_HIST |  | Generation Auxiliary Load Characteristics for MVAR Load - Small Motor, percent of total MVAR load.
AUXMW_DISCHARGE_PCT | RARF_HUB | CCUNIT_HIST |  | Generation Auxiliary Load Characteristics for MW Load - Discharge Lighting, percent of total MW load.
AUXMW_LARGEMTR_PCT | RARF_HUB | CCUNIT_HIST |  | Generation Auxiliary Load Characteristics for MW Load - Large Motor, percent of total MW load.
AUXMW_OTHER_PCT | RARF_HUB | CCUNIT_HIST |  | Generation Auxiliary Load Characteristics for MW Load - Other, percent of total MW load.
AUXMW_RESISTIVE_PCT | RARF_HUB | CCUNIT_HIST |  | Generation Auxiliary Load Characteristics for MW Load - Resistive (Heating) Load, percent of total MW load.
AUXMW_SMALLMTR_PCT | RARF_HUB | CCUNIT_HIST |  | Generation Auxiliary Load Characteristics for MW Load - Small Motor, percent of total MW load.
AVG_LD_MVAR_UNIT | RARF_HUB | CCUNIT_HIST |  | Average Amount of Auxiliary Reactive Power.
AVG_LD_MW_UNIT | RARF_HUB | CCUNIT_HIST |  | Average Amount of Auxiliary Real Power.
BREAKER_INTERRUP | RARF_HUB | CCUNIT_HIST |  | Breaker Interruption Time.
COMPSTR_FLG | RARF_HUB | CCUNIT_HIST |  | This column is not being used.
COMPSTR_FORM_FLG | RARF_HUB | CCUNIT_HIST |  | This column is not being used.
DATE_LOADED | RARF_HUB | CCUNIT_HIST |  | Date when the RARF is loaded into the Database
DATE_SUBMITTED | RARF_HUB | CCUNIT_HIST |  | Date when the RARF is submitted to ERCOT for processing
DIRECT_AXIS_SUBSTNT_REACTANCE | RARF_HUB | CCUNIT_HIST |  | Direct Axis Sub transient reactance, X"di.
DIRECT_AXIS_TRANSNT_REACTANCE | RARF_HUB | CCUNIT_HIST |  | Direct Axis Transient reactance, X'di.
ERCOT_INTRCONN_PROJ_NUM | RARF_HUB | CCUNIT_HIST |  | ERCOT Interconnection Project Number.
EXCITN_FORM_FLG | RARF_HUB | CCUNIT_HIST |  | This column is not being used.
GEN_FORM_FLG | RARF_HUB | CCUNIT_HIST |  | This column is not being used.
GROSS_CAPBLTY_MVAR_UNIT | RARF_HUB | CCUNIT_HIST |  | Gross Capability (MVAR).
GROSS_CAPBLTY_MW_UNIT | RARF_HUB | CCUNIT_HIST |  | Gross Capability (MW).
HR_LMT | RARF_HUB | CCUNIT_HIST |  | High Reasonability Limit.
HR_RAMPRATE_LMT | RARF_HUB | CCUNIT_HIST |  | High Reasonability Ramp Rate limit.
HYDROCOOLED | RARF_HUB | CCUNIT_HIST |  | hydro cooled.
KVBASE | RARF_HUB | CCUNIT_HIST |  | What is the kV base that the following data is based on?.
LOAD_TRIP_FLG | RARF_HUB | CCUNIT_HIST |  | Load Trip Flag.
LOAD_TRIP_PCT | RARF_HUB | CCUNIT_HIST |  | Load Trip percent.
LR_LMT | RARF_HUB | CCUNIT_HIST |  | Low Reasonability Limit.
LR_RAMP_RATE_LMT | RARF_HUB | CCUNIT_HIST |  | Low Reasonability Ramp rate Limit.
MACHINE_IMPEDANCE_R_PU | RARF_HUB | CCUNIT_HIST |  | This column is not being used.
MACHINE_IMPEDANCE_X_PU | RARF_HUB | CCUNIT_HIST |  | This column is not being used.
MFR_CAPABILITY_CURVE_FLG | RARF_HUB | CCUNIT_HIST |  | Manufactured Capability Curve Flag.
MUTUAL_COUPLING_Z_R_PU | RARF_HUB | CCUNIT_HIST |  | This column is not being used.
MUTUAL_COUPLING_Z_X_PU | RARF_HUB | CCUNIT_HIST |  | This column is not being used.
MVABASE | RARF_HUB | CCUNIT_HIST |  | What is the MVA base that the following data is based on?.
MVAR1LAG_GEN | RARF_HUB | CCUNIT_HIST |  | Unit's Lagging reactive power output capability associated with its MW1 output, in MVAR
MVAR1LEAD_GEN | RARF_HUB | CCUNIT_HIST |  | Unit's Leading reactive power output capability associated with its MW1 output, in MVAR; input as negative number.
MVAR2LAG_GEN | RARF_HUB | CCUNIT_HIST |  | Unit's Lagging reactive power output capability associated with its MW2 output, in MVAR
MVAR2LEAD_GEN | RARF_HUB | CCUNIT_HIST |  | Unit's Leading reactive power output capability associated with its MW2 output, in MVAR; input as negative number.
MVAR3LAG_GEN | RARF_HUB | CCUNIT_HIST |  | Unit's Lagging reactive power output capability associated with its MW3 output, in MVAR
MVAR3LEAD_GEN | RARF_HUB | CCUNIT_HIST |  | Unit's Leading reactive power output capability associated with its MW3 output, in MVAR; input as negative number.
MVAR4LAG_GEN | RARF_HUB | CCUNIT_HIST |  | Unit's Lagging reactive power output capability associated with its MW4 output, in MVAR
MVAR4LEAD_GEN | RARF_HUB | CCUNIT_HIST |  | Unit's Leading reactive power output capability associated with its MW4 output, in MVAR; input as negative number.
MW1_GEN | RARF_HUB | CCUNIT_HIST |  | Reactive Capability curve - point on curve of MW output for this unit, MW1.
MW2_GEN | RARF_HUB | CCUNIT_HIST |  | Reactive Capability curve - point on curve of MW output for this unit, MW2.
MW3_GEN | RARF_HUB | CCUNIT_HIST |  | Reactive Capability curve - point on curve of MW output for this unit, MW3.
MW4_GEN | RARF_HUB | CCUNIT_HIST |  | Reactive Capability curve - point on curve of MW output for this unit, MW4.
MW5UNITYPF_GEN | RARF_HUB | CCUNIT_HIST |  | From the Reactive Capability curve - the MW output at Unity Power Factor (zero MVAR).
NAME_PLT_RTG | RARF_HUB | CCUNIT_HIST |  | Name Plate Rating of the Unit.
NEGATIVE_SEQ_Z_R_PU | RARF_HUB | CCUNIT_HIST |  | Negative Sequence Z ( R in P.U).
NEGATIVE_SEQ_Z_X_PU | RARF_HUB | CCUNIT_HIST |  | Negative Sequence Z ( X in P.U).
NET_INTERCHNG_MVAR_UNIT | RARF_HUB | CCUNIT_HIST |  | Unit's Net interchange MVAR.
NET_INTERCHNG_MW_UNIT | RARF_HUB | CCUNIT_HIST |  | Unit's Net interchange MVW.
NETMAXLAG_GEN | RARF_HUB | CCUNIT_HIST |  | Net Maximum Lagging Operating Capability (MVAR).
NETMAXLEAD_GEN | RARF_HUB | CCUNIT_HIST |  | Net Maximum Leading Operating Capability (MVAR).
OFREQ_TRIP_HZ1 | RARF_HUB | CCUNIT_HIST |  | Over frequency Protection Setting- HZ1.
OFREQ_TRIP_HZ2 | RARF_HUB | CCUNIT_HIST |  | Over frequency Protection Setting- HZ2.
OFREQ_TRIP_HZ3 | RARF_HUB | CCUNIT_HIST |  | Over frequency Protection Setting- HZ3.
OFREQ_TRIP_HZ4 | RARF_HUB | CCUNIT_HIST |  | Over frequency Protection Setting- HZ4.
OFREQ_TRIP_INSTANT | RARF_HUB | CCUNIT_HIST |  | Instantaneous Over frequency Trip.
OFREQ_TRIP_TIME1 | RARF_HUB | CCUNIT_HIST |  | Over frequency Protection Setting- TIME1.
OFREQ_TRIP_TIME2 | RARF_HUB | CCUNIT_HIST |  | Over frequency Protection Setting- TIME2.
OFREQ_TRIP_TIME3 | RARF_HUB | CCUNIT_HIST |  | Over frequency Protection Setting- TIME3.
OFREQ_TRIP_TIME4 | RARF_HUB | CCUNIT_HIST |  | Over frequency Protection Setting- TIME4.
OVER_EXCITN_LIMITER_FLG | RARF_HUB | CCUNIT_HIST |  | This column is not being used.
OVER_EXCITN_LIMITER_FORM_FLG | RARF_HUB | CCUNIT_HIST |  | This column is not being used.
OVOLT_TRIP_INSTANT | RARF_HUB | CCUNIT_HIST |  | Instantaneous Overvoltage Trip.
OVOLT_TRIP_TIME1 | RARF_HUB | CCUNIT_HIST |  | Overvoltage Trip Time setting 1.
OVOLT_TRIP_TIME2 | RARF_HUB | CCUNIT_HIST |  | Overvoltage Trip Time setting 2.
OVOLT_TRIP_TIME3 | RARF_HUB | CCUNIT_HIST |  | Overvoltage Trip Time setting 3.
OVOLT_TRIP_TIME4 | RARF_HUB | CCUNIT_HIST |  | Overvoltage Trip Time setting 4.
OVOLT_TRIP_VOLT1 | RARF_HUB | CCUNIT_HIST |  | Overvoltage Trip Voltage setting 1.
OVOLT_TRIP_VOLT2 | RARF_HUB | CCUNIT_HIST |  | Overvoltage Trip Voltage setting 2.
OVOLT_TRIP_VOLT3 | RARF_HUB | CCUNIT_HIST |  | Overvoltage Trip Voltage setting 3.
OVOLT_TRIP_VOLT4 | RARF_HUB | CCUNIT_HIST |  | Overvoltage Trip Voltage setting 4.
PHYS_UNIT_TYPE | RARF_HUB | CCUNIT_HIST |  | Physical Unit Type.
POSITIVE_SEQ_Z_R_PU | RARF_HUB | CCUNIT_HIST |  | Positive Sequence Impedance ( R in P.U).
POSITIVE_SEQ_Z_X_PU | RARF_HUB | CCUNIT_HIST |  | Positive Sequence Impedance ( Z in P.U).
PRIM_FUELTYPE | RARF_HUB | CCUNIT_HIST |  | Primary Fuel type for the Unit.
PSS_FLG | RARF_HUB | CCUNIT_HIST |  | This column is not being used.
PSSFORM_FLG | RARF_HUB | CCUNIT_HIST |  | This column is not being used.
ROTOR_Z_R_PU | RARF_HUB | CCUNIT_HIST |  | This column is not being used.
ROTOR_Z_X_PU | RARF_HUB | CCUNIT_HIST |  | This column is not being used.
RTG_MVAR | RARF_HUB | CCUNIT_HIST |  | Reactive Power Rating.
RTG_MW | RARF_HUB | CCUNIT_HIST |  | Real Power Rating.
SEASON_NET_MAX_EMGY_RTG_FL | RARF_HUB | CCUNIT_HIST |  | Seasonal Net Maximum Emergency Rating -Fall (MW).
SEASON_NET_MAX_EMGY_RTG_SM | RARF_HUB | CCUNIT_HIST |  | Seasonal Net Maximum Emergency Rating -Summer (MW).
SEASON_NET_MAX_EMGY_RTG_SP | RARF_HUB | CCUNIT_HIST |  | Seasonal Net Maximum Emergency Rating -Spring (MW).
SEASON_NET_MAX_EMGY_RTG_WT | RARF_HUB | CCUNIT_HIST |  | Seasonal Net Maximum Emergency Rating -Winter (MW).
SEASON_NET_MAX_SUST_RTG_FL | RARF_HUB | CCUNIT_HIST |  | Seasonal Net Maximum Sustainable Rating -Fall (MW).
SEASON_NET_MAX_SUST_RTG_SM | RARF_HUB | CCUNIT_HIST |  | Seasonal Net Maximum Sustainable Rating -Summer (MW).
SEASON_NET_MAX_SUST_RTG_SP | RARF_HUB | CCUNIT_HIST |  | Seasonal Net Maximum Sustainable Rating -Spring (MW).
SEASON_NET_MAX_SUST_RTG_WT | RARF_HUB | CCUNIT_HIST |  | Seasonal Net Maximum Sustainable Rating -Winter (MW).
SEASON_NET_MIN_EMGY_RTG_FL | RARF_HUB | CCUNIT_HIST |  | Seasonal Net Minimum Emergency Rating -Fall (MW).
SEASON_NET_MIN_EMGY_RTG_SM | RARF_HUB | CCUNIT_HIST |  | Seasonal Net Minimum Emergency Rating -Summer (MW).
SEASON_NET_MIN_EMGY_RTG_SP | RARF_HUB | CCUNIT_HIST |  | Seasonal Net Minimum Emergency Rating -Spring (MW).
SEASON_NET_MIN_EMGY_RTG_WT | RARF_HUB | CCUNIT_HIST |  | Seasonal Net Minimum Emergency Rating -Winter (MW).
SEASON_NET_MIN_SUST_RTG_FL | RARF_HUB | CCUNIT_HIST |  | Seasonal Net Minimum Sustainable Rating -Fall (MW).
SEASON_NET_MIN_SUST_RTG_SM | RARF_HUB | CCUNIT_HIST |  | Seasonal Net Minimum Sustainable Rating - Summer (MW).
SEASON_NET_MIN_SUST_RTG_SP | RARF_HUB | CCUNIT_HIST |  | Seasonal Net Minimum Sustainable Rating - Spring (MW).
SEASON_NET_MIN_SUST_RTG_WT | RARF_HUB | CCUNIT_HIST |  | Seasonal Net Minimum Sustainable Rating - Winter (MW).
SEC_FUELTYPE | RARF_HUB | CCUNIT_HIST |  | Secondary Fuel Type.
SITE_CODE | RARF_HUB | CCUNIT_HIST |  | Unique Code for Resource Site (e.g.; CBY).
SUBMISSION_TYPE | RARF_HUB | CCUNIT_HIST |  | Submission Type: Internal or External.
TURB_GOVNR_FORM_FLG | RARF_HUB | CCUNIT_HIST |  | Turbine Governor Form Flag.
TURBINE_RTG | RARF_HUB | CCUNIT_HIST |  | Turbine Rating.
UFREQ_TRIP_HZ1 | RARF_HUB | CCUNIT_HIST |  | Under frequency Protection Setting- HZ1.
UFREQ_TRIP_HZ2 | RARF_HUB | CCUNIT_HIST |  | Under frequency Protection Setting- HZ2.
UFREQ_TRIP_HZ3 | RARF_HUB | CCUNIT_HIST |  | Under frequency Protection Setting- HZ3.
UFREQ_TRIP_HZ4 | RARF_HUB | CCUNIT_HIST |  | Under frequency Protection Setting- HZ4.
UFREQ_TRIP_INSTANT | RARF_HUB | CCUNIT_HIST |  | Instantaneous Under frequency Trip.
UFREQ_TRIP_TIME1 | RARF_HUB | CCUNIT_HIST |  | Under frequency Protection Setting- TIME1.
UFREQ_TRIP_TIME2 | RARF_HUB | CCUNIT_HIST |  | Under frequency Protection Setting- TIME2.
UFREQ_TRIP_TIME3 | RARF_HUB | CCUNIT_HIST |  | Under frequency Protection Setting- TIME3.
UFREQ_TRIP_TIME4 | RARF_HUB | CCUNIT_HIST |  | Under frequency Protection Setting- TIME4.
UNDER_EXCITN_LIMITER_FLG | RARF_HUB | CCUNIT_HIST |  | Under Excitation Limiter Flag: Y or N.
UNDER_EXCITN_LIMITER_FORM_FLG | RARF_HUB | CCUNIT_HIST |  | Under Excitation Limiter Form Submitted?: Y or N.
UNIT_CODE | RARF_HUB | CCUNIT_HIST |  | Concatenated Mnemonic of Resource Site Code and Unit name (e.g CBY_CBYG1).
UNIT_END_DT | RARF_HUB | CCUNIT_HIST |  | Unit Termination Date( MM/DD/YYYY ).
UNIT_KV | RARF_HUB | CCUNIT_HIST |  | Unit Generating Voltage.
UNIT_NAME | RARF_HUB | CCUNIT_HIST |  | Unit Name.
UNIT_START_DT | RARF_HUB | CCUNIT_HIST |  | Unit Commercial Operations Date. It is the date on which Generator declares that the construction of the Plant has been substantially completed, Trial Operation of the Plant has been completed, and the Plant is ready for dispatch. Format is MM/DD/YYYY.
UVOLT_TRIP_INSTANT | RARF_HUB | CCUNIT_HIST |  | Instantaneous Under voltage Trip.
UVOLT_TRIP_TIME1 | RARF_HUB | CCUNIT_HIST |  | Under Voltage Protection Setting- TIME1.
UVOLT_TRIP_TIME2 | RARF_HUB | CCUNIT_HIST |  | Under Voltage Protection Setting- TIME2.
UVOLT_TRIP_TIME3 | RARF_HUB | CCUNIT_HIST |  | Under Voltage Protection Setting- TIME3.
UVOLT_TRIP_TIME4 | RARF_HUB | CCUNIT_HIST |  | Under Voltage Protection Setting- TIME4.
UVOLT_TRIP_VOLT1 | RARF_HUB | CCUNIT_HIST |  | Under Voltage Protection Setting- VOLT1.
UVOLT_TRIP_VOLT2 | RARF_HUB | CCUNIT_HIST |  | Under Voltage Protection Setting- VOLT2.
UVOLT_TRIP_VOLT3 | RARF_HUB | CCUNIT_HIST |  | Under Voltage Protection Setting- VOLT3.
UVOLT_TRIP_VOLT4 | RARF_HUB | CCUNIT_HIST |  | Under Voltage Protection Setting- VOLT4.
ZERO_SEQ_Z_R_PU | RARF_HUB | CCUNIT_HIST |  | Zero Sequence Impedance ( R in P.U).
ZERO_SEQ_Z_X_PU | RARF_HUB | CCUNIT_HIST |  | Zero Sequence Impedance ( R in P.U).
AUX_LOAD_PWR_FACT | RARF_HUB | CCUNIT_HIST |  | Auxiliary Load Power Factor | Added 06/27/2012
DESIGN_MAX_AMB_TEMP | RARF_HUB | CCUNIT_HIST |  | Design Max Ambient Temperature | Added 06/27/2012
DESIGN_MIN_AMB_TEMP | RARF_HUB | CCUNIT_HIST |  | Design Min Ambient Temperature | Added 06/27/2012
DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED | RARF_HUB | CCUNIT_HIST |  | Direct Axis Subtransient Reactance, X"dv (saturated) | Added 06/27/2012
DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED | RARF_HUB | CCUNIT_HIST |  | Direct Axis Transient Reactance, X'dv (saturated) | Added 06/27/2012
DOES_ZERO_SEQ_EXIST | RARF_HUB | CCUNIT_HIST |  | Does Zero Sequence Z exist? | Added 06/27/2012
GOV_DEAD_BND | RARF_HUB | CCUNIT_HIST |  | Governor Dead-band | Added 06/27/2012
GOV_DROOP | RARF_HUB | CCUNIT_HIST |  | Governor Droop Setting | Added 06/27/2012
NEGATIVE_SEQ_Z_R_PU | RARF_HUB | CCUNIT_HIST |  | Negative Sequence Z (saturated) | Added 06/27/2012
NEGATIVE_SEQ_Z_X_PU | RARF_HUB | CCUNIT_HIST |  | Negative Sequence Z (saturated) | Added 06/27/2012
POSITIVE_SEQ_Z_R_PU | RARF_HUB | CCUNIT_HIST |  | Positive Sequence Z (saturated) | Added 06/27/2012
POSITIVE_SEQ_Z_X_PU | RARF_HUB | CCUNIT_HIST |  | Positive Sequence Z (saturated) | Added 06/27/2012
PTI_BUS_NUM | RARF_HUB | CCUNIT_HIST |  | PTI Bus Number | Added 06/27/2012
REACT_CAPB_DATA_GROSS_VAL | RARF_HUB | CCUNIT_HIST |  | Reactive Capability Data Provided is Gross Values? | Added 06/27/2012
REACT_CAPB_NDCRC_TEST_DATA | RARF_HUB | CCUNIT_HIST |  | Reactive Capability Data Provided is from NDCRC Test Data? | Added 06/27/2012
REACT_CAPB_NDCRC_TEST_DATA_DT | RARF_HUB | CCUNIT_HIST |  | If Reactive Capability Data Provided Is From NDCRC test Data Then Enter The Date On Which The Test Was Performed. | Added 06/27/2012
SGIA_SIG_DT | RARF_HUB | CCUNIT_HIST |  | Standard Generation Interconnection Agreement (SGIA) Signature Date | Added 06/27/2012
SUBSTAT_CODE_SUB_MNEMONIC | RARF_HUB | CCUNIT_HIST |  | SubStation Code/SubStation Mnemonic | Added 06/27/2012
TRANS_ONLY_DT | RARF_HUB | CCUNIT_HIST |  | Transmission Only Date (POI) | Added 06/27/2012
UNIT_MRD_ST_DT | RARF_HUB | CCUNIT_HIST |  | Unit Start Date (Model Ready Date) | Added 06/27/2012
VOL_LEV | RARF_HUB | CCUNIT_HIST |  | Voltage Level | Added 06/27/2012
ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU | RARF_HUB | CCUNIT_HIST |  | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Added 06/27/2012
ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU | RARF_HUB | CCUNIT_HIST |  | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Added 06/27/2012
ZERO_SEQ_Z_R_PU | RARF_HUB | CCUNIT_HIST |  | Zero Sequence Z (saturated) | Added 06/27/2012
ZERO_SEQ_Z_X_PU | RARF_HUB | CCUNIT_HIST |  | Zero Sequence Z (saturated) | Added 06/27/2012
COLDSTART | RARF_HUB | CONFIGURATIONS | Latest Approved Generation Resources Configurations Details. | Cold Start Time. |  | Latest Approved Generation Resources Configurations Details.
CONFIG_CODE | RARF_HUB | CONFIGURATIONS |  | Unique Code for each configuration defined as the concatenation of SITE_CODE_TRAIN_CODE.
DATE_LOADED | RARF_HUB | CONFIGURATIONS |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | CONFIGURATIONS |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
HOT_TO_INTMDT_TIME | RARF_HUB | CONFIGURATIONS |  | Hot to Intermediate Start Time.
HOTSTART | RARF_HUB | CONFIGURATIONS |  | Hot Start Time.
HR_LMT | RARF_HUB | CONFIGURATIONS |  | High reasonability Limit.
HR_RAMPRATE_LMT | RARF_HUB | CONFIGURATIONS |  | High Reasonability Ramp rate Limit.
INTERMSTART | RARF_HUB | CONFIGURATIONS |  | Intermediate Start Time.
INTMDT_TO_COLD_TIME | RARF_HUB | CONFIGURATIONS |  | Intermediate to Cold time.
LR_LMT | RARF_HUB | CONFIGURATIONS |  | Low reasonability Limit.
LR_RAMP_RATE_LMT | RARF_HUB | CONFIGURATIONS |  | Low Reasonability Ramp rate Limit.
MAX_ONLINE_TIME | RARF_HUB | CONFIGURATIONS |  | Maximum Online Time.
MAXDLYSTARTS | RARF_HUB | CONFIGURATIONS |  | Maximum Daily Starts.
MAXWKLYENRGY | RARF_HUB | CONFIGURATIONS |  | Maximum Weekly Energy.
MAXWKLYSTARTS | RARF_HUB | CONFIGURATIONS |  | Maximum Weekly Starts.
MIN_OFFLINE_TIME | RARF_HUB | CONFIGURATIONS |  | Minimum Offline Time.
MIN_ONLINE_TIME | RARF_HUB | CONFIGURATIONS |  | Minimum Online Time.
NOTES_CONFIG | RARF_HUB | CONFIGURATIONS |  | General Notes.
SEASON_NET_MAX_EMGY_RTG_FL | RARF_HUB | CONFIGURATIONS |  | Seasonal Net Maximum Emergency Rating -Fall (MW).
SEASON_NET_MAX_EMGY_RTG_SM | RARF_HUB | CONFIGURATIONS |  | Seasonal Net Maximum Emergency Rating -Summer (MW).
SEASON_NET_MAX_EMGY_RTG_SP | RARF_HUB | CONFIGURATIONS |  | Seasonal Net Maximum Emergency Rating -Spring (MW).
SEASON_NET_MAX_EMGY_RTG_WT | RARF_HUB | CONFIGURATIONS |  | Seasonal Net Maximum Emergency Rating -Winter (MW).
SEASON_NET_MAX_SUST_RTG_FL | RARF_HUB | CONFIGURATIONS |  | Seasonal Net Maximum Sustainable Rating -Fall (MW).
SEASON_NET_MAX_SUST_RTG_SM | RARF_HUB | CONFIGURATIONS |  | Seasonal Net Maximum Sustainable Rating -Summer (MW).
SEASON_NET_MAX_SUST_RTG_SP | RARF_HUB | CONFIGURATIONS |  | Seasonal Net Maximum Sustainable Rating -Spring (MW).
SEASON_NET_MAX_SUST_RTG_WT | RARF_HUB | CONFIGURATIONS |  | Seasonal Net Maximum Sustainable Rating -Winter (MW).
SEASON_NET_MIN_EMGY_RTG_FL | RARF_HUB | CONFIGURATIONS |  | Seasonal Net Minimum Emergency Rating -Fall (MW).
SEASON_NET_MIN_EMGY_RTG_SM | RARF_HUB | CONFIGURATIONS |  | Seasonal Net Minimum Emergency Rating -Summer (MW).
SEASON_NET_MIN_EMGY_RTG_SP | RARF_HUB | CONFIGURATIONS |  | Seasonal Net Minimum Emergency Rating -Spring (MW).
SEASON_NET_MIN_EMGY_RTG_WT | RARF_HUB | CONFIGURATIONS |  | Seasonal Net Minimum Emergency Rating -Winter (MW).
SEASON_NET_MIN_SUST_RTG_FL | RARF_HUB | CONFIGURATIONS |  | Seasonal Net Minimum Sustainable Rating -Fall (MW).
SEASON_NET_MIN_SUST_RTG_SM | RARF_HUB | CONFIGURATIONS |  | Seasonal Net Minimum Sustainable Rating - Summer (MW).
SEASON_NET_MIN_SUST_RTG_SP | RARF_HUB | CONFIGURATIONS |  | Seasonal Net Minimum Sustainable Rating - Spring (MW).
SEASON_NET_MIN_SUST_RTG_WT | RARF_HUB | CONFIGURATIONS |  | Seasonal Net Minimum Sustainable Rating - Winter (MW).
SITE_CODE | RARF_HUB | CONFIGURATIONS |  | Unique code for Site.
TRAIN_CODE | RARF_HUB | CONFIGURATIONS |  | Unique Code for each combined cycle Train defined as the concatenation of SITE_CODE_TRAIN_NAME( Defined in the TRAIN Table).
APPROVED_DATE | RARF_HUB | CONFIGURATIONS_HIST | History Table: All approved and Disapproved combined Cycle Configurations information. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved and Disapproved combined Cycle Configurations information.
COLDSTART | RARF_HUB | CONFIGURATIONS_HIST |  | Cold Start Time.
CONFIG_CODE | RARF_HUB | CONFIGURATIONS_HIST |  | Unique Code for each configuration defined as the concatenation of SITE_CODE_TRAIN_CODE.
DATE_LOADED | RARF_HUB | CONFIGURATIONS_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | CONFIGURATIONS_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
HOT_TO_INTMDT_TIME | RARF_HUB | CONFIGURATIONS_HIST |  | Hot to Intermediate Start Time.
HOTSTART | RARF_HUB | CONFIGURATIONS_HIST |  | Hot Start Time.
HR_LMT | RARF_HUB | CONFIGURATIONS_HIST |  | High reasonability Limit.
HR_RAMPRATE_LMT | RARF_HUB | CONFIGURATIONS_HIST |  | High Reasonability Ramp rate Limit.
INTERMSTART | RARF_HUB | CONFIGURATIONS_HIST |  | Intermediate Start Time.
INTMDT_TO_COLD_TIME | RARF_HUB | CONFIGURATIONS_HIST |  | Intermediate to Cold time.
LR_LMT | RARF_HUB | CONFIGURATIONS_HIST |  | Low reasonability Limit.
LR_RAMP_RATE_LMT | RARF_HUB | CONFIGURATIONS_HIST |  | Low Reasonability Ramp rate Limit.
MAX_ONLINE_TIME | RARF_HUB | CONFIGURATIONS_HIST |  | Maximum Online Time.
MAXDLYSTARTS | RARF_HUB | CONFIGURATIONS_HIST |  | Maximum Daily Starts.
MAXWKLYENRGY | RARF_HUB | CONFIGURATIONS_HIST |  | Maximum Weekly Energy.
MAXWKLYSTARTS | RARF_HUB | CONFIGURATIONS_HIST |  | Maximum Weekly Starts.
MIN_OFFLINE_TIME | RARF_HUB | CONFIGURATIONS_HIST |  | Minimum Offline Time.
MIN_ONLINE_TIME | RARF_HUB | CONFIGURATIONS_HIST |  | Minimum Online Time.
NOTES_CONFIG | RARF_HUB | CONFIGURATIONS_HIST |  | General Notes.
SEASON_NET_MAX_EMGY_RTG_FL | RARF_HUB | CONFIGURATIONS_HIST |  | Seasonal Net Maximum Emergency Rating -Fall (MW).
SEASON_NET_MAX_EMGY_RTG_SM | RARF_HUB | CONFIGURATIONS_HIST |  | Seasonal Net Maximum Emergency Rating -Summer (MW).
SEASON_NET_MAX_EMGY_RTG_SP | RARF_HUB | CONFIGURATIONS_HIST |  | Seasonal Net Maximum Emergency Rating -Spring (MW).
SEASON_NET_MAX_EMGY_RTG_WT | RARF_HUB | CONFIGURATIONS_HIST |  | Seasonal Net Maximum Emergency Rating -Winter (MW).
SEASON_NET_MAX_SUST_RTG_FL | RARF_HUB | CONFIGURATIONS_HIST |  | Seasonal Net Maximum Sustainable Rating -Fall (MW).
SEASON_NET_MAX_SUST_RTG_SM | RARF_HUB | CONFIGURATIONS_HIST |  | Seasonal Net Maximum Sustainable Rating -Summer (MW).
SEASON_NET_MAX_SUST_RTG_SP | RARF_HUB | CONFIGURATIONS_HIST |  | Seasonal Net Maximum Sustainable Rating -Spring (MW).
SEASON_NET_MAX_SUST_RTG_WT | RARF_HUB | CONFIGURATIONS_HIST |  | Seasonal Net Maximum Sustainable Rating -Winter (MW).
SEASON_NET_MIN_EMGY_RTG_FL | RARF_HUB | CONFIGURATIONS_HIST |  | Seasonal Net Minimum Emergency Rating -Fall (MW).
SEASON_NET_MIN_EMGY_RTG_SM | RARF_HUB | CONFIGURATIONS_HIST |  | Seasonal Net Minimum Emergency Rating -Summer (MW).
SEASON_NET_MIN_EMGY_RTG_SP | RARF_HUB | CONFIGURATIONS_HIST |  | Seasonal Net Minimum Emergency Rating -Spring (MW).
SEASON_NET_MIN_EMGY_RTG_WT | RARF_HUB | CONFIGURATIONS_HIST |  | Seasonal Net Minimum Emergency Rating -Winter (MW).
SEASON_NET_MIN_SUST_RTG_FL | RARF_HUB | CONFIGURATIONS_HIST |  | Seasonal Net Minimum Sustainable Rating -Fall (MW).
SEASON_NET_MIN_SUST_RTG_SM | RARF_HUB | CONFIGURATIONS_HIST |  | Seasonal Net Minimum Sustainable Rating - Summer (MW).
SEASON_NET_MIN_SUST_RTG_SP | RARF_HUB | CONFIGURATIONS_HIST |  | Seasonal Net Minimum Sustainable Rating - Spring (MW).
SEASON_NET_MIN_SUST_RTG_WT | RARF_HUB | CONFIGURATIONS_HIST |  | Seasonal Net Minimum Sustainable Rating - Winter (MW).
SITE_CODE | RARF_HUB | CONFIGURATIONS_HIST |  | Unique code for Site.
SUBMISSION_TYPE | RARF_HUB | CONFIGURATIONS_HIST |  | Submission Type: Internal or External.
TRAIN_CODE | RARF_HUB | CONFIGURATIONS_HIST |  | Unique Code for each combined cycle Train defined as the concatenation of SITE_CODE_TRAIN_NAME( Defined in the TRAIN Table).
CABLE_TYPE | RARF_HUB | COLLECTOR_SYS |  | Cable Type | Added 06/27/2012 | Latest approved Collector System Data details.
POS_CHRG_BC_KFT | RARF_HUB | COLLECTOR_SYS |  | Charging Bc/kft | Added 06/27/2012
POS_R_KFT | RARF_HUB | COLLECTOR_SYS |  | R/kft | Added 06/27/2012
POS_X_KFT | RARF_HUB | COLLECTOR_SYS |  | X/kft | Added 06/27/2012
VT_LEVEL_KV | RARF_HUB | COLLECTOR_SYS |  | Voltage Level kV | Added 06/27/2012
ZERO_R0_KFT | RARF_HUB | COLLECTOR_SYS |  | R0/kft | Added 06/27/2012
ZERO_X0_KFT | RARF_HUB | COLLECTOR_SYS |  | X0/kft | Added 06/27/2012
CABLE_TYPE | RARF_HUB | COLLECTOR_SYS_HIST |  | Cable Type | Added 06/27/2012 | History Table: ALL approved and DisapprovedCollector System Data details.
POS_CHRG_BC_KFT | RARF_HUB | COLLECTOR_SYS_HIST |  | Charging Bc/kft | Added 06/27/2012
POS_R_KFT | RARF_HUB | COLLECTOR_SYS_HIST |  | R/kft | Added 06/27/2012
POS_X_KFT | RARF_HUB | COLLECTOR_SYS_HIST |  | X/kft | Added 06/27/2012
VT_LEVEL_KV | RARF_HUB | COLLECTOR_SYS_HIST |  | Voltage Level kV | Added 06/27/2012
ZERO_R0_KFT | RARF_HUB | COLLECTOR_SYS_HIST |  | R0/kft | Added 06/27/2012
ZERO_X0_KFT | RARF_HUB | COLLECTOR_SYS_HIST |  | X0/kft | Added 06/27/2012
DE_RATING_TEM | RARF_HUB | DERATING_CC |  | 0°f to 120°f | Added 06/27/2012 | Latest approved CC DERATING Data details.
UNIT_CODE | RARF_HUB | DERATING_CC |  | Resource Name (Unit Code/Mnemonic) | Added 06/27/2012
UNIT_DERATING_TEMP_VAL | RARF_HUB | DERATING_CC |  | Derating Temperture Value for 0°f to 120°f | Added 06/27/2012
DE_RATING_TEM | RARF_HUB | DERATING_CC_HIST |  | 0°f to 120°f | Added 06/27/2012 | History Table: ALL approved and Disapproved CC DERATING Data details.
UNIT_CODE | RARF_HUB | DERATING_CC_HIST |  | Resource Name (Unit Code/Mnemonic) | Added 06/27/2012
UNIT_DERATING_TEMP_VAL | RARF_HUB | DERATING_CC_HIST |  | Derating Temperture Value for 0°f to 120°f | Added 06/27/2012
DE_RATING_TEM | RARF_HUB | DERATING_CFG |  | 0°f to 120°f | Added 06/27/2012 | Latest approved CFG DERATING Data details.
UNIT_CODE | RARF_HUB | DERATING_CFG |  | Resource Name (Unit Code/Mnemonic) | Added 06/27/2012
UNIT_DERATING_TEMP_VAL | RARF_HUB | DERATING_CFG |  | Derating Temperture Value for 0°f to 120°f | Added 06/27/2012
DE_RATING_TEM | RARF_HUB | DERATING_CFG_HIST |  | 0°f to 120°f | Added 06/27/2012 | History Table: ALL approved and Disapproved CFG DERATING Data details.
UNIT_CODE | RARF_HUB | DERATING_CFG_HIST |  | Resource Name (Unit Code/Mnemonic) | Added 06/27/2012
UNIT_DERATING_TEMP_VAL | RARF_HUB | DERATING_CFG_HIST |  | Derating Temperture Value for 0°f to 120°f | Added 06/27/2012
DE_RATING_TEM | RARF_HUB | DERATING_GEN |  | 0°f to 120°f | Added 06/27/2012 | Latest approved GEN DERATING Data details.
UNIT_CODE | RARF_HUB | DERATING_GEN |  | Resource Name (Unit Code/Mnemonic) | Added 06/27/2012
UNIT_DERATING_TEMP_VAL | RARF_HUB | DERATING_GEN |  | Derating Temperture Value for 0°f to 120°f | Added 06/27/2012
DE_RATING_TEM | RARF_HUB | DERATING_GEN_HIST |  | 0°f to 120°f | Added 06/27/2012 | History Table: ALL approved and Disapproved GEN DERATING Data details.
UNIT_CODE | RARF_HUB | DERATING_GEN_HIST |  | Resource Name (Unit Code/Mnemonic) | Added 06/27/2012
UNIT_DERATING_TEMP_VAL | RARF_HUB | DERATING_GEN_HIST |  | Derating Temperture Value for 0°f to 120°f | Added 06/27/2012
DE_RATING_TEM | RARF_HUB | DERATING_WIND |  | 0°f to 120°f | Added 06/27/2012 | Latest approved WIND DERATING Data details.
UNIT_CODE | RARF_HUB | DERATING_WIND |  | Resource Name (Unit Code/Mnemonic) | Added 06/27/2012
UNIT_DERATING_TEMP_VAL | RARF_HUB | DERATING_WIND |  | Derating Temperture Value for 0°f to 120°f | Added 06/27/2012
DE_RATING_TEM | RARF_HUB | DERATING_WIND_HIST |  | 0°f to 120°f | Added 06/27/2012 | History Table: ALL approved and Disapproved WINDDERATING Data details.
UNIT_CODE | RARF_HUB | DERATING_WIND_HIST |  | Resource Name (Unit Code/Mnemonic) | Added 06/27/2012
UNIT_DERATING_TEMP_VAL | RARF_HUB | DERATING_WIND_HIST |  | Derating Temperture Value for 0°f to 120°f | Added 06/27/2012
ARMATURE_Z_R_PU | RARF_HUB | generation | Latest Approved Generation Resources Unit Information Details. | Stator impedance value (R in P.U). |  | Latest Approved Generation Resources Unit Information Details.
ARMATURE_Z_X_PU | RARF_HUB | generation |  | Stator impedance value (X in P.U).
AUX_MVARTOTAL | RARF_HUB | generation |  | Average MVAR for Auxiliary Load.
AUX_MWTOTAL | RARF_HUB | generation |  | Average MW for Auxiliary Load.
AUXMVAR_DISCHARGE_PCT | RARF_HUB | generation |  | Generation Auxiliary Load Characteristics for MVAR Load - Discharge Lighting, percent of total MVAR load.
AUXMVAR_LARGEMTR_PCT | RARF_HUB | generation |  | Generation Auxiliary Load Characteristics for MVAR Load - Large Motor, percent of total MVAR load.
AUXMVAR_OTHER_PCT | RARF_HUB | generation |  | Generation Auxiliary Load Characteristics for MVAR Load - Other, percent of total MVAR load.
AUXMVAR_SMALLMTR_PCT | RARF_HUB | generation |  | Generation Auxiliary Load Characteristics for MVAR Load - Small Motor, percent of total MVAR load.
AUXMW_DISCHARGE_PCT | RARF_HUB | generation |  | Generation Auxiliary Load Characteristics for MW Load - Discharge Lighting, percent of total MW load.
AUXMW_LARGEMTR_PCT | RARF_HUB | generation |  | Generation Auxiliary Load Characteristics for MW Load - Large Motor, percent of total MW load.
AUXMW_OTHER_PCT | RARF_HUB | generation |  | Generation Auxiliary Load Characteristics for MW Load - Other, percent of total MW load.
AUXMW_RESISTIVE_PCT | RARF_HUB | generation |  | Generation Auxiliary Load Characteristics for MW Load - Resistive (Heating) Load, percent of total MW load.
AUXMW_SMALLMTR_PCT | RARF_HUB | generation |  | Generation Auxiliary Load Characteristics for MW Load - Small Motor, percent of total MW load.
AVG_LD_MVAR_UNIT | RARF_HUB | generation |  | Average Amount of Auxiliary Reactive Power.
AVG_LD_MW_UNIT | RARF_HUB | generation |  | Average Amount of Auxiliary Real Power.
BREAKER_INTERRUP | RARF_HUB | generation |  | Breaker Interruption Time.
COLDSTART | RARF_HUB | generation |  | Cold Start Time.
COMPSTR_FLG | RARF_HUB | generation |  | This column is not being used.
COMPSTR_FORM_FLG | RARF_HUB | generation |  | This column is not being used.
DATE_LOADED | RARF_HUB | generation |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | generation |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DIRECT_AXIS_SUBSTNT_REACTANCE | RARF_HUB | generation |  | Direct Axis Sub transient reactance, X"di.
DIRECT_AXIS_TRANSNT_REACTANCE | RARF_HUB | generation |  | Direct Axis Transient reactance, X'di.
ERCOT_INTRCONN_PROJ_NUM | RARF_HUB | generation |  | ERCOT Interconnection Project Number.
EXCITN_FORM_FLG | RARF_HUB | generation |  | This column is not being used.
FUEL_TRANSTYPE | RARF_HUB | generation |  | This column is not being used.
GEN_FORM_FLG | RARF_HUB | generation |  | This column is not being used.
GROSS_CAPBLTY_MVAR_UNIT | RARF_HUB | generation |  | Gross Capability (MVAR).
GROSS_CAPBLTY_MW_UNIT | RARF_HUB | generation |  | Gross Capability (MW).
HOT_TO_INTMDT_TIME | RARF_HUB | generation |  | Hot to Intermediate Start Time.
HOTSTART | RARF_HUB | generation |  | Hot Start Time.
HR_LMT | RARF_HUB | generation |  | High Reasonability Limit.
HR_RAMPRATE_LMT | RARF_HUB | generation |  | High Reasonability Ramp Rate limit.
HYDROCOOLED | RARF_HUB | generation |  | hydro cooled.
INTERMSTART | RARF_HUB | generation |  | Intermediate Start Time.
INTMDT_TO_COLD_TIME | RARF_HUB | generation |  | Intermediate to Cold time.
KVBASE | RARF_HUB | generation |  | What is the kV base that the following data is based on?.
LOAD_TRIP_FLG | RARF_HUB | generation |  | Load Trip Flag.
LOAD_TRIP_PCT | RARF_HUB | generation |  | Load Trip percent.
LR_LMT | RARF_HUB | generation |  | Low Reasonability Limit.
LR_RAMP_RATE_LMT | RARF_HUB | generation |  | Low Reasonability Ramp rate Limit.
MACHINE_IMPEDANCE_R_PU | RARF_HUB | generation |  | This column is not being used.
MACHINE_IMPEDANCE_X_PU | RARF_HUB | generation |  | This column is not being used.
MAX_ONLINE_TIME | RARF_HUB | generation |  | Maximum Online Time.
MAXDLYSTARTS | RARF_HUB | generation |  | Maximum Daily Starts.
MAXWKLYENRGY | RARF_HUB | generation |  | Maximum Weekly Energy.
MAXWKLYSTARTS | RARF_HUB | generation |  | Maximum Weekly Starts.
MFR_CAPABILITY_CURVE_FLG | RARF_HUB | generation |  | Manufactured Capability Curve Flag.
MIN_OFFLINE_TIME | RARF_HUB | generation |  | Minimum Off-line Time.
MIN_ONLINE_TIME | RARF_HUB | generation |  | Minimum On-line Time.
MUTUAL_COUPLING_Z_R_PU | RARF_HUB | generation |  | This column is not being used.
MUTUAL_COUPLING_Z_X_PU | RARF_HUB | generation |  | This column is not being used.
MVABASE | RARF_HUB | generation |  | What is the MVA base that the following data is based on?.
MVAR1LAG | RARF_HUB | generation |  | Unit's Lagging reactive power output capability associated with its MW1 output, in MVAR
MVAR1LEAD | RARF_HUB | generation |  | Unit's Leading reactive power output capability associated with its MW1 output, in MVAR; input as negative number.
MVAR2LAG | RARF_HUB | generation |  | Unit's Lagging reactive power output capability associated with its MW2 output, in MVAR
MVAR2LEAD | RARF_HUB | generation |  | Unit's Leading reactive power output capability associated with its MW2 output, in MVAR; input as negative number.
MVAR3LAG | RARF_HUB | generation |  | Unit's Lagging reactive power output capability associated with its MW3 output, in MVAR
MVAR3LEAD | RARF_HUB | generation |  | Unit's Leading reactive power output capability associated with its MW3 output, in MVAR; input as negative number.
MVAR4LAG | RARF_HUB | generation |  | Unit's Lagging reactive power output capability associated with its MW4 output, in MVAR
MVAR4LEAD | RARF_HUB | generation |  | Unit's Leading reactive power output capability associated with its MW4 output, in MVAR; input as negative number.
MW1 | RARF_HUB | generation |  | Reactive Capability curve - point on curve of MW output for this unit, MW1.
MW2 | RARF_HUB | generation |  | Reactive Capability curve - point on curve of MW output for this unit, MW2.
MW3 | RARF_HUB | generation |  | Reactive Capability curve - point on curve of MW output for this unit, MW3.
MW4 | RARF_HUB | generation |  | Reactive Capability curve - point on curve of MW output for this unit, MW4.
MW5UNITYPF | RARF_HUB | generation |  | From the Reactive Capability curve - the MW output at Unity Power Factor (zero MVAR).
NAME_PLT_RTG | RARF_HUB | generation |  | Name Plate Rating of the Unit.
NEGATIVE_SEQ_Z_R_PU | RARF_HUB | generation |  | Negative Sequence Impedance ( R in p.u).
NEGATIVE_SEQ_Z_X_PU | RARF_HUB | generation |  | Negative Sequence Impedance ( X in p.u).
NERC_NUM | RARF_HUB | generation |  | NERC Number.
NET_INTERCHNG_MVAR_UNIT | RARF_HUB | generation |  | Unit's Net interchange MVAR.
NET_INTERCHNG_MW_UNIT | RARF_HUB | generation |  | Unit's Net interchange MVW.
NETMAXLAG | RARF_HUB | generation |  | Net Maximum Lagging Operating Capability (MVAR).
NETMAXLEAD | RARF_HUB | generation |  | Net Maximum Leading Operating Capability (MVAR).
OFREQ_TRIP_HZ1 | RARF_HUB | generation |  | Over frequency Protection Setting- HZ1.
OFREQ_TRIP_HZ2 | RARF_HUB | generation |  | Over frequency Protection Setting- HZ2.
OFREQ_TRIP_HZ3 | RARF_HUB | generation |  | Over frequency Protection Setting- HZ3.
OFREQ_TRIP_HZ4 | RARF_HUB | generation |  | Over frequency Protection Setting- HZ4.
OFREQ_TRIP_INSTANT | RARF_HUB | generation |  | Instantaneous Over frequency Trip.
OFREQ_TRIP_TIME1 | RARF_HUB | generation |  | Over frequency Protection Setting- TIME1.
OFREQ_TRIP_TIME2 | RARF_HUB | generation |  | Over frequency Protection Setting- TIME2.
OFREQ_TRIP_TIME3 | RARF_HUB | generation |  | Over frequency Protection Setting- TIME3.
OFREQ_TRIP_TIME4 | RARF_HUB | generation |  | Over frequency Protection Setting- TIME4.
OVER_EXCITN_LIMITER_FLG | RARF_HUB | generation |  | This column is not being used.
OVER_EXCITN_LIMITER_FORM_FLG | RARF_HUB | generation |  | This column is not being used.
OVOLT_TRIP_INSTANT | RARF_HUB | generation |  | Instantaneous Overvoltage Trip.
OVOLT_TRIP_TIME1 | RARF_HUB | generation |  | Overvoltage Trip Time setting 1.
OVOLT_TRIP_TIME2 | RARF_HUB | generation |  | Overvoltage Trip Time setting 2.
OVOLT_TRIP_TIME3 | RARF_HUB | generation |  | Overvoltage Trip Time setting 3.
OVOLT_TRIP_TIME4 | RARF_HUB | generation |  | Overvoltage Trip Time setting 4.
OVOLT_TRIP_VOLT1 | RARF_HUB | generation |  | Overvoltage Trip Voltage setting 1.
OVOLT_TRIP_VOLT2 | RARF_HUB | generation |  | Overvoltage Trip Voltage setting 2.
OVOLT_TRIP_VOLT3 | RARF_HUB | generation |  | Overvoltage Trip Voltage setting 3.
OVOLT_TRIP_VOLT4 | RARF_HUB | generation |  | Overvoltage Trip Voltage setting 4.
PHYS_UNIT_TYPE | RARF_HUB | generation |  | Physical Unit Type.
POSITIVE_SEQ_Z_R_PU | RARF_HUB | generation |  | Positive Sequence Impedance (R in P.U).
POSITIVE_SEQ_Z_X_PU | RARF_HUB | generation |  | Positive Sequence Impedance (X in P.U).
PRIM_FUELTYPE | RARF_HUB | generation |  | Primary Fuel type for the Unit.
PSS_FLG | RARF_HUB | generation |  | This column is not being used.
PSSFORM_FLG | RARF_HUB | generation |  | This column is not being used.
PUC_NUM | RARF_HUB | generation |  | PUCT Number.
QUAL_FACILITY_FLG | RARF_HUB | generation |  | Qualifying Facility Flag : Y or N.
RENEWABLE_FLG | RARF_HUB | generation |  | Renewable Flag : Y or N.
RENEWABLE_OFFSET | RARF_HUB | generation |  | Renewable Off-set Flag: Y or N.
RES_CATG | RARF_HUB | generation |  | Resource Category.
ROTOR_Z_R_PU | RARF_HUB | generation |  | This column is not being used.
ROTOR_Z_X_PU | RARF_HUB | generation |  | This column is not being used.
RTG_MVAR | RARF_HUB | generation |  | Reactive Power Rating.
RTG_MW | RARF_HUB | generation |  | Real Power Rating.
SEASON_NET_MAX_EMGY_RTG_FL | RARF_HUB | generation |  | Seasonal Net Maximum Emergency Rating -Fall (MW).
SEASON_NET_MAX_EMGY_RTG_SM | RARF_HUB | generation |  | Seasonal Net Maximum Emergency Rating -Summer (MW).
SEASON_NET_MAX_EMGY_RTG_SP | RARF_HUB | generation |  | Seasonal Net Maximum Emergency Rating -Spring (MW).
SEASON_NET_MAX_EMGY_RTG_WT | RARF_HUB | generation |  | Seasonal Net Maximum Emergency Rating -Winter (MW).
SEASON_NET_MAX_SUST_RTG_FL | RARF_HUB | generation |  | Seasonal Net Maximum Sustainable Rating -Fall (MW).
SEASON_NET_MAX_SUST_RTG_SM | RARF_HUB | generation |  | Seasonal Net Maximum Sustainable Rating -Summer (MW).
SEASON_NET_MAX_SUST_RTG_SP | RARF_HUB | generation |  | Seasonal Net Maximum Sustainable Rating -Spring (MW).
SEASON_NET_MAX_SUST_RTG_WT | RARF_HUB | generation |  | Seasonal Net Maximum Sustainable Rating -Winter (MW).
SEASON_NET_MIN_EMGY_RTG_FL | RARF_HUB | generation |  | Seasonal Net Minimum Emergency Rating -Fall (MW).
SEASON_NET_MIN_EMGY_RTG_SM | RARF_HUB | generation |  | Seasonal Net Minimum Emergency Rating -Summer (MW).
SEASON_NET_MIN_EMGY_RTG_SP | RARF_HUB | generation |  | Seasonal Net Minimum Emergency Rating -Spring (MW).
SEASON_NET_MIN_EMGY_RTG_WT | RARF_HUB | generation |  | Seasonal Net Minimum Emergency Rating -Winter (MW).
SEASON_NET_MIN_SUST_RTG_FL | RARF_HUB | generation |  | Seasonal Net Minimum Sustainable Rating -Fall (MW).
SEASON_NET_MIN_SUST_RTG_SM | RARF_HUB | generation |  | Seasonal Net Minimum Sustainable Rating - Summer (MW).
SEASON_NET_MIN_SUST_RTG_SP | RARF_HUB | generation |  | Seasonal Net Minimum Sustainable Rating - Spring (MW).
SEASON_NET_MIN_SUST_RTG_WT | RARF_HUB | generation |  | Seasonal Net Minimum Sustainable Rating - Winter (MW).
SEC_FUELTYPE | RARF_HUB | generation |  | Secondary Fuel Type.
SITE_CODE | RARF_HUB | generation |  | Unique Code for Resource Site.
TURB_GOVNR_FORM_FLG | RARF_HUB | generation |  | This column is not being used.
TURBINE_RTG | RARF_HUB | generation |  | Turbine Rating.
UFREQ_TRIP_HZ1 | RARF_HUB | generation |  | Under frequency Protection Setting- HZ1.
UFREQ_TRIP_HZ2 | RARF_HUB | generation |  | Under frequency Protection Setting- HZ2.
UFREQ_TRIP_HZ3 | RARF_HUB | generation |  | Under frequency Protection Setting- HZ3.
UFREQ_TRIP_HZ4 | RARF_HUB | generation |  | Under frequency Protection Setting- HZ4.
UFREQ_TRIP_INSTANT | RARF_HUB | generation |  | Instantaneous Under frequency Trip.
UFREQ_TRIP_TIME1 | RARF_HUB | generation |  | Under frequency Protection Setting- TIME1.
UFREQ_TRIP_TIME2 | RARF_HUB | generation |  | Under frequency Protection Setting- TIME2.
UFREQ_TRIP_TIME3 | RARF_HUB | generation |  | Under frequency Protection Setting- TIME3.
UFREQ_TRIP_TIME4 | RARF_HUB | generation |  | Under frequency Protection Setting- TIME4.
UNDER_EXCITN_LIMITER_FLG | RARF_HUB | generation |  | This column is not being used.
UNDER_EXCITN_LIMITER_FORM_FLG | RARF_HUB | generation |  | This column is not being used.
UNIT_CODE | RARF_HUB | generation |  | Concatenated Mnemonic of Resource Site Code and Unit name (e.g CBY_CBYG1).
UNIT_END_DT | RARF_HUB | generation |  | Unit Termination Date( MM/DD/YYYY ).
UNIT_KV | RARF_HUB | generation |  | Unit Generating Voltage.
UNIT_NAME | RARF_HUB | generation |  | Unit Name.
UNIT_START_DT | RARF_HUB | generation |  | Unit Commercial Operations Date. It is the date on which Generator declares that the construction of the Plant has been substantially completed, Trial Operation of the Plant has been completed, and the Plant is ready for dispatch. Format is MM/DD/YYYY.
UVOLT_TRIP_INSTANT | RARF_HUB | generation |  | Instantaneous Under voltage Trip.
UVOLT_TRIP_TIME1 | RARF_HUB | generation |  | Under Voltage Protection Setting- TIME1.
UVOLT_TRIP_TIME2 | RARF_HUB | generation |  | Under Voltage Protection Setting- TIME2.
UVOLT_TRIP_TIME3 | RARF_HUB | generation |  | Under Voltage Protection Setting- TIME3.
UVOLT_TRIP_TIME4 | RARF_HUB | generation |  | Under Voltage Protection Setting- TIME4.
UVOLT_TRIP_VOLT1 | RARF_HUB | generation |  | Under Voltage Protection Setting- VOLT1.
UVOLT_TRIP_VOLT2 | RARF_HUB | generation |  | Under Voltage Protection Setting- VOLT2.
UVOLT_TRIP_VOLT3 | RARF_HUB | generation |  | Under Voltage Protection Setting- VOLT3.
UVOLT_TRIP_VOLT4 | RARF_HUB | generation |  | Under Voltage Protection Setting- VOLT4.
ZERO_SEQ_Z_R_PU | RARF_HUB | generation |  | Zero Sequence Z ( R in P.U).
ZERO_SEQ_Z_X_PU | RARF_HUB | generation |  | zero Sequence Z ( X in P.U).
AGR_MW_MDL_RTG | RARF_HUB | GENERATION |  | MW Rating for this Aggregated Generation Resource | Added 06/27/2012
AGR_NUM | RARF_HUB | GENERATION |  | Number of this type of Aggregated Generation Resource | Added 06/27/2012
AGR_TYPE | RARF_HUB | GENERATION |  | Aggregated Generation Resource(Manufacturer/Model) | Added 06/27/2012
AUX_LOAD_PWR_FACT | RARF_HUB | GENERATION |  | Auxilary Load Power Factor | Added 06/27/2012
DESIGN_MAX_AMB_TEMP | RARF_HUB | GENERATION |  | Design Max Ambient Temperature | Added 06/27/2012
DESIGN_MIN_AMB_TEMP | RARF_HUB | GENERATION |  | Design Min Ambient Temperature | Added 06/27/2012
DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED | RARF_HUB | GENERATION |  | Direct Axis Subtransient Reactance, X"dv (saturated) | Added 06/27/2012
DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED | RARF_HUB | GENERATION |  | Direct Axis Transient Reactance, X'dv (saturated) | Added 06/27/2012
DOES_ZERO_SEQ_EXIST | RARF_HUB | GENERATION |  | Does Zero Sequence Z exist? | Added 06/27/2012
GOV_DEAD_BND | RARF_HUB | GENERATION |  | Governor Dead-band | Added 06/27/2012
GOV_DROOP | RARF_HUB | GENERATION |  | Governor Droop Setting | Added 06/27/2012
LAT_CENTER_PLT | RARF_HUB | GENERATION |  | Latitude Of Center Of Plant | Added 06/27/2012
LONG_CENTER_PLT | RARF_HUB | GENERATION |  | Longitude Of Center Of Plant | Added 06/27/2012
NEGATIVE_SEQ_Z_R_PU | RARF_HUB | GENERATION |  | Negative Sequence Z (saturated) | Added 06/27/2012
NEGATIVE_SEQ_Z_X_PU | RARF_HUB | GENERATION |  | Negative Sequence Z (saturated) | Added 06/27/2012
NON_MOD_GEN | RARF_HUB | GENERATION |  | Non_Modeled Generator | Added 06/27/2012
POSITIVE_SEQ_Z_R_PU | RARF_HUB | GENERATION |  | Positive Sequence Z (saturated) | Added 06/27/2012
POSITIVE_SEQ_Z_X_PU | RARF_HUB | GENERATION |  | Positive Sequence Z (saturated) | Added 06/27/2012
PTI_BUS_NUM | RARF_HUB | GENERATION |  | PTI Bus Number | Added 06/27/2012
REACT_CAPB_DATA_GROSS_VAL | RARF_HUB | GENERATION |  | Reactive Capability Data Provided Below Is Gross Values? | Added 06/27/2012
REACT_CAPB_NDCRC_TEST_DATA | RARF_HUB | GENERATION |  | Reactive Capability Data Provided Below Is From NDCRC Test Data? | Added 06/27/2012
REACT_CAPB_NDCRC_TEST_DATA_DT | RARF_HUB | GENERATION |  | If Reactive Capability Data Provided Below Is From NDCRC Test Data Then Enter The Date On Which The Test Was Performed. | Added 06/27/2012
SGIA_SIGA_DT | RARF_HUB | GENERATION |  | Standard Generation Interconnection Agreement (SGIA) Signature Date | Added 06/27/2012
SUBSTAT_CODE_SUB_MNEMONIC | RARF_HUB | GENERATION |  | SubStation Code/SubStation Mnemonic | Added 06/27/2012
TRANS_ONLY_DT | RARF_HUB | GENERATION |  | Transmission Only Date (POI) | Added 06/27/2012
UNIT_CODE | RARF_HUB | GENERATION |  | Resource Name (Unit Code/Mnemonic) | Added 06/27/2012
UNIT_MRD_ST_DT | RARF_HUB | GENERATION |  | Unit Start Date (Model Ready Date) | Added 06/27/2012
VOL_LEV | RARF_HUB | GENERATION |  | Voltage Level | Added 06/27/2012
ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU | RARF_HUB | GENERATION |  | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Added 06/27/2012
ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU | RARF_HUB | GENERATION |  | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Added 06/27/2012
ZERO_SEQ_Z_R_PU | RARF_HUB | GENERATION |  | Zero Sequence Z (saturated) | Added 06/27/2012
ZERO_SEQ_Z_X_PU | RARF_HUB | GENERATION |  | Zero Sequence Z (saturated) | Added 06/27/2012
APPROVED_DATE | RARF_HUB | generation_HIST | History Table: All Approved and Disapproved Generation Resources Unit Information Details. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All Approved and Disapproved Generation Resources Unit Information Details.
ARMATURE_Z_R_PU | RARF_HUB | generation_HIST |  | Stator impedance value (R in P.U).
ARMATURE_Z_X_PU | RARF_HUB | generation_HIST |  | Stator impedance value (X in P.U).
AUX_MVARTOTAL | RARF_HUB | generation_HIST |  | Average MVAR for Auxiliary Load.
AUX_MWTOTAL | RARF_HUB | generation_HIST |  | Average MW for Auxiliary Load.
AUXMVAR_DISCHARGE_PCT | RARF_HUB | generation_HIST |  | Generation Auxiliary Load Characteristics for MVAR Load - Discharge Lighting, percent of total MVAR load.
AUXMVAR_LARGEMTR_PCT | RARF_HUB | generation_HIST |  | Generation Auxiliary Load Characteristics for MVAR Load - Large Motor, percent of total MVAR load.
AUXMVAR_OTHER_PCT | RARF_HUB | generation_HIST |  | Generation Auxiliary Load Characteristics for MVAR Load - Other, percent of total MVAR load.
AUXMVAR_SMALLMTR_PCT | RARF_HUB | generation_HIST |  | Generation Auxiliary Load Characteristics for MVAR Load - Small Motor, percent of total MVAR load.
AUXMW_DISCHARGE_PCT | RARF_HUB | generation_HIST |  | Generation Auxiliary Load Characteristics for MW Load - Discharge Lighting, percent of total MW load.
AUXMW_LARGEMTR_PCT | RARF_HUB | generation_HIST |  | Generation Auxiliary Load Characteristics for MW Load - Large Motor, percent of total MW load.
AUXMW_OTHER_PCT | RARF_HUB | generation_HIST |  | Generation Auxiliary Load Characteristics for MW Load - Other, percent of total MW load.
AUXMW_RESISTIVE_PCT | RARF_HUB | generation_HIST |  | Generation Auxiliary Load Characteristics for MW Load - Resistive (Heating) Load, percent of total MW load.
AUXMW_SMALLMTR_PCT | RARF_HUB | generation_HIST |  | Generation Auxiliary Load Characteristics for MW Load - Small Motor, percent of total MW load.
AVG_LD_MVAR_UNIT | RARF_HUB | generation_HIST |  | Average Amount of Auxiliary Reactive Power.
AVG_LD_MW_UNIT | RARF_HUB | generation_HIST |  | Average Amount of Auxiliary Real Power.
BREAKER_INTERRUP | RARF_HUB | generation_HIST |  | Breaker Interruption Time.
COLDSTART | RARF_HUB | generation_HIST |  | Cold Start Time.
COMPSTR_FLG | RARF_HUB | generation_HIST |  | This column is not being used.
COMPSTR_FORM_FLG | RARF_HUB | generation_HIST |  | This column is not being used.
DATE_LOADED | RARF_HUB | generation_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | generation_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DIRECT_AXIS_SUBSTNT_REACTANCE | RARF_HUB | generation_HIST |  | Direct Axis Sub transient reactance, X"di.
DIRECT_AXIS_TRANSNT_REACTANCE | RARF_HUB | generation_HIST |  | Direct Axis Transient reactance, X'di.
ERCOT_INTRCONN_PROJ_NUM | RARF_HUB | generation_HIST |  | ERCOT Interconnection Project Number.
EXCITN_FORM_FLG | RARF_HUB | generation_HIST |  | This column is not being used.
FUEL_TRANSTYPE | RARF_HUB | generation_HIST |  | This column is not being used.
GEN_FORM_FLG | RARF_HUB | generation_HIST |  | This column is not being used.
GROSS_CAPBLTY_MVAR_UNIT | RARF_HUB | generation_HIST |  | Gross Capability (MVAR).
GROSS_CAPBLTY_MW_UNIT | RARF_HUB | generation_HIST |  | Gross Capability (MW).
HOT_TO_INTMDT_TIME | RARF_HUB | generation_HIST |  | Hot to Intermediate Start Time.
HOTSTART | RARF_HUB | generation_HIST |  | Hot Start Time.
HR_LMT | RARF_HUB | generation_HIST |  | High Reasonability Limit.
HR_RAMPRATE_LMT | RARF_HUB | generation_HIST |  | High Reasonability Ramp Rate limit.
HYDROCOOLED | RARF_HUB | generation_HIST |  | hydro cooled.
INTERMSTART | RARF_HUB | generation_HIST |  | Intermediate Start Time.
INTMDT_TO_COLD_TIME | RARF_HUB | generation_HIST |  | Intermediate to Cold time.
KVBASE | RARF_HUB | generation_HIST |  | What is the kV base that the following data is based on?.
LOAD_TRIP_FLG | RARF_HUB | generation_HIST |  | Load Trip Flag.
LOAD_TRIP_PCT | RARF_HUB | generation_HIST |  | Load Trip percent.
LR_LMT | RARF_HUB | generation_HIST |  | Low Reasonability Limit.
LR_RAMP_RATE_LMT | RARF_HUB | generation_HIST |  | Low Reasonability Ramp rate Limit.
MACHINE_IMPEDANCE_R_PU | RARF_HUB | generation_HIST |  | This column is not being used.
MACHINE_IMPEDANCE_X_PU | RARF_HUB | generation_HIST |  | This column is not being used.
MAX_ONLINE_TIME | RARF_HUB | generation_HIST |  | Maximum Online Time.
MAXDLYSTARTS | RARF_HUB | generation_HIST |  | Maximum Daily Starts.
MAXWKLYENRGY | RARF_HUB | generation_HIST |  | Maximum Weekly Energy.
MAXWKLYSTARTS | RARF_HUB | generation_HIST |  | Maximum Weekly Starts.
MFR_CAPABILITY_CURVE_FLG | RARF_HUB | generation_HIST |  | Manufactured Capability Curve Flag.
MIN_OFFLINE_TIME | RARF_HUB | generation_HIST |  | Minimum Off-line Time.
MIN_ONLINE_TIME | RARF_HUB | generation_HIST |  | Minimum On-line Time.
MUTUAL_COUPLING_Z_R_PU | RARF_HUB | generation_HIST |  | This column is not being used.
MUTUAL_COUPLING_Z_X_PU | RARF_HUB | generation_HIST |  | This column is not being used.
MVABASE | RARF_HUB | generation_HIST |  | What is the MVA base that the following data is based on?.
MVAR1LAG | RARF_HUB | generation_HIST |  | Unit's Lagging reactive power output capability associated with its MW1 output, in MVAR
MVAR1LEAD | RARF_HUB | generation_HIST |  | Unit's Leading reactive power output capability associated with its MW1 output, in MVAR; input as negative number.
MVAR2LAG | RARF_HUB | generation_HIST |  | Unit's Lagging reactive power output capability associated with its MW2 output, in MVAR
MVAR2LEAD | RARF_HUB | generation_HIST |  | Unit's Leading reactive power output capability associated with its MW2 output, in MVAR; input as negative number.
MVAR3LAG | RARF_HUB | generation_HIST |  | Unit's Lagging reactive power output capability associated with its MW3 output, in MVAR
MVAR3LEAD | RARF_HUB | generation_HIST |  | Unit's Leading reactive power output capability associated with its MW3 output, in MVAR; input as negative number.
MVAR4LAG | RARF_HUB | generation_HIST |  | Unit's Lagging reactive power output capability associated with its MW4 output, in MVAR
MVAR4LEAD | RARF_HUB | generation_HIST |  | Unit's Leading reactive power output capability associated with its MW4 output, in MVAR; input as negative number.
MW1 | RARF_HUB | generation_HIST |  | Reactive Capability curve - point on curve of MW output for this unit, MW1.
MW2 | RARF_HUB | generation_HIST |  | Reactive Capability curve - point on curve of MW output for this unit, MW2.
MW3 | RARF_HUB | generation_HIST |  | Reactive Capability curve - point on curve of MW output for this unit, MW3.
MW4 | RARF_HUB | generation_HIST |  | Reactive Capability curve - point on curve of MW output for this unit, MW4.
MW5UNITYPF | RARF_HUB | generation_HIST |  | From the Reactive Capability curve - the MW output at Unity Power Factor (zero MVAR).
NAME_PLT_RTG | RARF_HUB | generation_HIST |  | Name Plate Rating of the Unit.
NEGATIVE_SEQ_Z_R_PU | RARF_HUB | generation_HIST |  | Negative Sequence Impedance ( R in p.u).
NEGATIVE_SEQ_Z_X_PU | RARF_HUB | generation_HIST |  | Negative Sequence Impedance ( X in p.u).
NERC_NUM | RARF_HUB | generation_HIST |  | NERC Number.
NET_INTERCHNG_MVAR_UNIT | RARF_HUB | generation_HIST |  | Unit's Net interchange MVAR.
NET_INTERCHNG_MW_UNIT | RARF_HUB | generation_HIST |  | Unit's Net interchange MVW.
NETMAXLAG | RARF_HUB | generation_HIST |  | Net Maximum Lagging Operating Capability (MVAR).
NETMAXLEAD | RARF_HUB | generation_HIST |  | Net Maximum Leading Operating Capability (MVAR).
OFREQ_TRIP_HZ1 | RARF_HUB | generation_HIST |  | Over frequency Protection Setting- HZ1.
OFREQ_TRIP_HZ2 | RARF_HUB | generation_HIST |  | Over frequency Protection Setting- HZ2.
OFREQ_TRIP_HZ3 | RARF_HUB | generation_HIST |  | Over frequency Protection Setting- HZ3.
OFREQ_TRIP_HZ4 | RARF_HUB | generation_HIST |  | Over frequency Protection Setting- HZ4.
OFREQ_TRIP_INSTANT | RARF_HUB | generation_HIST |  | Instantaneous Over frequency Trip.
OFREQ_TRIP_TIME1 | RARF_HUB | generation_HIST |  | Over frequency Protection Setting- TIME1.
OFREQ_TRIP_TIME2 | RARF_HUB | generation_HIST |  | Over frequency Protection Setting- TIME2.
OFREQ_TRIP_TIME3 | RARF_HUB | generation_HIST |  | Over frequency Protection Setting- TIME3.
OFREQ_TRIP_TIME4 | RARF_HUB | generation_HIST |  | Over frequency Protection Setting- TIME4.
OVER_EXCITN_LIMITER_FLG | RARF_HUB | generation_HIST |  | This column is not being used.
OVER_EXCITN_LIMITER_FORM_FLG | RARF_HUB | generation_HIST |  | This column is not being used.
OVOLT_TRIP_INSTANT | RARF_HUB | generation_HIST |  | Instantaneous Overvoltage Trip.
OVOLT_TRIP_TIME1 | RARF_HUB | generation_HIST |  | Overvoltage Trip Time setting 1.
OVOLT_TRIP_TIME2 | RARF_HUB | generation_HIST |  | Overvoltage Trip Time setting 2.
OVOLT_TRIP_TIME3 | RARF_HUB | generation_HIST |  | Overvoltage Trip Time setting 3.
OVOLT_TRIP_TIME4 | RARF_HUB | generation_HIST |  | Overvoltage Trip Time setting 4.
OVOLT_TRIP_VOLT1 | RARF_HUB | generation_HIST |  | Overvoltage Trip Voltage setting 1.
OVOLT_TRIP_VOLT2 | RARF_HUB | generation_HIST |  | Overvoltage Trip Voltage setting 2.
OVOLT_TRIP_VOLT3 | RARF_HUB | generation_HIST |  | Overvoltage Trip Voltage setting 3.
OVOLT_TRIP_VOLT4 | RARF_HUB | generation_HIST |  | Overvoltage Trip Voltage setting 4.
PHYS_UNIT_TYPE | RARF_HUB | generation_HIST |  | Physical Unit Type.
POSITIVE_SEQ_Z_R_PU | RARF_HUB | generation_HIST |  | Positive Sequence Impedance (R in P.U).
POSITIVE_SEQ_Z_X_PU | RARF_HUB | generation_HIST |  | Positive Sequence Impedance (X in P.U).
PRIM_FUELTYPE | RARF_HUB | generation_HIST |  | Primary Fuel type for the Unit.
PSS_FLG | RARF_HUB | generation_HIST |  | This column is not being used.
PSSFORM_FLG | RARF_HUB | generation_HIST |  | This column is not being used.
PUC_NUM | RARF_HUB | generation_HIST |  | PUCT Number.
QUAL_FACILITY_FLG | RARF_HUB | generation_HIST |  | Qualifying Facility Flag : Y or N.
RENEWABLE_FLG | RARF_HUB | generation_HIST |  | Renewable Flag : Y or N.
RENEWABLE_OFFSET | RARF_HUB | generation_HIST |  | Renewable Off-set Flag: Y or N.
RES_CATG | RARF_HUB | generation_HIST |  | Resource Category.
ROTOR_Z_R_PU | RARF_HUB | generation_HIST |  | This column is not being used.
ROTOR_Z_X_PU | RARF_HUB | generation_HIST |  | This column is not being used.
RTG_MVAR | RARF_HUB | generation_HIST |  | Reactive Power Rating.
RTG_MW | RARF_HUB | generation_HIST |  | Real Power Rating.
SEASON_NET_MAX_EMGY_RTG_FL | RARF_HUB | generation_HIST |  | Seasonal Net Maximum Emergency Rating -Fall (MW).
SEASON_NET_MAX_EMGY_RTG_SM | RARF_HUB | generation_HIST |  | Seasonal Net Maximum Emergency Rating -Summer (MW).
SEASON_NET_MAX_EMGY_RTG_SP | RARF_HUB | generation_HIST |  | Seasonal Net Maximum Emergency Rating -Spring (MW).
SEASON_NET_MAX_EMGY_RTG_WT | RARF_HUB | generation_HIST |  | Seasonal Net Maximum Emergency Rating -Winter (MW).
SEASON_NET_MAX_SUST_RTG_FL | RARF_HUB | generation_HIST |  | Seasonal Net Maximum Sustainable Rating -Fall (MW).
SEASON_NET_MAX_SUST_RTG_SM | RARF_HUB | generation_HIST |  | Seasonal Net Maximum Sustainable Rating -Summer (MW).
SEASON_NET_MAX_SUST_RTG_SP | RARF_HUB | generation_HIST |  | Seasonal Net Maximum Sustainable Rating -Spring (MW).
SEASON_NET_MAX_SUST_RTG_WT | RARF_HUB | generation_HIST |  | Seasonal Net Maximum Sustainable Rating -Winter (MW).
SEASON_NET_MIN_EMGY_RTG_FL | RARF_HUB | generation_HIST |  | Seasonal Net Minimum Emergency Rating -Fall (MW).
SEASON_NET_MIN_EMGY_RTG_SM | RARF_HUB | generation_HIST |  | Seasonal Net Minimum Emergency Rating -Summer (MW).
SEASON_NET_MIN_EMGY_RTG_SP | RARF_HUB | generation_HIST |  | Seasonal Net Minimum Emergency Rating -Spring (MW).
SEASON_NET_MIN_EMGY_RTG_WT | RARF_HUB | generation_HIST |  | Seasonal Net Minimum Emergency Rating -Winter (MW).
SEASON_NET_MIN_SUST_RTG_FL | RARF_HUB | generation_HIST |  | Seasonal Net Minimum Sustainable Rating -Fall (MW).
SEASON_NET_MIN_SUST_RTG_SM | RARF_HUB | generation_HIST |  | Seasonal Net Minimum Sustainable Rating - Summer (MW).
SEASON_NET_MIN_SUST_RTG_SP | RARF_HUB | generation_HIST |  | Seasonal Net Minimum Sustainable Rating - Spring (MW).
SEASON_NET_MIN_SUST_RTG_WT | RARF_HUB | generation_HIST |  | Seasonal Net Minimum Sustainable Rating - Winter (MW).
SEC_FUELTYPE | RARF_HUB | generation_HIST |  | Secondary Fuel Type.
SITE_CODE | RARF_HUB | generation_HIST |  | Unique Code for Resource Site.
SUBMISSION_TYPE | RARF_HUB | generation_HIST |  | Submission Type: Internal or External.
TURB_GOVNR_FORM_FLG | RARF_HUB | generation_HIST |  | This column is not being used.
TURBINE_RTG | RARF_HUB | generation_HIST |  | Turbine Rating.
UFREQ_TRIP_HZ1 | RARF_HUB | generation_HIST |  | Under frequency Protection Setting- HZ1.
UFREQ_TRIP_HZ2 | RARF_HUB | generation_HIST |  | Under frequency Protection Setting- HZ2.
UFREQ_TRIP_HZ3 | RARF_HUB | generation_HIST |  | Under frequency Protection Setting- HZ3.
UFREQ_TRIP_HZ4 | RARF_HUB | generation_HIST |  | Under frequency Protection Setting- HZ4.
UFREQ_TRIP_INSTANT | RARF_HUB | generation_HIST |  | Instantaneous Under frequency Trip.
UFREQ_TRIP_TIME1 | RARF_HUB | generation_HIST |  | Under frequency Protection Setting- TIME1.
UFREQ_TRIP_TIME2 | RARF_HUB | generation_HIST |  | Under frequency Protection Setting- TIME2.
UFREQ_TRIP_TIME3 | RARF_HUB | generation_HIST |  | Under frequency Protection Setting- TIME3.
UFREQ_TRIP_TIME4 | RARF_HUB | generation_HIST |  | Under frequency Protection Setting- TIME4.
UNDER_EXCITN_LIMITER_FLG | RARF_HUB | generation_HIST |  | This column is not being used.
UNDER_EXCITN_LIMITER_FORM_FLG | RARF_HUB | generation_HIST |  | This column is not being used.
UNIT_CODE | RARF_HUB | generation_HIST |  | Concatenated Mnemonic of Resource Site Code and Unit name (e.g CBY_CBYG1).
UNIT_END_DT | RARF_HUB | generation_HIST |  | Unit Termination Date( MM/DD/YYYY ).
UNIT_KV | RARF_HUB | generation_HIST |  | Unit Generating Voltage.
UNIT_NAME | RARF_HUB | generation_HIST |  | Unit Name.
UNIT_START_DT | RARF_HUB | generation_HIST |  | Unit Commercial Operations Date. It is the date on which Generator declares that the construction of the Plant has been substantially completed, Trial Operation of the Plant has been completed, and the Plant is ready for dispatch. Format is MM/DD/YYYY.
UVOLT_TRIP_INSTANT | RARF_HUB | generation_HIST |  | Instantaneous Under voltage Trip.
UVOLT_TRIP_TIME1 | RARF_HUB | generation_HIST |  | Under Voltage Protection Setting- TIME1.
UVOLT_TRIP_TIME2 | RARF_HUB | generation_HIST |  | Under Voltage Protection Setting- TIME2.
UVOLT_TRIP_TIME3 | RARF_HUB | generation_HIST |  | Under Voltage Protection Setting- TIME3.
UVOLT_TRIP_TIME4 | RARF_HUB | generation_HIST |  | Under Voltage Protection Setting- TIME4.
UVOLT_TRIP_VOLT1 | RARF_HUB | generation_HIST |  | Under Voltage Protection Setting- VOLT1.
UVOLT_TRIP_VOLT2 | RARF_HUB | generation_HIST |  | Under Voltage Protection Setting- VOLT2.
UVOLT_TRIP_VOLT3 | RARF_HUB | generation_HIST |  | Under Voltage Protection Setting- VOLT3.
UVOLT_TRIP_VOLT4 | RARF_HUB | generation_HIST |  | Under Voltage Protection Setting- VOLT4.
ZERO_SEQ_Z_R_PU | RARF_HUB | generation_HIST |  | Zero Sequence Z ( R in P.U).
ZERO_SEQ_Z_X_PU | RARF_HUB | generation_HIST |  | zero Sequence Z ( X in P.U).
AGR_MW_MDL_RTG | RARF_HUB | GENERATION_HIST |  | MW Rating for this Aggregated Generation Resource | Added 06/27/2012
AGR_NUM | RARF_HUB | GENERATION_HIST |  | Number of this type of Aggregated Generation Resource | Added 06/27/2012
AGR_TYPE | RARF_HUB | GENERATION_HIST |  | Aggregated Generation Resource(Manufacturer/Model) | Added 06/27/2012
AUX_LOAD_PWR_FACT | RARF_HUB | GENERATION_HIST |  | Auxilary Load Power Factor | Added 06/27/2012
DESIGN_MAX_AMB_TEMP | RARF_HUB | GENERATION_HIST |  | Design Max Ambient Temperature | Added 06/27/2012
DESIGN_MIN_AMB_TEMP | RARF_HUB | GENERATION_HIST |  | Design Min Ambient Temperature | Added 06/27/2012
DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED | RARF_HUB | GENERATION_HIST |  | Direct Axis Subtransient Reactance, X"dv (saturated) | Added 06/27/2012
DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED | RARF_HUB | GENERATION_HIST |  | Direct Axis Transient Reactance, X'dv (saturated) | Added 06/27/2012
DOES_ZERO_SEQ_EXIST | RARF_HUB | GENERATION_HIST |  | Does Zero Sequence Z exist? | Added 06/27/2012
GOV_DEAD_BND | RARF_HUB | GENERATION_HIST |  | Governor Dead-band | Added 06/27/2012
GOV_DROOP | RARF_HUB | GENERATION_HIST |  | Governor Droop Setting | Added 06/27/2012
LAT_CENTER_PLT | RARF_HUB | GENERATION_HIST |  | Latitude Of Center Of Plant | Added 06/27/2012
LONG_CENTER_PLT | RARF_HUB | GENERATION_HIST |  | Longitude Of Center Of Plant | Added 06/27/2012
NEGATIVE_SEQ_Z_R_PU | RARF_HUB | GENERATION_HIST |  | Negative Sequence Z (saturated) | Added 06/27/2012
NEGATIVE_SEQ_Z_X_PU | RARF_HUB | GENERATION_HIST |  | Negative Sequence Z (saturated) | Added 06/27/2012
NON_MOD_GEN | RARF_HUB | GENERATION_HIST |  | Non_Modeled Generator | Added 06/27/2012
POSITIVE_SEQ_Z_R_PU | RARF_HUB | GENERATION_HIST |  | Positive Sequence Z (saturated) | Added 06/27/2012
POSITIVE_SEQ_Z_X_PU | RARF_HUB | GENERATION_HIST |  | Positive Sequence Z (saturated) | Added 06/27/2012
PTI_BUS_NUM | RARF_HUB | GENERATION_HIST |  | PTI Bus Number | Added 06/27/2012
REACT_CAPB_DATA_GROSS_VAL | RARF_HUB | GENERATION_HIST |  | Reactive Capability Data Provided Below Is Gross Values? | Added 06/27/2012
REACT_CAPB_NDCRC_TEST_DATA | RARF_HUB | GENERATION_HIST |  | Reactive Capability Data Provided Below Is From NDCRC Test Data? | Added 06/27/2012
REACT_CAPB_NDCRC_TEST_DATA_DT | RARF_HUB | GENERATION_HIST |  | If Reactive Capability Data Provided Below Is From NDCRC Test Data Then Enter The Date On Which The Test Was Performed. | Added 06/27/2012
SGIA_SIGA_DT | RARF_HUB | GENERATION_HIST |  | Standard Generation Interconnection Agreement (SGIA) Signature Date | Added 06/27/2012
SUBSTAT_CODE_SUB_MNEMONIC | RARF_HUB | GENERATION_HIST |  | SubStation Code/SubStation Mnemonic | Added 06/27/2012
TRANS_ONLY_DT | RARF_HUB | GENERATION_HIST |  | Transmission Only Date (POI) | Added 06/27/2012
UNIT_CODE | RARF_HUB | GENERATION_HIST |  | Resource Name (Unit Code/Mnemonic) | Added 06/27/2012
UNIT_MRD_ST_DT | RARF_HUB | GENERATION_HIST |  | Unit Start Date (Model Ready Date) | Added 06/27/2012
VOL_LEV | RARF_HUB | GENERATION_HIST |  | Voltage Level | Added 06/27/2012
ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU | RARF_HUB | GENERATION_HIST |  | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Added 06/27/2012
ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU | RARF_HUB | GENERATION_HIST |  | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Added 06/27/2012
ZERO_SEQ_Z_R_PU | RARF_HUB | GENERATION_HIST |  | Zero Sequence Z (saturated) | Added 06/27/2012
ZERO_SEQ_Z_X_PU | RARF_HUB | GENERATION_HIST |  | Zero Sequence Z (saturated) | Added 06/27/2012
DATE_LOADED | RARF_HUB | GOVERNOR_PARAMETERS | Latest Approved Unit GOVERNOR_PARAMETERS Details. | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format). |  | Latest Approved Unit GOVERNOR_PARAMETERS Details.
DATE_SUBMITTED | RARF_HUB | GOVERNOR_PARAMETERS |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
FREQ_BIAS | RARF_HUB | GOVERNOR_PARAMETERS |  | Frequency Bias.
FREQ_DEVIATION_DEAD-BAND | RARF_HUB | GOVERNOR_PARAMETERS |  | Frequency Deviation Dead band.
JOCODE | RARF_HUB | GOVERNOR_PARAMETERS |  | Jointly Owned Unit Code.
RE_DUNS | RARF_HUB | GOVERNOR_PARAMETERS |  | Resource Entity Duns#.
RE_NAME | RARF_HUB | GOVERNOR_PARAMETERS |  | Resource Entity Name.
UNIT_CODE | RARF_HUB | GOVERNOR_PARAMETERS |  | Concatenated Mnemonic of Resource Site Code and Unit name (e.g CBY_CBYG1).
DATE_LOADED | RARF_HUB | GOVERNOR_PARAMETERS_HIST | History Table: All Approved and Disapproved Unit GOVERNOR_PARAMETERS Details. | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format). |  | History Table: All Approved and Disapproved Unit GOVERNOR_PARAMETERS Details.
DATE_SUBMITTED | RARF_HUB | GOVERNOR_PARAMETERS_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
FREQ_BIAS | RARF_HUB | GOVERNOR_PARAMETERS_HIST |  | Frequency Bias.
FREQ_DEVIATION_DEAD-BAND | RARF_HUB | GOVERNOR_PARAMETERS_HIST |  | Frequency Deviation Dead band.
JOCODE | RARF_HUB | GOVERNOR_PARAMETERS_HIST |  | Jointly Owned Unit Code.
RE_DUNS | RARF_HUB | GOVERNOR_PARAMETERS_HIST |  | Resource Entity Duns#.
RE_NAME | RARF_HUB | GOVERNOR_PARAMETERS_HIST |  | Resource Entity Name.
UNIT_CODE | RARF_HUB | GOVERNOR_PARAMETERS_HIST |  | Concatenated Mnemonic of Resource Site Code and Unit name (e.g CBY_CBYG1).
DATE_COMP | RARF_HUB | LD_RES_GENRL_INFO | Latest Approved General Information on Load Resources being registered. | Date when the RARF form is filled out.(MM/DD/YYYY Format). |  | Latest Approved General Information on Load Resources being registered.
DATE_LOADED | RARF_HUB | LD_RES_GENRL_INFO |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | LD_RES_GENRL_INFO |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
EMAIL_PC | RARF_HUB | LD_RES_GENRL_INFO |  | Email address of the Primary Contact for the RARF
FAX_PC | RARF_HUB | LD_RES_GENRL_INFO |  | Fax# of the Primary Contact for the RARF
NAME_PC | RARF_HUB | LD_RES_GENRL_INFO |  | Name of the Primary Contact for the RARF
PHONE_PC | RARF_HUB | LD_RES_GENRL_INFO |  | Ph# of the Primary Contact for the RARF
RE_DUNS | RARF_HUB | LD_RES_GENRL_INFO |  | Resource Entity Duns# Submitting the RARF
RE_SUB_FORM | RARF_HUB | LD_RES_GENRL_INFO |  | Resource Entity Name Submitting the RARF
SUBMIT_REASON | RARF_HUB | LD_RES_GENRL_INFO |  | Reason for Submittal: New, Delete Or Update
TITLE_PC | RARF_HUB | LD_RES_GENRL_INFO |  | Title of the Primary Contact for the RARF
APPROVED_DATE | RARF_HUB | LD_RES_GENRL_INFO_HIST | History Table: All approved and Disapproved General Information on Load Resources being registered. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. (MM/DD/YYYY Format). |  | History Table: All approved and Disapproved General Information on Load Resources being registered.
DATE_COMP | RARF_HUB | LD_RES_GENRL_INFO_HIST |  | Date when the RARF form is filled out.(MM/DD/YYYY Format).
DATE_LOADED | RARF_HUB | LD_RES_GENRL_INFO_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | LD_RES_GENRL_INFO_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
EMAIL_PC | RARF_HUB | LD_RES_GENRL_INFO_HIST |  | Email address of the Primary Contact for the RARF
FAX_PC | RARF_HUB | LD_RES_GENRL_INFO_HIST |  | Fax# of the Primary Contact for the RARF
NAME_PC | RARF_HUB | LD_RES_GENRL_INFO_HIST |  | Name of the Primary Contact for the RARF
PHONE_PC | RARF_HUB | LD_RES_GENRL_INFO_HIST |  | Ph# of the Primary Contact for the RARF
RE_DUNS | RARF_HUB | LD_RES_GENRL_INFO_HIST |  | Resource Entity Duns# Submitting the RARF
RE_SUB_FORM | RARF_HUB | LD_RES_GENRL_INFO_HIST |  | Resource Entity Name Submitting the RARF
SUBMISSION_TYPE | RARF_HUB | LD_RES_GENRL_INFO_HIST |  | Submission Type: Internal or External.
SUBMIT_REASON | RARF_HUB | LD_RES_GENRL_INFO_HIST |  | Reason for Submittal: New, Delete Or Update
TITLE_PC | RARF_HUB | LD_RES_GENRL_INFO_HIST |  | Title of the Primary Contact for the RARF
CODE_MW_ERRC | RARF_HUB | LD_RES_RAMPRATES_ERRC | Latest Approved Load Resources Emergency Ramp Rate Details. | Unique Code: Concatenation of Dispatch Asset Code _MW_NUMBER_ERRC. |  | Latest Approved Load Resources Emergency Ramp Rate Details.
DATE_LOADED | RARF_HUB | LD_RES_RAMPRATES_ERRC |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | LD_RES_RAMPRATES_ERRC |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DISPATCH_ASSET_CODE | RARF_HUB | LD_RES_RAMPRATES_ERRC |  | Mnemonic (Unique identifier) for each Load Resource.
DOWNWARD_RAMPRATE_ERRC | RARF_HUB | LD_RES_RAMPRATES_ERRC |  | Emergency Rate at which resource can decrease MW output in MW/minute for the given output level.
MW_NUMBER_ERRC | RARF_HUB | LD_RES_RAMPRATES_ERRC |  | MW Number (MW to MW10).
MW_RATING_ERRC | RARF_HUB | LD_RES_RAMPRATES_ERRC |  | MW Output.
UPWARD_RAMPRATE_ERRC | RARF_HUB | LD_RES_RAMPRATES_ERRC |  | Emergency Rate at which resource can increase MW output in MW/minute for the given output level (1-10 values).
APPROVED_DATE | RARF_HUB | LD_RES_RAMPRATES_ERRC_HIST | History Table: All approved and Disapproved Load Resources Emergency Ramp Rate Details. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved and Disapproved Load Resources Emergency Ramp Rate Details.
CODE_MW_ERRC | RARF_HUB | LD_RES_RAMPRATES_ERRC_HIST |  | Unique Code: Concatenation of Dispatch Asset Code _MW_NUMBER_ERRC.
DATE_LOADED | RARF_HUB | LD_RES_RAMPRATES_ERRC_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | LD_RES_RAMPRATES_ERRC_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DISPATCH_ASSET_CODE | RARF_HUB | LD_RES_RAMPRATES_ERRC_HIST |  | Mnemonic (Unique identifier) for each Load Resource.
DOWNWARD_RAMPRATE_ERRC | RARF_HUB | LD_RES_RAMPRATES_ERRC_HIST |  | Emergency Rate at which resource can decrease MW output in MW/minute for the given output level.
MW_NUMBER_ERRC | RARF_HUB | LD_RES_RAMPRATES_ERRC_HIST |  | MW Number (MW to MW10).
MW_RATING_ERRC | RARF_HUB | LD_RES_RAMPRATES_ERRC_HIST |  | MW Output.
SUBMISSION_TYPE | RARF_HUB | LD_RES_RAMPRATES_ERRC_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
UPWARD_RAMPRATE_ERRC | RARF_HUB | LD_RES_RAMPRATES_ERRC_HIST |  | Emergency Rate at which resource can increase MW output in MW/minute for the given output level (1-10 values).
CODE_MW_NRRC | RARF_HUB | LD_RES_RAMPRATES_NRRC | Latest Approved Load Resources Normal Ramp Rate Details. | Unique Code: Concatenation of Dispatch Asset Code _MW_NUMBER_NRRC. |  | Latest Approved Load Resources Normal Ramp Rate Details.
DATE_LOADED | RARF_HUB | LD_RES_RAMPRATES_NRRC |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | LD_RES_RAMPRATES_NRRC |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DISPATCH_ASSET_CODE | RARF_HUB | LD_RES_RAMPRATES_NRRC |  | Mnemonic (Unique identifier) for each Load Resource.
DOWNWARD_RAMPRATE_NRRC | RARF_HUB | LD_RES_RAMPRATES_NRRC |  | Normal Rate at which resource can decrease MW output in MW/minute for the given output level
MW_NUMBER_NRRC | RARF_HUB | LD_RES_RAMPRATES_NRRC |  | Normal Rate at which resource can increase MW output in MW/minute for the given output level
MW_RATING_NRRC | RARF_HUB | LD_RES_RAMPRATES_NRRC |  | MW Output.
UPWARD_RAMPRATE_NRRC | RARF_HUB | LD_RES_RAMPRATES_NRRC |  | Normal Rate at which resource can increase MW output in MW/minute for the given output level
APPROVED_DATE | RARF_HUB | LD_RES_RAMPRATES_NRRC_HIST | History Table: All approved and Disapproved Load Resources Normal Ramp Rate Details. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved and Disapproved Load Resources Normal Ramp Rate Details.
CODE_MW_NRRC | RARF_HUB | LD_RES_RAMPRATES_NRRC_HIST |  | Unique Code: Concatenation of Dispatch Asset Code _MW_NUMBER_NRRC.
DATE_LOADED | RARF_HUB | LD_RES_RAMPRATES_NRRC_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | LD_RES_RAMPRATES_NRRC_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DISPATCH_ASSET_CODE | RARF_HUB | LD_RES_RAMPRATES_NRRC_HIST |  | Mnemonic (Unique identifier) for each Load Resource.
DOWNWARD_RAMPRATE_NRRC | RARF_HUB | LD_RES_RAMPRATES_NRRC_HIST |  | Normal Rate at which resource can decrease MW output in MW/minute for the given output level
MW_NUMBER_NRRC | RARF_HUB | LD_RES_RAMPRATES_NRRC_HIST |  | Normal Rate at which resource can increase MW output in MW/minute for the given output level
MW_RATING_NRRC | RARF_HUB | LD_RES_RAMPRATES_NRRC_HIST |  | MW Output.
SUBMISSION_TYPE | RARF_HUB | LD_RES_RAMPRATES_NRRC_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
UPWARD_RAMPRATE_NRRC | RARF_HUB | LD_RES_RAMPRATES_NRRC_HIST |  | Normal Rate at which resource can increase MW output in MW/minute for the given output level
BUS_NUM_TO | RARF_HUB | LINE | Latest Approved Line Equipment Details. | TO STATION - Bus Number (PTI Bus Number). |  | Latest Approved Line Equipment Details.
BUSNUMBR_FROM | RARF_HUB | LINE |  | FROM STATION - Bus Number (PTI Bus Number).
CHANGE_DESCRIPTION | RARF_HUB | LINE |  | Description of Change, indicates if new Equipment is added; Existing Equipment is deleted or Updated
CHARGING_SUSC | RARF_HUB | LINE |  | Charging Susceptance in PU (100 MVA Base).
COMMENTS_LINE | RARF_HUB | LINE |  | General comments on LINE equipment.
CONTINUOUS_RTG | RARF_HUB | LINE |  | Nominal (Static) - Continuous Rating.
DATE_LOADED | RARF_HUB | LINE |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | LINE |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
EFF_DATE | RARF_HUB | LINE |  | Date when the Equipment will be effective in Model. Format: (MM/DD/YYYY).
EMGCY_RTG_2HR | RARF_HUB | LINE |  | Nominal (Static) - 2-hr Emergency Rating.
ERCOT_CODE_FROM | RARF_HUB | LINE |  | FROM STATION - ERCOT Station Code Mnemonic.
ERCOT_CODE_TO | RARF_HUB | LINE |  | TO STATION - ERCOT Station Code Mnemonic.
ERCOT_LINE_NAME | RARF_HUB | LINE |  | ERCOT Line Name.
INTERNAL_LINE_TO_FLG | RARF_HUB | LINE |  | Internal Line Flag (Y or N).
LINE_CODE | RARF_HUB | LINE |  | Unique Code for each Line equipment defined as the concatenation of SITE_CODE_ERCOT_CODE_FROM_Line Name.
LINE_RATING | RARF_HUB | LINE |  | Line Rating (Static or Dynamic).
LINE_VOLT_LVL | RARF_HUB | LINE |  | Line Voltage Level.
REACTANCE | RARF_HUB | LINE |  | Reactance in P.U. (100 MVA Base).
RESISTANCE | RARF_HUB | LINE |  | Resistance in P.U. (100 MVA Base).
RTG_15MIN | RARF_HUB | LINE |  | Nominal (Static) - 15-min Rating.
SEGMENT_LENGTH | RARF_HUB | LINE |  | Segment Length.
SITE_CODE | RARF_HUB | LINE |  | Unique Code for Resource Site ( eg:CBY).
TSPNAME_TO | RARF_HUB | LINE |  | TO STATION - TSP Name.
TYPE | RARF_HUB | LINE |  | Line Type (overhead / underground).
WEATHERZONE_FROM | RARF_HUB | LINE |  | FROM STATION - Weather Zone / Weather Station (used for Dynamic Ratings).
WEATHERZONE_TO | RARF_HUB | LINE |  | TO STATION - Weather Zone / Weather Station (used for Dynamic Ratings).
PLANNING_RATE_C | RARF_HUB | LINE |  | Planning Rate C | Added 06/27/2012
ZERO_ SEQ_ CHRG_ SUSECPTANCE_PU | RARF_HUB | LINE |  | Zero Sequence Charging Susceptance In P.u. (100mva Base) | Added 06/27/2012
ZERO_SEQ_LINE_REACTANCE_PU | RARF_HUB | LINE |  | Zero Sequence Line Reactance In P.u. (100mva Base) | Added 06/27/2012
ZERO_SEQ_LINE_RESISTANCE_PU | RARF_HUB | LINE |  | Zero Sequence Line Resistance In P.u. (100mva Base) | Added 06/27/2012
DATE_LOADED | RARF_HUB | LINE_DEVICES | Latest Approved Line Devices Details. | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format). |  | Latest Approved Line Devices Details.
DATE_SUBMITTED | RARF_HUB | LINE_DEVICES |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DEVICE_NAME | RARF_HUB | LINE_DEVICES |  | Connected Device Name.
LINE_CODE | RARF_HUB | LINE_DEVICES |  | Unique Code for each Line equipment defined as the concatenation of SITE_CODE_ERCOT_CODE_FROM_Line Name.
TO_FROM_FLG | RARF_HUB | LINE_DEVICES |  | TO/FROM Flag.
APPROVED_DATE | RARF_HUB | LINE_DEVICES_HIST | History Table: All approved Line Device Details. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved Line Device Details.
DATE_LOADED | RARF_HUB | LINE_DEVICES_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | LINE_DEVICES_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DEVICE_NAME | RARF_HUB | LINE_DEVICES_HIST |  | Connected Device Name.
LINE_CODE | RARF_HUB | LINE_DEVICES_HIST |  | Unique Code for each Line equipment defined as the concatenation of SITE_CODE_ERCOT_CODE_FROM_Line Name.
SUBMISSION_TYPE | RARF_HUB | LINE_DEVICES_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
TO_FROM_FLG | RARF_HUB | LINE_DEVICES_HIST |  | TO/FROM Flag.
APPROVED_DATE | RARF_HUB | LINE_HIST | History Table: All approved Line Data. | Date & time when the RARF is approved. NULL indicates Disapproved RARF |  | History Table: All approved Line Data.
BUS_NUM_TO | RARF_HUB | LINE_HIST |  | TO STATION - Bus Number (PTI Bus Number).
BUSNUMBR_FROM | RARF_HUB | LINE_HIST |  | FROM STATION - Bus Number (PTI Bus Number).
CHANGE_DESCRIPTION | RARF_HUB | LINE_HIST |  | Description of Change, indicates if new Equipment is added; Existing Equipment is deleted or Updated
CHARGING_SUSC | RARF_HUB | LINE_HIST |  | Charging Susceptance in PU (100 MVA Base).
COMMENTS_LINE | RARF_HUB | LINE_HIST |  | General comments on LINE equipment.
CONTINUOUS_RTG | RARF_HUB | LINE_HIST |  | Nominal (Static) - Continuous Rating.
DATE_LOADED | RARF_HUB | LINE_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | LINE_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
EFF_DATE | RARF_HUB | LINE_HIST |  | Date when the Equipment will be effective in Model. Format: (MM/DD/YYYY).
EMGCY_RTG_2HR | RARF_HUB | LINE_HIST |  | Nominal (Static) - 2-hr Emergency Rating.
ERCOT_CODE_FROM | RARF_HUB | LINE_HIST |  | FROM STATION - ERCOT Station Code Mnemonic.
ERCOT_CODE_TO | RARF_HUB | LINE_HIST |  | TO STATION - ERCOT Station Code Mnemonic.
ERCOT_LINE_NAME | RARF_HUB | LINE_HIST |  | ERCOT Line Name.
INTERNAL_LINE_TO_FLG | RARF_HUB | LINE_HIST |  | Internal Line Flag (Y or N).
LINE_CODE | RARF_HUB | LINE_HIST |  | Unique Code for each Line equipment defined as the concatenation of SITE_CODE_ERCOT_CODE_FROM_Line Name.
LINE_RATING | RARF_HUB | LINE_HIST |  | Line Rating (Static or Dynamic).
LINE_VOLT_LVL | RARF_HUB | LINE_HIST |  | Line Voltage Level.
REACTANCE | RARF_HUB | LINE_HIST |  | Reactance in P.U. (100 MVA Base).
RESISTANCE | RARF_HUB | LINE_HIST |  | Resistance in P.U. (100 MVA Base).
RTG_15MIN | RARF_HUB | LINE_HIST |  | Nominal (Static) - 15-min Rating.
SEGMENT_LENGTH | RARF_HUB | LINE_HIST |  | Segment Length.
SITE_CODE | RARF_HUB | LINE_HIST |  | Unique Code for Resource Site ( eg:CBY).
SUBMISSION_TYPE | RARF_HUB | LINE_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
TSPNAME_TO | RARF_HUB | LINE_HIST |  | TO STATION - TSP Name.
TYPE | RARF_HUB | LINE_HIST |  | Line Type (overhead / underground).
WEATHERZONE_FROM | RARF_HUB | LINE_HIST |  | FROM STATION - Weather Zone / Weather Station (used for Dynamic Ratings).
WEATHERZONE_TO | RARF_HUB | LINE_HIST |  | TO STATION - Weather Zone / Weather Station (used for Dynamic Ratings).
PLANNING_RATE_C | RARF_HUB | LINE_HIST |  | Planning Rate C | Added 06/27/2012
ZERO_ SEQ_ CHRG_ SUSECPTANCE_PU | RARF_HUB | LINE_HIST |  | Zero Sequence Charging Susceptance In P.u. (100mva Base) | Added 06/27/2012
ZERO_SEQ_LINE_REACTANCE_PU | RARF_HUB | LINE_HIST |  | Zero Sequence Line Reactance In P.u. (100mva Base) | Added 06/27/2012
ZERO_SEQ_LINE_RESISTANCE_PU | RARF_HUB | LINE_HIST |  | Zero Sequence Line Resistance In P.u. (100mva Base) | Added 06/27/2012
CONTINUOUS_RTG | RARF_HUB | LINE_TEMP | Latest Approved Line Temperature Details. | Nominal (Static) - Continuous Rating. |  | Latest Approved Line Temperature Details.
DATE_LOADED | RARF_HUB | LINE_TEMP |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | LINE_TEMP |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
EMGCY_RTG_2HR | RARF_HUB | LINE_TEMP |  | Nominal (Static) - 2-hr Emergency Rating.
LINE_CODE | RARF_HUB | LINE_TEMP |  | Unique Code for each Line equipment defined as the concatenation of SITE_CODE_ERCOT_CODE_FROM_Line Name.
RTG_15MIN | RARF_HUB | LINE_TEMP |  | Nominal (Static) - 15-min Rating.
TEMP | RARF_HUB | LINE_TEMP |  | Line Temperature value.
CHANGE_DESCRIPTION | RARF_HUB | LINE_TEMP |  | DESCRIPTION OF CHANGE | Added 06/27/2012
PLANNING_RATE_C | RARF_HUB | LINE_TEMP |  | Planning Rate C | Added 06/27/2012
APPROVED_DATE | RARF_HUB | LINE_TEMP_HIST | History Table: ALL Approved and Disapproved Line Temperature Details. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: ALL Approved and Disapproved Line Temperature Details.
CONTINUOUS_RTG | RARF_HUB | LINE_TEMP_HIST |  | Nominal (Static) - Continuous Rating.
DATE_LOADED | RARF_HUB | LINE_TEMP_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | LINE_TEMP_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
EMGCY_RTG_2HR | RARF_HUB | LINE_TEMP_HIST |  | Line Emergency Rating.
LINE_CODE | RARF_HUB | LINE_TEMP_HIST |  | Unique Code for each Line defined as the concatenation of SITE_CODE_STATION_CODE_LINENAME.
RTG_15MIN | RARF_HUB | LINE_TEMP_HIST |  | Line 15-min Rating.
SUBMISSION_TYPE | RARF_HUB | LINE_TEMP_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
TEMP | RARF_HUB | LINE_TEMP_HIST |  | Line Temperature value.
CHANGE_DESCRIPTION | RARF_HUB | LINE_TEMP_HIST |  | DESCRIPTION OF CHANGE | Added 06/27/2012
PLANNING_RATE_C | RARF_HUB | LINE_TEMP_HIST |  | Planning Rate C | Added 06/27/2012
DATE_LOADED | RARF_HUB | LOAD_DEVICES | Transmission equipment: Latest Approved LOAD DEVICES Details. | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format). |  | Transmission equipment: Latest Approved LOAD DEVICES Details.
DATE_SUBMITTED | RARF_HUB | LOAD_DEVICES |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
LOAD_CODE | RARF_HUB | LOAD_DEVICES |  | Unique Code for LOAD defined as SITE_CODE_SUBSTATION_CODE_LOAD_DEVICE_NAME.
LOAD_DEVICE_NAME | RARF_HUB | LOAD_DEVICES |  | Load Device Name.
APPROVED_DATE | RARF_HUB | LOAD_DEVICES_HIST | History Table: All approved and Disapproved LOAD DEVICES Details. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved and Disapproved LOAD DEVICES Details.
DATE_LOADED | RARF_HUB | LOAD_DEVICES_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | LOAD_DEVICES_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
LOAD_CODE | RARF_HUB | LOAD_DEVICES_HIST |  | Unique Code for LOAD defined as SITE_CODE_SUBSTATION_CODE_LOAD_DEVICE_NAME.
LOAD_DEVICE_NAME | RARF_HUB | LOAD_DEVICES_HIST |  | Load Device Name.
SUBMISSION_TYPE | RARF_HUB | LOAD_DEVICES_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
CITY_POD | RARF_HUB | LOAD_RESOURCES | Latest approved Load Resources Unit Details. | Name of City for Point of Delivery (POD). |  | Latest approved Load Resources Unit Details.
CLR_DYNAMIC_SCHED_FLG | RARF_HUB | LOAD_RESOURCES |  | If CLR, will CLR be Dynamically Scheduling? Y or N.
CLR_OPERATE_AS_UFR_FLG | RARF_HUB | LOAD_RESOURCES |  | Can the CLR be operated as a UFR type resource?.
COMMON_NAME_LOAD_RSRC | RARF_HUB | LOAD_RESOURCES |  | Common name of the load that will be acting as a resource.
DATE_LOADED | RARF_HUB | LOAD_RESOURCES |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | LOAD_RESOURCES |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DISPATCH_ASSET_CODE | RARF_HUB | LOAD_RESOURCES |  | Mnemonic (Unique identifier) for each Load Resource.
END_USE_CUSTOMER | RARF_HUB | LOAD_RESOURCES |  | END USE CUSTOMER NAME.
ERCOT_LOAD_ZONE | RARF_HUB | LOAD_RESOURCES |  | ERCOT Congestion Management Zone--West; North; Northeast; South; or Houston.
ESIID_ASSIGNED | RARF_HUB | LOAD_RESOURCES |  | ESI-ID assigned to the load
ESIID_STATION_CODE | RARF_HUB | LOAD_RESOURCES |  | The station code associated with the ESIID that will be utilized
ESIID_STATION_NAME | RARF_HUB | LOAD_RESOURCES |  | The station name associated with the ESIID that will be utilized
HIGH_REAS_LIMIT | RARF_HUB | LOAD_RESOURCES |  | High Reasonability Limit( MW).
HIGH_REAS_RAMPRATE_LIMIT | RARF_HUB | LOAD_RESOURCES |  | CLR High Reasonability Ramp Rate Limit(MW/min).
HIGH_SET_UFR_STG | RARF_HUB | LOAD_RESOURCES |  | High Set Under-frequency Relay (UFR) Setting.
LOAD_BEHIND_NOIE_FLG | RARF_HUB | LOAD_RESOURCES |  | Is Load Behind a NOIE Settlement Meter Point?( Y or N).
LOAD_NET_FROM_GENSITE_FLG | RARF_HUB | LOAD_RESOURCES |  | Is Load Netted From Generation at ERCOT Read Gensite? (Y or N).
LOAD_RES_CTRL_DEVICE | RARF_HUB | LOAD_RESOURCES |  | Load Resource Control Device(Type of interrupting device. (Control Technology / Interruptible Switch / Circuit Breaker).
LOAD_RESOURCE_EFF_DATE | RARF_HUB | LOAD_RESOURCES |  | Effective date the load was placed in service
LOAD_RESOURCE_EXP_DATE | RARF_HUB | LOAD_RESOURCES |  | Expiration Date of the Load Resource.
LOAD_RESOURCE_TYPE | RARF_HUB | LOAD_RESOURCES |  | Load Resource Type.
LOW_REAS_LIMIT | RARF_HUB | LOAD_RESOURCES |  | Low Reasonability Limit.
LOW_REAS_RAMPRATE_LIMIT | RARF_HUB | LOAD_RESOURCES |  | CLR Low Reasonability Ramp Rate Limit(MW/min).
MAX_DAILY_DEPLOYS | RARF_HUB | LOAD_RESOURCES |  | For Non-CLR Resource Parameters: Max Deployment Time: The maximum number of times the Resource can be deployed in a day under normal operating conditions
MAX_DEPLOY_TIME_CLR | RARF_HUB | LOAD_RESOURCES |  | For CLR Resource Parameters: The maximum amount of time a Controllable Load Resource can be deployed before it must return to normal operating conditions
MAX_INTERUPT_TIME | RARF_HUB | LOAD_RESOURCES |  | Minimum Interruption Time(The maximum number of consecutive hours the Resource can remain deployed before it needs to be energized).
MAX_POD_TOTAL_LOAD | RARF_HUB | LOAD_RESOURCES |  | Maximum total load at the point of delivery
MAX_WKLY_DEPLOYS | RARF_HUB | LOAD_RESOURCES |  | For NON-CLR Resources: Max WEEKLY Deployments: The maximum number of times the Resource can be deployed in seven consecutive days under normal operating conditions;.
MAX_WKLY_ENERGY | RARF_HUB | LOAD_RESOURCES |  | For NON-CLR Resources: The maximum amount of energy, in MWh, a for which the Resource can be deployed in seven consecutive days.
MAX_WKLY_ENERGY_CLR | RARF_HUB | LOAD_RESOURCES |  | The maximum amount of energy a Controllable Load Resource can be deployed in seven consecutive days
MIN_INTERUPT_TIME | RARF_HUB | LOAD_RESOURCES |  | Minimum Interruption Time(The minimum number of consecutive hours the Resource can be deployed (between breaker open to breaker close))
MIN_NOTICE_TIME | RARF_HUB | LOAD_RESOURCES |  | Minimum Notice Time(The notice time that the Resource requires before deployment (e.g., instantaneous, 30 minutes, etc.)
MIN_RESTOR_TIME | RARF_HUB | LOAD_RESOURCES |  | Minimum Restoration Time(The minimum number of consecutive hours the Resource must remain energized (not deployed), from the time the Resource is restored from interruption and available for the next potential interruption)
MTR_RDG_ENTITY_DUNS | RARF_HUB | LOAD_RESOURCES |  | Meter Reading Entity Duns Number.
MTR_RDG_ENTITY_TDSP | RARF_HUB | LOAD_RESOURCES |  | Meter Reading Entity (TDSP).
NOTICE_REQ_INTERRUPT | RARF_HUB | LOAD_RESOURCES |  | Notice Requirements to Interrupt.
PRIVATE_USE_NETWRK_FLG | RARF_HUB | LOAD_RESOURCES |  | PTI Bus Number.
QSE_DUNS | RARF_HUB | LOAD_RESOURCES |  | Duns# of the Qualified Scheduling Entity who represents the load
QSE_NAME | RARF_HUB | LOAD_RESOURCES |  | Name of the Qualified Scheduling Entity who represents the load
RE_DUNS | RARF_HUB | LOAD_RESOURCES |  | Resource Entity Duns# who submitted the LAAR RARF.
STREET_ADD_POD | RARF_HUB | LOAD_RESOURCES |  | Physical Street Address for point of Delivery (POD).
SUBSTATION_CODE_POD | RARF_HUB | LOAD_RESOURCES |  | TDSP substation code
SUBSTATION_NAME_POD | RARF_HUB | LOAD_RESOURCES |  | Station name associated with the ESIID that will be utilized
SUMMER_INTERUPT_MW | RARF_HUB | LOAD_RESOURCES |  | Summer interruptible load in MW
TRANSMISSION_BUS_POD | RARF_HUB | LOAD_RESOURCES |  | Transmission bus location by bus number or by specifying the transmission line
VOLTAGE_LVL_TLMTRD_LOAD | RARF_HUB | LOAD_RESOURCES |  | Voltage level of the load.
WHOLESALE_DLVRY_PT | RARF_HUB | LOAD_RESOURCES |  | Wholesale Delivery Point? Y or N.
WINTER_INTERUPT_MW | RARF_HUB | LOAD_RESOURCES |  | Winter interruptible load in MW
TRANS_STAT_LOAD_NAM_NOM | RARF_HUB | LOAD_RESOURCES |  | Transmission Station Load Name in Network Operations Model | Added 06/27/2012
APPROVED_DATE | RARF_HUB | LOAD_RESOURCES_HIST | History Table: All approved and Disapproved Load Resources Unit Details. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved and Disapproved Load Resources Unit Details.
CITY_POD | RARF_HUB | LOAD_RESOURCES_HIST |  | Name of City for Point of Delivery (POD).
CLR_DYNAMIC_SCHED_FLG | RARF_HUB | LOAD_RESOURCES_HIST |  | If CLR, will CLR be Dynamically Scheduling? Y or N.
CLR_OPERATE_AS_UFR_FLG | RARF_HUB | LOAD_RESOURCES_HIST |  | Can the CLR be operated as a UFR type resource?.
COMMON_NAME_LOAD_RSRC | RARF_HUB | LOAD_RESOURCES_HIST |  | Common name of the load that will be acting as a resource.
DATE_LOADED | RARF_HUB | LOAD_RESOURCES_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | LOAD_RESOURCES_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DISPATCH_ASSET_CODE | RARF_HUB | LOAD_RESOURCES_HIST |  | Mnemonic (Unique identifier) for each Load Resource.
END_USE_CUSTOMER | RARF_HUB | LOAD_RESOURCES_HIST |  | END USE CUSTOMER NAME.
ERCOT_LOAD_ZONE | RARF_HUB | LOAD_RESOURCES_HIST |  | ERCOT Congestion Management Zone--West; North; Northeast; South; or Houston.
ESIID_ASSIGNED | RARF_HUB | LOAD_RESOURCES_HIST |  | ESI-ID assigned to the load
ESIID_STATION_CODE | RARF_HUB | LOAD_RESOURCES_HIST |  | The station code associated with the ESIID that will be utilized
ESIID_STATION_NAME | RARF_HUB | LOAD_RESOURCES_HIST |  | The station name associated with the ESIID that will be utilized
HIGH_REAS_LIMIT | RARF_HUB | LOAD_RESOURCES_HIST |  | High Reasonability Limit( MW).
HIGH_REAS_RAMPRATE_LIMIT | RARF_HUB | LOAD_RESOURCES_HIST |  | CLR High Reasonability Ramp Rate Limit(MW/min).
HIGH_SET_UFR_STG | RARF_HUB | LOAD_RESOURCES_HIST |  | High Set Under-frequency Relay (UFR) Setting.
LOAD_BEHIND_NOIE_FLG | RARF_HUB | LOAD_RESOURCES_HIST |  | Is Load Behind a NOIE Settlement Meter Point?( Y or N).
LOAD_NET_FROM_GENSITE_FLG | RARF_HUB | LOAD_RESOURCES_HIST |  | Is Load Netted From Generation at ERCOT Read Gensite? (Y or N).
LOAD_RES_CTRL_DEVICE | RARF_HUB | LOAD_RESOURCES_HIST |  | Load Resource Control Device(Type of interrupting device. (Control Technology / Interruptible Switch / Circuit Breaker).
LOAD_RESOURCE_EFF_DATE | RARF_HUB | LOAD_RESOURCES_HIST |  | Effective date the load was placed in service
LOAD_RESOURCE_EXP_DATE | RARF_HUB | LOAD_RESOURCES_HIST |  | Expiration Date of the Load Resource.
LOAD_RESOURCE_TYPE | RARF_HUB | LOAD_RESOURCES_HIST |  | Load Resource Type.
LOW_REAS_LIMIT | RARF_HUB | LOAD_RESOURCES_HIST |  | Low Reasonability Limit.
LOW_REAS_RAMPRATE_LIMIT | RARF_HUB | LOAD_RESOURCES_HIST |  | CLR Low Reasonability Ramp Rate Limit(MW/min).
MAX_DAILY_DEPLOYS | RARF_HUB | LOAD_RESOURCES_HIST |  | For Non-CLR Resource Parameters: Max Deployment Time: The maximum number of times the Resource can be deployed in a day under normal operating conditions
MAX_DEPLOY_TIME_CLR | RARF_HUB | LOAD_RESOURCES_HIST |  | For CLR Resource Parameters: The maximum amount of time a Controllable Load Resource can be deployed before it must return to normal operating conditions
MAX_INTERUPT_TIME | RARF_HUB | LOAD_RESOURCES_HIST |  | Minimum Interruption Time(The maximum number of consecutive hours the Resource can remain deployed before it needs to be energized).
MAX_POD_TOTAL_LOAD | RARF_HUB | LOAD_RESOURCES_HIST |  | Maximum total load at the point of delivery
MAX_WKLY_DEPLOYS | RARF_HUB | LOAD_RESOURCES_HIST |  | For NON-CLR Resources: Max WEEKLY Deployments: The maximum number of times the Resource can be deployed in seven consecutive days under normal operating conditions;.
MAX_WKLY_ENERGY | RARF_HUB | LOAD_RESOURCES_HIST |  | For NON-CLR Resources: The maximum amount of energy, in MWh, a for which the Resource can be deployed in seven consecutive days.
MAX_WKLY_ENERGY_CLR | RARF_HUB | LOAD_RESOURCES_HIST |  | The maximum amount of energy a Controllable Load Resource can be deployed in seven consecutive days
MIN_INTERUPT_TIME | RARF_HUB | LOAD_RESOURCES_HIST |  | Minimum Interruption Time(The minimum number of consecutive hours the Resource can be deployed (between breaker open to breaker close))
MIN_NOTICE_TIME | RARF_HUB | LOAD_RESOURCES_HIST |  | Minimum Notice Time(The notice time that the Resource requires before deployment (e.g., instantaneous, 30 minutes, etc.)
MIN_RESTOR_TIME | RARF_HUB | LOAD_RESOURCES_HIST |  | Minimum Restoration Time(The minimum number of consecutive hours the Resource must remain energized (not deployed), from the time the Resource is restored from interruption and available for the next potential interruption)
MTR_RDG_ENTITY_DUNS | RARF_HUB | LOAD_RESOURCES_HIST |  | Meter Reading Entity Duns Number.
MTR_RDG_ENTITY_TDSP | RARF_HUB | LOAD_RESOURCES_HIST |  | Meter Reading Entity (TDSP).
NOTICE_REQ_INTERRUPT | RARF_HUB | LOAD_RESOURCES_HIST |  | Notice Requirements to Interrupt.
PRIVATE_USE_NETWRK_FLG | RARF_HUB | LOAD_RESOURCES_HIST |  | PTI Bus Number.
QSE_DUNS | RARF_HUB | LOAD_RESOURCES_HIST |  | Duns# of the Qualified Scheduling Entity who represents the load
QSE_NAME | RARF_HUB | LOAD_RESOURCES_HIST |  | Name of the Qualified Scheduling Entity who represents the load
RE_DUNS | RARF_HUB | LOAD_RESOURCES_HIST |  | Resource Entity Duns# who submitted the LAAR RARF.
STREET_ADD_POD | RARF_HUB | LOAD_RESOURCES_HIST |  | Physical Street Address for point of Delivery (POD).
SUBMISSION_TYPE | RARF_HUB | LOAD_RESOURCES_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
SUBSTATION_CODE_POD | RARF_HUB | LOAD_RESOURCES_HIST |  | TDSP substation code
SUBSTATION_NAME_POD | RARF_HUB | LOAD_RESOURCES_HIST |  | Station name associated with the ESIID that will be utilized
SUMMER_INTERUPT_MW | RARF_HUB | LOAD_RESOURCES_HIST |  | Summer interruptible load in MW
TRANSMISSION_BUS_POD | RARF_HUB | LOAD_RESOURCES_HIST |  | Transmission bus location by bus number or by specifying the transmission line
VOLTAGE_LVL_TLMTRD_LOAD | RARF_HUB | LOAD_RESOURCES_HIST |  | Voltage level of the load.
WHOLESALE_DLVRY_PT | RARF_HUB | LOAD_RESOURCES_HIST |  | Wholesale Delivery Point? Y or N.
WINTER_INTERUPT_MW | RARF_HUB | LOAD_RESOURCES_HIST |  | Winter interruptible load in MW
TRANS_STAT_LOAD_NAM_NOM | RARF_HUB | LOAD_RESOURCES_HIST |  | Transmission Station Load Name in Network Operations Model | Added 06/27/2012
AVG_LOAD | RARF_HUB | LOADS | Transmission equipment: Latest Approved LOAD Data. | Average MW Load Under Normal Operations. |  | Transmission equipment: Latest Approved LOAD Data.
AVG_MVAR | RARF_HUB | LOADS |  | Average MVAR Under Normal Operations.
CHANGE_DESCRIPTION | RARF_HUB | LOADS |  | Description of Change, indicates if new Equipment is added; Existing Equipment is deleted or Updated
DATE_LOADED | RARF_HUB | LOADS |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | LOADS |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
EFF_DATE | RARF_HUB | LOADS |  | Date when the Equipment will be effective in Model
LOAD_CODE | RARF_HUB | LOADS |  | Unique Code for each LOAD DEVICE defined as the concatenation of SITE_CODE_SUBSTATION_CODE_LOADNAME.
LOAD_COMMENTS | RARF_HUB | LOADS |  | General comments on LOAD equipment.
LOAD_NAME | RARF_HUB | LOADS |  | Load Name (as it appears in the ERCOT model).
PTI_BUS_NUM | RARF_HUB | LOADS |  | PTI Bus Number.
SITE_CODE | RARF_HUB | LOADS |  | Unique Code for Resource Site (eg:CBY).
SUBSTATION_CODE | RARF_HUB | LOADS |  | Substation Code.
VOLATGE | RARF_HUB | LOADS |  | Load Voltage Level.
APPROVED_DATE | RARF_HUB | LOADS_HIST | History Table:Transmission equipment: All Approved & Disapproved LOAD Data. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table:Transmission equipment: All Approved & Disapproved LOAD Data.
AVG_LOAD | RARF_HUB | LOADS_HIST |  | Average MW Load Under Normal Operations.
AVG_MVAR | RARF_HUB | LOADS_HIST |  | Average MVAR Under Normal Operations.
CHANGE_DESCRIPTION | RARF_HUB | LOADS_HIST |  | Description of Change, indicates if new Equipment is added; Existing Equipment is deleted or Updated
DATE_LOADED | RARF_HUB | LOADS_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | LOADS_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
EFF_DATE | RARF_HUB | LOADS_HIST |  | Date when the Equipment will be effective in Model
LOAD_CODE | RARF_HUB | LOADS_HIST |  | Unique Code for each LOAD DEVICE defined as the concatenation of SITE_CODE_SUBSTATION_CODE_LOADNAME.
LOAD_COMMENTS | RARF_HUB | LOADS_HIST |  | General comments on LOAD equipment.
LOAD_NAME | RARF_HUB | LOADS_HIST |  | Load Name (as it appears in the ERCOT model).
PTI_BUS_NUM | RARF_HUB | LOADS_HIST |  | PTI Bus Number.
SITE_CODE | RARF_HUB | LOADS_HIST |  | Unique Code for Resource Site (eg:CBY).
SUBMISSION_TYPE | RARF_HUB | LOADS_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
SUBSTATION_CODE | RARF_HUB | LOADS_HIST |  | Substation Code.
VOLATGE | RARF_HUB | LOADS_HIST |  | Load Voltage Level.
AMT_SELFSRV_COGEN | RARF_HUB | NON_MODELED |  | Amount of Self Serve for Cogen | Added 06/27/2012 | Latest approved Non Modeled Unit Details.
GEN_FUEL_CAT | RARF_HUB | NON_MODELED |  | Generic Fuel Category | Added 06/27/2012
GEN_STUP_OPER_CAT | RARF_HUB | NON_MODELED |  | Generic Start-up / Operating Category | Added 06/27/2012
NAME_PLT_RTG_MVA | RARF_HUB | NON_MODELED |  | Name Plate Rating | Added 06/27/2012
NAME_PLT_RTG_MW | RARF_HUB | NON_MODELED |  | Name Plate Rating | Added 06/27/2012
NUM_WIND_TURBINES | RARF_HUB | NON_MODELED |  | If Wind, Number of Turbines | Added 06/27/2012
PHYS_UNIT_TYPE | RARF_HUB | NON_MODELED |  | Physical Unit Type | Added 06/27/2012
PRIM_FUELTYPE | RARF_HUB | NON_MODELED |  | Primary Fuel Type | Added 06/27/2012
PRIVATE_NET_GROSS_UNT_MVAR | RARF_HUB | NON_MODELED |  | Private Network Gross Unit MVAR | Added 06/27/2012
PRIVATE_NET_GROSS_UNT_MW | RARF_HUB | NON_MODELED |  | Private Network Gross Unit MW | Added 06/27/2012
PRIVATE_NWK_NET_INTERCHANGE | RARF_HUB | NON_MODELED |  | Private Network Net Interchange | Added 06/27/2012
PUN_FLG | RARF_HUB | NON_MODELED |  | Private Network / Cogen | Added 06/27/2012
RE_DUNS | RARF_HUB | NON_MODELED |  | Resource Entity Duns Number | Added 06/27/2012
RE_NAME | RARF_HUB | NON_MODELED |  | Resource Entity Name | Added 06/27/2012
RENEWABLE_FLG | RARF_HUB | NON_MODELED |  | Renewable | Added 06/27/2012
RENEWABLE_OFFSET | RARF_HUB | NON_MODELED |  | Renewable/Offset | Added 06/27/2012
SEC_FUELTYPE | RARF_HUB | NON_MODELED |  | Secondary Fuel Type | Added 06/27/2012
TECHNOLOGY_TYPE | RARF_HUB | NON_MODELED |  | Technology Type | Added 06/27/2012
UNIT_CODE | RARF_HUB | NON_MODELED |  | Unit Code | Added 06/27/2012
UNIT_END_DT | RARF_HUB | NON_MODELED |  | Unit End Date | Added 06/27/2012
UNIT_MRD_ST_DT | RARF_HUB | NON_MODELED |  | Unit Start Date | Added 06/27/2012
UNIT_NAME | RARF_HUB | NON_MODELED |  | Unit Name | Added 06/27/2012
AMT_SELFSRV_COGEN | RARF_HUB | NON_MODELED_HIST |  | Amount of Self Serve for Cogen | Added 06/27/2012 | History Table:Transmission equipment: All Approved & Disapproved Non Modeled Unit Details.
GEN_FUEL_CAT | RARF_HUB | NON_MODELED_HIST |  | Generic Fuel Category | Added 06/27/2012
GEN_STUP_OPER_CAT | RARF_HUB | NON_MODELED_HIST |  | Generic Start-up / Operating Category | Added 06/27/2012
NAME_PLT_RTG_MVA | RARF_HUB | NON_MODELED_HIST |  | Name Plate Rating | Added 06/27/2012
NAME_PLT_RTG_MW | RARF_HUB | NON_MODELED_HIST |  | Name Plate Rating | Added 06/27/2012
NUM_WIND_TURBINES | RARF_HUB | NON_MODELED_HIST |  | If Wind, Number of Turbines | Added 06/27/2012
PHYS_UNIT_TYPE | RARF_HUB | NON_MODELED_HIST |  | Physical Unit Type | Added 06/27/2012
PRIM_FUELTYPE | RARF_HUB | NON_MODELED_HIST |  | Primary Fuel Type | Added 06/27/2012
PRIVATE_NET_GROSS_UNT_MVAR | RARF_HUB | NON_MODELED_HIST |  | Private Network Gross Unit MVAR | Added 06/27/2012
PRIVATE_NET_GROSS_UNT_MW | RARF_HUB | NON_MODELED_HIST |  | Private Network Gross Unit MW | Added 06/27/2012
PRIVATE_NWK_NET_INTERCHANGE | RARF_HUB | NON_MODELED_HIST |  | Private Network Net Interchange | Added 06/27/2012
PUN_FLG | RARF_HUB | NON_MODELED_HIST |  | Private Network / Cogen | Added 06/27/2012
RE_DUNS | RARF_HUB | NON_MODELED_HIST |  | Resource Entity Duns Number | Added 06/27/2012
RE_NAME | RARF_HUB | NON_MODELED_HIST |  | Resource Entity Name | Added 06/27/2012
RENEWABLE_FLG | RARF_HUB | NON_MODELED_HIST |  | Renewable | Added 06/27/2012
RENEWABLE_OFFSET | RARF_HUB | NON_MODELED_HIST |  | Renewable/Offset | Added 06/27/2012
SEC_FUELTYPE | RARF_HUB | NON_MODELED_HIST |  | Secondary Fuel Type | Added 06/27/2012
TECHNOLOGY_TYPE | RARF_HUB | NON_MODELED_HIST |  | Technology Type | Added 06/27/2012
UNIT_CODE | RARF_HUB | NON_MODELED_HIST |  | Unit Code | Added 06/27/2012
UNIT_END_DT | RARF_HUB | NON_MODELED_HIST |  | Unit End Date | Added 06/27/2012
UNIT_MRD_ST_DT | RARF_HUB | NON_MODELED_HIST |  | Unit Start Date | Added 06/27/2012
UNIT_NAME | RARF_HUB | NON_MODELED_HIST |  | Unit Name | Added 06/27/2012
DATE_LOADED | RARF_HUB | OWNERSHIP | Latest Resource Owner Details for ALL Generation Units. | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format). |  | Latest Resource Owner Details for ALL Generation Units.
DATE_SUBMITTED | RARF_HUB | OWNERSHIP |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
FIX_OWNRSHP_PCT | RARF_HUB | OWNERSHIP |  | Fixed Ownership Percentage.
J0CODE | RARF_HUB | OWNERSHIP |  | This column is not used currently.
MASTR_OWNR_FLG | RARF_HUB | OWNERSHIP |  | MASTER OWNER Flag( Y or N).
MKT_PRTCPT | RARF_HUB | OWNERSHIP |  | Resource Entity who owns the Unit.
MKT_PRTCPT_DUNS | RARF_HUB | OWNERSHIP |  | Resource Entity Duns# who owns the Unit.
TYPE | RARF_HUB | OWNERSHIP |  | This column is not used currently.
UNIT_CODE | RARF_HUB | OWNERSHIP |  | Concatenated mnemonic of Resource Site Code and Unit name (e.g CBY_CBYG1) where CBY is Site_code and CBYG1 is Unit Name.
J0CODE | RARF_HUB | OWNERSHIP |  | Joint Ownership? | Added 06/27/2012
OWNR_END_DT | RARF_HUB | OWNERSHIP |  | Ownership Stop Date | Added 06/27/2012
OWNR_START_DT | RARF_HUB | OWNERSHIP |  | Ownership Start Date | Added 06/27/2012
APPROVED_DATE | RARF_HUB | OWNERSHIP_HIST | History Table: All approved and Disapproved Resource Owner Details for a Generation Unit. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved and Disapproved Resource Owner Details for a Generation Unit.
DATE_LOADED | RARF_HUB | OWNERSHIP_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | OWNERSHIP_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
FIX_OWNRSHP_PCT | RARF_HUB | OWNERSHIP_HIST |  | Fixed Ownership Percentage.
J0CODE | RARF_HUB | OWNERSHIP_HIST |  | This column is not used currently.
MASTR_OWNR_FLG | RARF_HUB | OWNERSHIP_HIST |  | MASTER OWNER Flag( Y or N).
MKT_PRTCPT | RARF_HUB | OWNERSHIP_HIST |  | Resource Entity who owns the Unit.
MKT_PRTCPT_DUNS | RARF_HUB | OWNERSHIP_HIST |  | Resource Entity Duns# who owns the Unit.
SUBMISSION_TYPE | RARF_HUB | OWNERSHIP_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
TYPE | RARF_HUB | OWNERSHIP_HIST |  | This column is not used currently.
UNIT_CODE | RARF_HUB | OWNERSHIP_HIST |  | Concatenated mnemonic of Resource Site Code and Unit name (e.g CBY_CBYG1) where CBY is Site_code and CBYG1 is Unit Name.
J0CODE | RARF_HUB | OWNERSHIP_HIST |  | Joint Ownership? | Added 06/27/2012
OWNR_END_DT | RARF_HUB | OWNERSHIP_HIST |  | Ownership Stop Date | Added 06/27/2012
OWNR_START_DT | RARF_HUB | OWNERSHIP_HIST |  | Ownership Start Date | Added 06/27/2012
DAY | RARF_HUB | PUN_LOAD |  | Day of Week | Added 06/27/2012 | Latest approved PUN LOAD Details.
HOUR_ENDING | RARF_HUB | PUN_LOAD |  | Hour Ending | Added 06/27/2012
MW | RARF_HUB | PUN_LOAD |  | MW | Added 06/27/2012
PUN_LOAD_CODE | RARF_HUB | PUN_LOAD |  | Load Code | Added 06/27/2012
PUN_LOAD_NAME | RARF_HUB | PUN_LOAD |  | Load Name | Added 06/27/2012
SUBSTATION_CODE | RARF_HUB | PUN_LOAD |  | Station Code | Added 06/27/2012
DAY | RARF_HUB | PUN_LOAD_HIST |  | Day of Week | Added 06/27/2012 | History Table:Transmission equipment: All Approved & Disapproved PUN LOAD Details.
HOUR_ENDING | RARF_HUB | PUN_LOAD_HIST |  | Hour Ending | Added 06/27/2012
MW | RARF_HUB | PUN_LOAD_HIST |  | MW | Added 06/27/2012
PUN_LOAD_CODE | RARF_HUB | PUN_LOAD_HIST |  | Load Code | Added 06/27/2012
PUN_LOAD_NAME | RARF_HUB | PUN_LOAD_HIST |  | Load Name | Added 06/27/2012
SUBSTATION_CODE | RARF_HUB | PUN_LOAD_HIST |  | Station Code | Added 06/27/2012
DATE_LOADED | RARF_HUB | RAMP_RATES_ERRC | Latest Approved Emergency Ramp rate values for a generating Unit. | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format). |  | Latest Approved Emergency Ramp rate values for a generating Unit.
DATE_SUBMITTED | RARF_HUB | RAMP_RATES_ERRC |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DOWNWARD_RAMPRATE_ERRC | RARF_HUB | RAMP_RATES_ERRC |  | Emergency Downward Ramp Rate.
MW_NUMBER_ERRC | RARF_HUB | RAMP_RATES_ERRC |  | MW1 to MWX ( X can be up to 12 points).
MW_RATING_ERRC | RARF_HUB | RAMP_RATES_ERRC |  | MW Rating.
UNIT_CODE | RARF_HUB | RAMP_RATES_ERRC |  | Concatenated mnemonic of Resource Site Code and Unit name (e.g CBY_CBYG1) where CBY is Site_code and CBYG1 is Unit Name.
UNIT_MW_ERRC | RARF_HUB | RAMP_RATES_ERRC |  | MW Output.
UPWARD_RAMPRATE_ERRC | RARF_HUB | RAMP_RATES_ERRC |  | Emergency Upward Ramp Rate.
APPROVED_DATE | RARF_HUB | RAMP_RATES_ERRC_HIST | History Table: All approved and Disapproved Emergency Ramp rate values for a generating Unit. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved and Disapproved Emergency Ramp rate values for a generating Unit.
DATE_LOADED | RARF_HUB | RAMP_RATES_ERRC_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | RAMP_RATES_ERRC_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DOWNWARD_RAMPRATE_ERRC | RARF_HUB | RAMP_RATES_ERRC_HIST |  | Emergency Downward Ramp Rate.
MW_NUMBER_ERRC | RARF_HUB | RAMP_RATES_ERRC_HIST |  | MW1 to MWX ( X can be up to 12 points).
MW_RATING_ERRC | RARF_HUB | RAMP_RATES_ERRC_HIST |  | MW Rating.
SUBMISSION_TYPE | RARF_HUB | RAMP_RATES_ERRC_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
UNIT_CODE | RARF_HUB | RAMP_RATES_ERRC_HIST |  | Concatenated mnemonic of Resource Site Code and Unit name (e.g CBY_CBYG1) where CBY is Site_code and CBYG1 is Unit Name.
UNIT_MW_ERRC | RARF_HUB | RAMP_RATES_ERRC_HIST |  | MW Output.
UPWARD_RAMPRATE_ERRC | RARF_HUB | RAMP_RATES_ERRC_HIST |  | Emergency Upward Ramp Rate.
DATE_LOADED | RARF_HUB | RAMP_RATES_NRRC | Latest Approved Normal Ramp rate values for a generating Unit. | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format). |  | Latest Approved Normal Ramp rate values for a generating Unit.
DATE_SUBMITTED | RARF_HUB | RAMP_RATES_NRRC |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DOWNWARD_RAMPRATE_NRRC | RARF_HUB | RAMP_RATES_NRRC |  | Normal Downward Ramp Rate.
MW_NUMBER_NRRC | RARF_HUB | RAMP_RATES_NRRC |  | MW1 to MWX ( X can be up to 12 points).
MW_RATING_NRRC | RARF_HUB | RAMP_RATES_NRRC |  | MW Rating.
UNIT_CODE | RARF_HUB | RAMP_RATES_NRRC |  | Concatenated mnemonic of Resource Site Code and Unit name (e.g CBY_CBYG1) where CBY is Site_code and CBYG1 is Unit Name.
UNIT_MW_NRRC | RARF_HUB | RAMP_RATES_NRRC |  | MW Output.
UPWARD_RAMPRATE_NRRC | RARF_HUB | RAMP_RATES_NRRC |  | Normal Upward Ramp Rate.
APPROVED_DATE | RARF_HUB | RAMP_RATES_NRRC_HIST | History Table: All approved and Disapproved Normal Ramp rate values for a generating Unit. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved and Disapproved Normal Ramp rate values for a generating Unit.
DATE_LOADED | RARF_HUB | RAMP_RATES_NRRC_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | RAMP_RATES_NRRC_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DOWNWARD_RAMPRATE_NRRC | RARF_HUB | RAMP_RATES_NRRC_HIST |  | Normal Downward Ramp Rate.
MW_NUMBER_NRRC | RARF_HUB | RAMP_RATES_NRRC_HIST |  | MW1 to MWX ( X can be up to 12 points).
MW_RATING_NRRC | RARF_HUB | RAMP_RATES_NRRC_HIST |  | MW Rating.
SUBMISSION_TYPE | RARF_HUB | RAMP_RATES_NRRC_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
UNIT_CODE | RARF_HUB | RAMP_RATES_NRRC_HIST |  | Concatenated mnemonic of Resource Site Code and Unit name (e.g CBY_CBYG1) where CBY is Site_code and CBYG1 is Unit Name.
UNIT_MW_NRRC | RARF_HUB | RAMP_RATES_NRRC_HIST |  | MW Output.
UPWARD_RAMPRATE_NRRC | RARF_HUB | RAMP_RATES_NRRC_HIST |  | Normal Upward Ramp Rate.
DATE_LOADED | RARF_HUB | RE_RARF | Latest Approved Contact Details of the Authorized Representative for the RARF | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format). |  | Latest Approved Contact Details of the Authorized Representative for the RARF
EMAIL_AR | RARF_HUB | RE_RARF |  | E-mail address of the Authorized Representative
FAX_AR | RARF_HUB | RE_RARF |  | Fax# of the Authorized Representative
NAME_AR | RARF_HUB | RE_RARF |  | Authorized Representative Name
NOTES_RE_RARF | RARF_HUB | RE_RARF |  | General Notes about the RARF Submitted
PHONE_AR | RARF_HUB | RE_RARF |  | Title of the Authorized Representative
RE_DUNS | RARF_HUB | RE_RARF |  | Resource Entity Duns# Submitting the RARF
RE_NAME | RARF_HUB | RE_RARF |  | Resource Entity Name# Submitting the RARF
SIGN | RARF_HUB | RE_RARF |  | Signature of the Resource Entity Name# Submitting the RARF
TITLE_AR | RARF_HUB | RE_RARF |  | Title of the Authorized Representative
APPROVED_DATE | RARF_HUB | RE_RARF_HIST | History Table: All approved and Disapproved Contact Details of the Authorized Representative for the RARF | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved and Disapproved Contact Details of the Authorized Representative for the RARF
DATE_LOADED | RARF_HUB | RE_RARF_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
EMAIL_AR | RARF_HUB | RE_RARF_HIST |  | E-mail address of the Authorized Representative
FAX_AR | RARF_HUB | RE_RARF_HIST |  | Fax# of the Authorized Representative
NAME_AR | RARF_HUB | RE_RARF_HIST |  | Authorized Representative Name
NOTES_RE_RARF | RARF_HUB | RE_RARF_HIST |  | General Notes about the RARF Submitted
PHONE_AR | RARF_HUB | RE_RARF_HIST |  | Title of the Authorized Representative
RE_DUNS | RARF_HUB | RE_RARF_HIST |  | Resource Entity Duns# Submitting the RARF
RE_NAME | RARF_HUB | RE_RARF_HIST |  | Resource Entity Name# Submitting the RARF
SIGN | RARF_HUB | RE_RARF_HIST |  | Signature of the Resource Entity Name# Submitting the RARF
SUBMISSION_TYPE | RARF_HUB | RE_RARF_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
TITLE_AR | RARF_HUB | RE_RARF_HIST |  | Title of the Authorized Representative
DATE_LOADED | RARF_HUB | REACT_CAP_WIND | Latest Approved Reactive Capability Data for Wind Generation Units. | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format). |  | Latest Approved Reactive Capability Data for Wind Generation Units.
DATE_SUBMITTED | RARF_HUB | REACT_CAP_WIND |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
GROUP_CODE | RARF_HUB | REACT_CAP_WIND |  | Turbine Group Code.
MFR_CAP_CURVE | RARF_HUB | REACT_CAP_WIND |  | Manufacturer's Capability Curve submitted ( Y or N)?.
MVAR1LAG | RARF_HUB | REACT_CAP_WIND |  | Lagging MVAR limit associated with MW1 output.
MVAR1LEAD | RARF_HUB | REACT_CAP_WIND |  | Leading MVAR limit associated with MW1 output.
MVAR2LAG | RARF_HUB | REACT_CAP_WIND |  | Lagging MVAR limit associated with MW2 output.
MVAR2LEAD | RARF_HUB | REACT_CAP_WIND |  | Leading MVAR limit associated with MW2 output.
MVAR3LAG | RARF_HUB | REACT_CAP_WIND |  | Lagging MVAR limit associated with MW3 output.
MVAR3LEAD | RARF_HUB | REACT_CAP_WIND |  | Leading MVAR limit associated with MW3 output.
MVAR4LAG | RARF_HUB | REACT_CAP_WIND |  | Lagging MVAR limit associated with MW4 output.
MVAR4LEAD | RARF_HUB | REACT_CAP_WIND |  | Leading MVAR limit associated with MW4 output.
MW1 | RARF_HUB | REACT_CAP_WIND |  | MW1.
MW2 | RARF_HUB | REACT_CAP_WIND |  | MW2.
MW3 | RARF_HUB | REACT_CAP_WIND |  | MW3.
MW4 | RARF_HUB | REACT_CAP_WIND |  | MW4.
MW5UNITYPF | RARF_HUB | REACT_CAP_WIND |  | MW5 - Unity Power Factor- This column is not used anymore, removed from RARF.
NETMAXLAG | RARF_HUB | REACT_CAP_WIND |  | Net Maximum Lagging Operating Capability.
NETMAXLEAD | RARF_HUB | REACT_CAP_WIND |  | Net Maximum Leading Operating Capability.
REACTIVE_STD | RARF_HUB | REACT_CAP_WIND |  | Reactive Standard (Y or N)?.
UNIT_CODE | RARF_HUB | REACT_CAP_WIND |  | Concatenated mnemonic of Resource Site Code and Unit name (e.g CBY_CBYG1) where CBY is Site_code and CBYG1 is Unit Name.
REACT_CAPB_DATA_GROSS_VAL | RARF_HUB | REACT_CAP_WIND |  | Reactive Capability Data Provided Below Is Gross Values? | Added 06/27/2012
REACT_CAPB_NDCRC_TEST_DATA | RARF_HUB | REACT_CAP_WIND |  | Reactive Capability Data Provided is from NDCRC Test Data? | Added 06/27/2012
REACT_CAPB_NDCRC_TEST_DATA_DT | RARF_HUB | REACT_CAP_WIND |  | If Reactive Capability Data Provided Is From NDCRC test Data Then Enter The Date On Which The Test Was Performed. | Added 06/27/2012
APPROVED_DATE | RARF_HUB | REACT_CAP_WIND_HIST | History Table: All approved and Disapproved Reactive Capability Data for Wind Generation Units. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved and Disapproved Reactive Capability Data for Wind Generation Units.
DATE_LOADED | RARF_HUB | REACT_CAP_WIND_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | REACT_CAP_WIND_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
GROUP_CODE | RARF_HUB | REACT_CAP_WIND_HIST |  | Turbine Group Code.
MFR_CAP_CURVE | RARF_HUB | REACT_CAP_WIND_HIST |  | Manufacturer's Capability Curve submitted ( Y or N)?.
MVAR1LAG | RARF_HUB | REACT_CAP_WIND_HIST |  | Lagging MVAR limit associated with MW1 output.
MVAR1LEAD | RARF_HUB | REACT_CAP_WIND_HIST |  | Leading MVAR limit associated with MW1 output.
MVAR2LAG | RARF_HUB | REACT_CAP_WIND_HIST |  | Lagging MVAR limit associated with MW2 output.
MVAR2LEAD | RARF_HUB | REACT_CAP_WIND_HIST |  | Leading MVAR limit associated with MW2 output.
MVAR3LAG | RARF_HUB | REACT_CAP_WIND_HIST |  | Lagging MVAR limit associated with MW3 output.
MVAR3LEAD | RARF_HUB | REACT_CAP_WIND_HIST |  | Leading MVAR limit associated with MW3 output.
MVAR4LAG | RARF_HUB | REACT_CAP_WIND_HIST |  | Lagging MVAR limit associated with MW4 output.
MVAR4LEAD | RARF_HUB | REACT_CAP_WIND_HIST |  | Leading MVAR limit associated with MW4 output.
MW1 | RARF_HUB | REACT_CAP_WIND_HIST |  | MW1.
MW2 | RARF_HUB | REACT_CAP_WIND_HIST |  | MW2.
MW3 | RARF_HUB | REACT_CAP_WIND_HIST |  | MW3.
MW4 | RARF_HUB | REACT_CAP_WIND_HIST |  | MW4.
MW5UNITYPF | RARF_HUB | REACT_CAP_WIND_HIST |  | MW5 - Unity Power Factor- This column is not used anymore, removed from RARF.
NETMAXLAG | RARF_HUB | REACT_CAP_WIND_HIST |  | Net Maximum Lagging Operating Capability.
NETMAXLEAD | RARF_HUB | REACT_CAP_WIND_HIST |  | Net Maximum Leading Operating Capability.
REACTIVE_STD | RARF_HUB | REACT_CAP_WIND_HIST |  | Reactive Standard (Y or N)?.
SUBMISSION_TYPE | RARF_HUB | REACT_CAP_WIND_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
UNIT_CODE | RARF_HUB | REACT_CAP_WIND_HIST |  | Concatenated mnemonic of Resource Site Code and Unit name (e.g CBY_CBYG1) where CBY is Site_code and CBYG1 is Unit Name.
REACT_CAPB_DATA_GROSS_VAL | RARF_HUB | REACT_CAP_WIND_HIST |  | Reactive Capability Data Provided Below Is Gross Values? | Added 06/27/2012
REACT_CAPB_NDCRC_TEST_DATA | RARF_HUB | REACT_CAP_WIND_HIST |  | Reactive Capability Data Provided is from NDCRC Test Data? | Added 06/27/2012
REACT_CAPB_NDCRC_TEST_DATA_DT | RARF_HUB | REACT_CAP_WIND_HIST |  | If Reactive Capability Data Provided Is From NDCRC test Data Then Enter The Date On Which The Test Was Performed. | Added 06/27/2012
CHANGE_DESCRIPTION | RARF_HUB | SERIES_DEVICE_DATA | Latest Approved Series Device equipment details. | Description of Change, indicates if new Equipment is added; Existing Equipment is deleted or Updated |  | Latest Approved Series Device equipment details.
CONTINUOUS_RTG | RARF_HUB | SERIES_DEVICE_DATA |  | Continuous Rating.
DATE_LOADED | RARF_HUB | SERIES_DEVICE_DATA |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | SERIES_DEVICE_DATA |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
EFF_DATE | RARF_HUB | SERIES_DEVICE_DATA |  | Date when the Equipment will become effective in Model
EMGCY_RTG_2HR | RARF_HUB | SERIES_DEVICE_DATA |  | 2-hr Emergency Rating.
REACTANCE | RARF_HUB | SERIES_DEVICE_DATA |  | Reactance.
RESISTANCE | RARF_HUB | SERIES_DEVICE_DATA |  | Resistance.
RTG_15MIN | RARF_HUB | SERIES_DEVICE_DATA |  | 15-min Rating.
SD_CODE | RARF_HUB | SERIES_DEVICE_DATA |  | Unique Code for each Series Device equipment that is defined as the concatenation of SITE_CODE_SUBSTATION_CODE_SD_NAME.
SD_COMMENTS | RARF_HUB | SERIES_DEVICE_DATA |  | General comments on Series Device equipment.
SD_NAME | RARF_HUB | SERIES_DEVICE_DATA |  | Series Device Name.
SIDE1_PTI_BUS_NUM | RARF_HUB | SERIES_DEVICE_DATA |  | Side 1 - Bus Number (PTI Bus Number).
SIDE2_PTI_BUS_NUM | RARF_HUB | SERIES_DEVICE_DATA |  | Side 2 - Bus Number (PTI Bus Number).
SITE_CODE | RARF_HUB | SERIES_DEVICE_DATA |  | Unique Code for Resource Site -- Determined jointly with ERCOT.
SUBSTATION_CODE | RARF_HUB | SERIES_DEVICE_DATA |  | ERCOT Station Name (Station Code or Station Mnemonic).
VOLATGE | RARF_HUB | SERIES_DEVICE_DATA |  | Voltage Level.
APPROVED_DATE | RARF_HUB | SERIES_DEVICE_DATA_HIST | History Table: All approved and Disapproved Series Device equipment details. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved and Disapproved Series Device equipment details.
CHANGE_DESCRIPTION | RARF_HUB | SERIES_DEVICE_DATA_HIST |  | Description of Change, indicates if new Equipment is added; Existing Equipment is deleted or Updated
CONTINUOUS_RTG | RARF_HUB | SERIES_DEVICE_DATA_HIST |  | Continuous Rating.
DATE_LOADED | RARF_HUB | SERIES_DEVICE_DATA_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | SERIES_DEVICE_DATA_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
EFF_DATE | RARF_HUB | SERIES_DEVICE_DATA_HIST |  | Date when the Equipment will become effective in Model
EMGCY_RTG_2HR | RARF_HUB | SERIES_DEVICE_DATA_HIST |  | 2-hr Emergency Rating.
REACTANCE | RARF_HUB | SERIES_DEVICE_DATA_HIST |  | Reactance.
RESISTANCE | RARF_HUB | SERIES_DEVICE_DATA_HIST |  | Resistance.
RTG_15MIN | RARF_HUB | SERIES_DEVICE_DATA_HIST |  | 15-min Rating.
SD_CODE | RARF_HUB | SERIES_DEVICE_DATA_HIST |  | Unique Code for each Series Device equipment that is defined as the concatenation of SITE_CODE_SUBSTATION_CODE_SD_NAME.
SD_COMMENTS | RARF_HUB | SERIES_DEVICE_DATA_HIST |  | General comments on Series Device equipment.
SD_NAME | RARF_HUB | SERIES_DEVICE_DATA_HIST |  | Series Device Name.
SIDE1_PTI_BUS_NUM | RARF_HUB | SERIES_DEVICE_DATA_HIST |  | Side 1 - Bus Number (PTI Bus Number).
SIDE2_PTI_BUS_NUM | RARF_HUB | SERIES_DEVICE_DATA_HIST |  | Side 2 - Bus Number (PTI Bus Number).
SITE_CODE | RARF_HUB | SERIES_DEVICE_DATA_HIST |  | Unique Code for Resource Site.
SUBMISSION_TYPE | RARF_HUB | SERIES_DEVICE_DATA_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
SUBSTATION_CODE | RARF_HUB | SERIES_DEVICE_DATA_HIST |  | ERCOT Station Name (Station Code or Station Mnemonic).
VOLATGE | RARF_HUB | SERIES_DEVICE_DATA_HIST |  | Voltage Level.
DATE_LOADED | RARF_HUB | SERIES_DEVICE_DATA_SIDE | Latest Approved Connected switching Design Names(s), Side 1&2. | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format). |  | Latest Approved Connected switching Design Names(s), Side 1&2.
DATE_SUBMITTED | RARF_HUB | SERIES_DEVICE_DATA_SIDE |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
SD_CODE | RARF_HUB | SERIES_DEVICE_DATA_SIDE |  | Unique Code for each Series Device equipment that is defined as the concatenation of SITE_CODE_SUBSTATION_CODE_SD_NAME.
SIDE | RARF_HUB | SERIES_DEVICE_DATA_SIDE |  | 1 or 2.
SWITCH_DEVICE_NAME | RARF_HUB | SERIES_DEVICE_DATA_SIDE |  | Connected Switching Device Name(s)- Side 1 and Side 2.
APPROVED_DATE | RARF_HUB | SERIES_DEVICE_DATA_SIDE_HIST | History Table: All approved and Disapproved Connected switching Design Names(s), Side 1&2. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved and Disapproved Connected switching Design Names(s), Side 1&2.
DATE_LOADED | RARF_HUB | SERIES_DEVICE_DATA_SIDE_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | SERIES_DEVICE_DATA_SIDE_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
SD_CODE | RARF_HUB | SERIES_DEVICE_DATA_SIDE_HIST |  | Unique Code for each Series Device equipment that is defined as the concatenation of SITE_CODE_SUBSTATION_CODE_SD_NAME.
SIDE | RARF_HUB | SERIES_DEVICE_DATA_SIDE_HIST |  | 1 or 2.
SUBMISSION_TYPE | RARF_HUB | SERIES_DEVICE_DATA_SIDE_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
SWITCH_DEVICE_NAME | RARF_HUB | SERIES_DEVICE_DATA_SIDE_HIST |  | Connected Switching Device Name(s)- Side 1 and Side 2.
COMP_RETAILER | RARF_HUB | SITE_LOAD_SPLIT | Contains the Latest Approved Data if the Gen Site Load is split among multiple ESI IDs:. | Load Serving entity associated with that ESI ID If the Gen Site Load is split among multiple ESI IDs |  | Contains the Latest Approved Data if the Gen Site Load is split among multiple ESI IDs:.
COMP_RETAILER_DUNS | RARF_HUB | SITE_LOAD_SPLIT |  | Load Serving entity Duns# associated with that ESI ID If the Gen Site Load is split among multiple ESI IDs
DATE_LOADED | RARF_HUB | SITE_LOAD_SPLIT |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | SITE_LOAD_SPLIT |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
ESI_ID | RARF_HUB | SITE_LOAD_SPLIT |  | ESI ID.
ESIID_NUMBER | RARF_HUB | SITE_LOAD_SPLIT |  | ESIID NUMBER.
FIXED_LD_SPLIT | RARF_HUB | SITE_LOAD_SPLIT |  | Fixed Load Splitting % If the Gen Site Load is split among multiple ESI IDs
SITE_CODE | RARF_HUB | SITE_LOAD_SPLIT |  | Code for Resource Site -- Determined jointly with ERCOT
SITECODE_ESIID | RARF_HUB | SITE_LOAD_SPLIT |  | Concatenation of SITE_CODE_ESIID_ESIIDNUMBER.
TDSP_DUNS | RARF_HUB | SITE_LOAD_SPLIT |  | TDSP DUNS number
TDSP_PROVIDING_SVC | RARF_HUB | SITE_LOAD_SPLIT |  | Name of the TDSP that provides distribution service to the site
APPROVED_DATE | RARF_HUB | SITE_LOAD_SPLIT_HIST | History Table: Contains All the Approved and Disapproved Generation Site Load Split details data | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: Contains All the Approved and Disapproved Generation Site Load Split details data
COMP_RETAILER | RARF_HUB | SITE_LOAD_SPLIT_HIST |  | Load Serving entity associated with that ESI ID If the Gen Site Load is split among multiple ESI IDs
COMP_RETAILER_DUNS | RARF_HUB | SITE_LOAD_SPLIT_HIST |  | Load Serving entity Duns# associated with that ESI ID If the Gen Site Load is split among multiple ESI IDs
DATE_LOADED | RARF_HUB | SITE_LOAD_SPLIT_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | SITE_LOAD_SPLIT_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
ESI_ID | RARF_HUB | SITE_LOAD_SPLIT_HIST |  | ESI ID.
ESIID_NUMBER | RARF_HUB | SITE_LOAD_SPLIT_HIST |  | ESIID NUMBER.
FIXED_LD_SPLIT | RARF_HUB | SITE_LOAD_SPLIT_HIST |  | Fixed Load Splitting % If the Gen Site Load is split among multiple ESI IDs
SITE_CODE | RARF_HUB | SITE_LOAD_SPLIT_HIST |  | Code for Resource Site -- Determined jointly with ERCOT
SITECODE_ESIID | RARF_HUB | SITE_LOAD_SPLIT_HIST |  | Concatenation of SITE_CODE_ESIID_ESIIDNUMBER.
SUBMISSION_TYPE | RARF_HUB | SITE_LOAD_SPLIT_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
TDSP_DUNS | RARF_HUB | SITE_LOAD_SPLIT_HIST |  | TDSP DUNS number
TDSP_PROVIDING_SVC | RARF_HUB | SITE_LOAD_SPLIT_HIST |  | Name of the TDSP that provides distribution service to the site
AVG_LD_MVAR_SITE | RARF_HUB | SITECODES | Contains the latest Approved Generation Site details. | Amount of the total site generation MVAR output used for self serve and not available for the grid |  | Contains the latest Approved Generation Site details.
AVG_LD_MW_SITE | RARF_HUB | SITECODES |  | Amount of the total site generation MW output used for self serve and not available for the grid
CITY | RARF_HUB | SITECODES |  | Site Address: 'CITY' of the Generation Site location
CMZ_2003 | RARF_HUB | SITECODES |  | Congestion Management Zone for 2003
COUNTY | RARF_HUB | SITECODES |  | Site Address: 'County' of the Generation Site location
DATE_LOADED | RARF_HUB | SITECODES |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | SITECODES |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
EMAIL_PC | RARF_HUB | SITECODES |  | EMAIL address of the Primary Contact for the RARF
ERCOT_READ_FLG | RARF_HUB | SITECODES |  | Are the meters read (polled) by ERCOT? Y or N?.
ESI_ID | RARF_HUB | SITECODES |  | Site ESI ID
FAX_PC | RARF_HUB | SITECODES |  | Fax# of the Primary Contact for the RARF
FORM_COMP_DT | RARF_HUB | SITECODES |  | Date when the RARF form is filled out
GEN_LOAD_SPLIT_FLG | RARF_HUB | SITECODES |  | Indicates if Gen Site Load is split among multiple ESI IDs. Options: Y or N.
GROSS_CAPBLTY_MVAR_SITE | RARF_HUB | SITECODES |  | Private Network Gross Unit Reactive Capability
GROSS_CAPBLTY_MW_SITE | RARF_HUB | SITECODES |  | MW Gross Generation Capability for the Site
NAME_PC | RARF_HUB | SITECODES |  | Name of the Primary Contact for the RARF( The Primary Contact person - Site or facility contact for Generation Resources - Resource Entity contact for Load Resources who can address ERCOT questions regarding RARF submittal
NET_INTERCHNG_MVAR_SITE | RARF_HUB | SITECODES |  | MVAR Net Interchange with ERCOT grid
NET_INTERCHNG_MW_SITE | RARF_HUB | SITECODES |  | MW Net Interchange with ERCOT grid
NOTES_SITE | RARF_HUB | SITECODES |  | General Notes about the Generation Site
NUM_EPS_METERS | RARF_HUB | SITECODES |  | Total number of primary EPS meters associated with the Generation Site
ONELINE_SUBTD_FLG | RARF_HUB | SITECODES |  | One-Line Diagram Submitted? Y or N flag
PHONE_PC | RARF_HUB | SITECODES |  | Ph# of the Primary Contact for the RARF
PRIVATE_NTWK_SITE_FLG | RARF_HUB | SITECODES |  | Indicates if it is Private Network or not. Options: Y or N
PUN_MVAR_DISCHARGE_PCT | RARF_HUB | SITECODES |  | Discharge Lighting, percent of total MVAR load
PUN_MVAR_LARGEMTR_PCT | RARF_HUB | SITECODES |  | Large Motor, percent of total MVAR load
PUN_MVAR_OTHER_PCT | RARF_HUB | SITECODES |  | Other, percent of total MVAR load
PUN_MVAR_SMALLMTR_PCT | RARF_HUB | SITECODES |  | Small Motor, percent of total MVAR load
PUN_MW_DISCHARGE_PCT | RARF_HUB | SITECODES |  | Discharge Lighting, percent of total MW load
PUN_MW_LARGEMTR_PCT | RARF_HUB | SITECODES |  | Large Motor, percent of total MW load
PUN_MW_OTHER_PCT | RARF_HUB | SITECODES |  | Other, percent of total MW load
PUN_MW_RESISTIVE_PCT | RARF_HUB | SITECODES |  | Resistive (Heating) Load, percent of total MW load
PUN_MW_SMALLMTR_PCT | RARF_HUB | SITECODES |  | Small Motor, percent of total MW load
RE_BHND_NOIE_SMP_FLG | RARF_HUB | SITECODES |  | For resources that are connected to the grid behind NOIE settlement meter points. Is Resource behind a NOIE Settlement Meter Point? (Y,N).
RE_DUNS | RARF_HUB | SITECODES |  | Market Participant unique identifier as registered with ERCOT for Resource Entity ; RE Duns who submitted the RARF
RE_OWNED_NOIE_FLG | RARF_HUB | SITECODES |  | Indicate NOIE Ownership of resource: Y or N
RESOURCE_ID | RARF_HUB | SITECODES |  | Resource ID as determined by ERCOT
SITE_CODE | RARF_HUB | SITECODES |  | Code for Resource Site -- Determined jointly with ERCOT
SITE_IN_SRVC_DT | RARF_HUB | SITECODES |  | Site In-Service Date is the date when plant or unit was commissioned
SITE_NAME | RARF_HUB | SITECODES |  | Resource site or main facility name
SITE_STOP_SRVC_DT | RARF_HUB | SITECODES |  | Site Stop-Service Date is the date when plant or unit will be decommissioned or blank if not known.
STATE | RARF_HUB | SITECODES |  | Site Address: 'STATE' in which the SITE is located (Ex: TX).
STREET_ADDRESS | RARF_HUB | SITECODES |  | Site Address: 'Street Address' in which the SITE is located
SUBMIT_REASON | RARF_HUB | SITECODES |  | Reason for RARF Submittal, Options available are: New Site, Revision, Addition of unit(s), or Deletion of unit(s).
TDSP | RARF_HUB | SITECODES |  | Name of the TDSP that provides transmission or distribution service to the site
TDSP_DUNS | RARF_HUB | SITECODES |  | TDSP DUNS number
TITLE_PC | RARF_HUB | SITECODES |  | Title of the Primary Contact for the RARF
ZIPCODE | RARF_HUB | SITECODES |  | Site Address: 'Zipcode' of the SITE location
RE_CLAIM_NONMOD_STATUS | RARF_HUB | SITECODES |  | Is Resource claiming status as a Non-Modeled Generator as defined in ERCOT Protocol Section 2, Resource | Added 06/27/2012
RES_GREAT_TEN_MW | RARF_HUB | SITECODES |  | Is Resource >10 MW? | Added 06/27/2012
APPROVED_DATE | RARF_HUB | SITECODES_HIST | History Table: Contains All the Approved and Disapproved Generation Site details data | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: Contains All the Approved and Disapproved Generation Site details data
AVG_LD_MVAR_SITE | RARF_HUB | SITECODES_HIST |  | Amount of the total site generation MVAR output used for self serve and not available for the grid
AVG_LD_MW_SITE | RARF_HUB | SITECODES_HIST |  | Amount of the total site generation MW output used for self serve and not available for the grid
CITY | RARF_HUB | SITECODES_HIST |  | Site Address: 'CITY' of the Generation Site location
CMZ_2003 | RARF_HUB | SITECODES_HIST |  | Congestion Management Zone for 2003
COUNTY | RARF_HUB | SITECODES_HIST |  | Site Address: 'County' of the Generation Site location
DATE_LOADED | RARF_HUB | SITECODES_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | SITECODES_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
EMAIL_PC | RARF_HUB | SITECODES_HIST |  | EMAIL address of the Primary Contact for the RARF
ERCOT_READ_FLG | RARF_HUB | SITECODES_HIST |  | Are the meters read (polled) by ERCOT? Y or N?.
ESI_ID | RARF_HUB | SITECODES_HIST |  | Site ESI ID
FAX_PC | RARF_HUB | SITECODES_HIST |  | Fax# of the Primary Contact for the RARF
FORM_COMP_DT | RARF_HUB | SITECODES_HIST |  | Date when the RARF form is filled out
GEN_LOAD_SPLIT_FLG | RARF_HUB | SITECODES_HIST |  | Indicates if Gen Site Load is split among multiple ESI IDs. Options: Y or N.
GROSS_CAPBLTY_MVAR_SITE | RARF_HUB | SITECODES_HIST |  | Private Network Gross Unit Reactive Capability
GROSS_CAPBLTY_MW_SITE | RARF_HUB | SITECODES_HIST |  | MW Gross Generation Capability for the Site
NAME_PC | RARF_HUB | SITECODES_HIST |  | Name of the Primary Contact for the RARF( The Primary Contact person - Site or facility contact for Generation Resources - Resource Entity contact for Load Resources who can address ERCOT questions regarding RARF submittal
NET_INTERCHNG_MVAR_SITE | RARF_HUB | SITECODES_HIST |  | MVAR Net Interchange with ERCOT grid
NET_INTERCHNG_MW_SITE | RARF_HUB | SITECODES_HIST |  | MW Net Interchange with ERCOT grid
NOTES_SITE | RARF_HUB | SITECODES_HIST |  | General Notes about the Generation Site
NUM_EPS_METERS | RARF_HUB | SITECODES_HIST |  | Total number of primary EPS meters associated with the Generation Site
ONELINE_SUBTD_FLG | RARF_HUB | SITECODES_HIST |  | One-Line Diagram Submitted? Y or N flag
PHONE_PC | RARF_HUB | SITECODES_HIST |  | Ph# of the Primary Contact for the RARF
PRIVATE_NTWK_SITE_FLG | RARF_HUB | SITECODES_HIST |  | Indicates if it is Private Network or not. Options: Y or N
PUN_MVAR_DISCHARGE_PCT | RARF_HUB | SITECODES_HIST |  | Discharge Lighting, percent of total MVAR load
PUN_MVAR_LARGEMTR_PCT | RARF_HUB | SITECODES_HIST |  | Large Motor, percent of total MVAR load
PUN_MVAR_OTHER_PCT | RARF_HUB | SITECODES_HIST |  | Other, percent of total MVAR load
PUN_MVAR_SMALLMTR_PCT | RARF_HUB | SITECODES_HIST |  | Small Motor, percent of total MVAR load
PUN_MW_DISCHARGE_PCT | RARF_HUB | SITECODES_HIST |  | Discharge Lighting, percent of total MW load
PUN_MW_LARGEMTR_PCT | RARF_HUB | SITECODES_HIST |  | Large Motor, percent of total MW load
PUN_MW_OTHER_PCT | RARF_HUB | SITECODES_HIST |  | Other, percent of total MW load
PUN_MW_RESISTIVE_PCT | RARF_HUB | SITECODES_HIST |  | Resistive (Heating) Load, percent of total MW load
PUN_MW_SMALLMTR_PCT | RARF_HUB | SITECODES_HIST |  | Small Motor, percent of total MW load
RE_BHND_NOIE_SMP_FLG | RARF_HUB | SITECODES_HIST |  | For resources that are connected to the grid behind NOIE settlement meter points. Is Resource behind a NOIE Settlement Meter Point? (Y,N).
RE_DUNS | RARF_HUB | SITECODES_HIST |  | Market Participant unique identifier as registered with ERCOT for Resource Entity ; RE Duns who submitted the RARF
RE_OWNED_NOIE_FLG | RARF_HUB | SITECODES_HIST |  | Indicate NOIE Ownership of resource: Y or N
RESOURCE_ID | RARF_HUB | SITECODES_HIST |  | Resource ID as determined by ERCOT
SITE_CODE | RARF_HUB | SITECODES_HIST |  | Code for Resource Site -- Determined jointly with ERCOT
SITE_IN_SRVC_DT | RARF_HUB | SITECODES_HIST |  | Site In-Service Date is the date when plant or unit was commissioned
SITE_NAME | RARF_HUB | SITECODES_HIST |  | Resource site or main facility name
SITE_STOP_SRVC_DT | RARF_HUB | SITECODES_HIST |  | Site Stop-Service Date is the date when plant or unit will be decommissioned or blank if not known.
STATE | RARF_HUB | SITECODES_HIST |  | Site Address: 'STATE' in which the SITE is located (Ex: TX).
STREET_ADDRESS | RARF_HUB | SITECODES_HIST |  | Site Address: 'Street Address' in which the SITE is located
SUBMISSION_TYPE | RARF_HUB | SITECODES_HIST |  | Indicates whether MP Submitted the RARF(External Submission) or If a RARF is re-loaded internally
SUBMIT_REASON | RARF_HUB | SITECODES_HIST |  | Reason for RARF Submittal, Options available are: New Site, Revision, Addition of unit(s), or Deletion of unit(s).
TDSP | RARF_HUB | SITECODES_HIST |  | Name of the TDSP that provides transmission or distribution service to the site
TDSP_DUNS | RARF_HUB | SITECODES_HIST |  | TDSP DUNS number
TITLE_PC | RARF_HUB | SITECODES_HIST |  | Title of the Primary Contact for the RARF
ZIPCODE | RARF_HUB | SITECODES_HIST |  | Site Address: 'Zipcode' of the SITE location
RE_CLAIM_NONMOD_STATUS | RARF_HUB | SITECODES_HIST |  | Is Resource claiming status as a Non-Modeled Generator as defined in ERCOT Protocol Section 2, Resource | Added 06/27/2012
RES_GREAT_TEN_MW | RARF_HUB | SITECODES_HIST |  | Is Resource >10 MW? | Added 06/27/2012
CHANGE_DESCRIPTION | RARF_HUB | STATIC_VAR_COMP | Latest Approved STATIC VAR Compensator Details. | Description of Change, indicates if new Equipment is added; Existing Equipment is deleted or Updated |  | Latest Approved STATIC VAR Compensator Details.
COMMENTS_STATIC_VAR_COMP | RARF_HUB | STATIC_VAR_COMP |  | General comments on the Static Var compensator equipment.
DATE_LOADED | RARF_HUB | STATIC_VAR_COMP |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | STATIC_VAR_COMP |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
EFF_DATE | RARF_HUB | STATIC_VAR_COMP |  | Date when the Equipment will become effective in Model
FIXED_MVAR | RARF_HUB | STATIC_VAR_COMP |  | Fixed MVAR (VAR injection at nominal voltage).
MAX_ADM_LIMIT | RARF_HUB | STATIC_VAR_COMP |  | Maximum Admittance Limits (100 MVA Base).
MAX_STD_STATE_REACT | RARF_HUB | STATIC_VAR_COMP |  | Maximum Steady State Reactive Power Limits.
MAX_THRESH_REACT | RARF_HUB | STATIC_VAR_COMP |  | Maximum Threshold (post contingency) Reactive Power Limits.
MAX_VOLT_THRESH | RARF_HUB | STATIC_VAR_COMP |  | Maximum Voltage Threshold (100 MVA Base).
MIN_ADM_LIMIT | RARF_HUB | STATIC_VAR_COMP |  | Minimum Admittance Limits (100 MVA Base).
MIN_STD_STATE_REACT | RARF_HUB | STATIC_VAR_COMP |  | Minimum Steady State Reactive Power Limits.
MIN_THRESH_REACT | RARF_HUB | STATIC_VAR_COMP |  | Minimum Threshold (post contingency) Reactive Power Limits.
MIN_VOLT_THRESH | RARF_HUB | STATIC_VAR_COMP |  | Minimum Voltage Threshold (100 MVA Base).
SITE_CODE | RARF_HUB | STATIC_VAR_COMP |  | Unique code for Resource Site.
SUBSTATION_CODE | RARF_HUB | STATIC_VAR_COMP |  | ERCOT Station Name (Station Code or Station Mnemonic).
SVC_BASE_VOLT | RARF_HUB | STATIC_VAR_COMP |  | SVC Base Voltage Level.
SVC_CODE | RARF_HUB | STATIC_VAR_COMP |  | Unique Code each Static Var compensator defined as the Concatenation of SITE_CODE_SUBSTATION_CODE_SVC_NAME.
SVC_NAME | RARF_HUB | STATIC_VAR_COMP |  | SVC Name.
DATE_LOADED | RARF_HUB | STATIC_VAR_COMP_DEVICES | Latest Approved Static Var Compensator Device Details (Child Table to the above Table). | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format). |  | Latest Approved Static Var Compensator Device Details (Child Table to the above Table).
DATE_SUBMITTED | RARF_HUB | STATIC_VAR_COMP_DEVICES |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
SVC_CODE | RARF_HUB | STATIC_VAR_COMP_DEVICES |  | Unique Code each Static Var compensator defined as the Concatenation of SITE_CODE_SUBSTATION_CODE_SVC_NAME.
SWITCH_DEVICE_NAME | RARF_HUB | STATIC_VAR_COMP_DEVICES |  | Device Name(s) - that this reactive device is directly connected to.
APPROVED_DATE | RARF_HUB | STATIC_VAR_COMP_DEVICES_HIST | History Table: All approved and disapproved STATIC VAR Compensator Devices Details. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved and disapproved STATIC VAR Compensator Devices Details.
DATE_LOADED | RARF_HUB | STATIC_VAR_COMP_DEVICES_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | STATIC_VAR_COMP_DEVICES_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
SUBMISSION_TYPE | RARF_HUB | STATIC_VAR_COMP_DEVICES_HIST |  | Submission Type: Internal or External.
SVC_CODE | RARF_HUB | STATIC_VAR_COMP_DEVICES_HIST |  | Unique Code each Static Var compensator defined as the Concatenation of SITE_CODE_SUBSTATION_CODE_SVC_NAME.
SWITCH_DEVICE_NAME | RARF_HUB | STATIC_VAR_COMP_DEVICES_HIST |  | Device Name(s) - that this reactive device is directly connected to.
APPROVED_DATE | RARF_HUB | STATIC_VAR_COMP_HIST | History Table: All approved and disapproved STATIC VAR Compensator Details. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved and disapproved STATIC VAR Compensator Details.
CHANGE_DESCRIPTION | RARF_HUB | STATIC_VAR_COMP_HIST |  | Description of Change, indicates if new Equipment is added; Existing Equipment is deleted or Updated
COMMENTS_STATIC_VAR_COMP | RARF_HUB | STATIC_VAR_COMP_HIST |  | General comments on the Static Var compensator equipment.
DATE_LOADED | RARF_HUB | STATIC_VAR_COMP_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | STATIC_VAR_COMP_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
EFF_DATE | RARF_HUB | STATIC_VAR_COMP_HIST |  | Date when the Equipment will become effective in Model
FIXED_MVAR | RARF_HUB | STATIC_VAR_COMP_HIST |  | Fixed MVAR (VAR injection at nominal voltage).
MAX_ADM_LIMIT | RARF_HUB | STATIC_VAR_COMP_HIST |  | Maximum Admittance Limits (100 MVA Base).
MAX_STD_STATE_REACT | RARF_HUB | STATIC_VAR_COMP_HIST |  | Maximum Steady State Reactive Power Limits.
MAX_THRESH_REACT | RARF_HUB | STATIC_VAR_COMP_HIST |  | Maximum Threshold (post contingency) Reactive Power Limits.
MAX_VOLT_THRESH | RARF_HUB | STATIC_VAR_COMP_HIST |  | Maximum Voltage Threshold (100 MVA Base).
MIN_ADM_LIMIT | RARF_HUB | STATIC_VAR_COMP_HIST |  | Minimum Admittance Limits (100 MVA Base).
MIN_STD_STATE_REACT | RARF_HUB | STATIC_VAR_COMP_HIST |  | Minimum Steady State Reactive Power Limits.
MIN_THRESH_REACT | RARF_HUB | STATIC_VAR_COMP_HIST |  | Minimum Threshold (post contingency) Reactive Power Limits.
MIN_VOLT_THRESH | RARF_HUB | STATIC_VAR_COMP_HIST |  | Minimum Voltage Threshold (100 MVA Base).
SITE_CODE | RARF_HUB | STATIC_VAR_COMP_HIST |  | Unique code for Resource Site.
SUBMISSION_TYPE | RARF_HUB | STATIC_VAR_COMP_HIST |  | Submission Type: Internal or External.
SUBSTATION_CODE | RARF_HUB | STATIC_VAR_COMP_HIST |  | ERCOT Station Name (Station Code or Station Mnemonic).
SVC_BASE_VOLT | RARF_HUB | STATIC_VAR_COMP_HIST |  | SVC Base Voltage Level.
SVC_CODE | RARF_HUB | STATIC_VAR_COMP_HIST |  | Unique Code each Static Var compensator defined as the Concatenation of SITE_CODE_SUBSTATION_CODE_SVC_NAME.
SVC_NAME | RARF_HUB | STATIC_VAR_COMP_HIST |  | SVC Name.
ASST_DMPG | RARF_HUB | SUBSYNC | Latest Approved SUBSYNC RESONANCE Data. | Associated damping: The damping associated with each mass either in p.u. torque/p.u. speed deviation, or lbf.ft.sec/rad. |  | Latest Approved SUBSYNC RESONANCE Data.
DATE_LOADED | RARF_HUB | SUBSYNC |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | SUBSYNC |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DMPG_UNITS | RARF_HUB | SUBSYNC |  | Damping units: p.u. torque/p.u. speed or lbf.ft.sec/rad.
INERTIA_UNITS | RARF_HUB | SUBSYNC |  | Inertia units:MW's, MVA, or lbm.ft².
MASS | RARF_HUB | SUBSYNC |  | Mass Identifier: Identification of the masses- HP, IP, LP1, LP2, EXC, etc
MASS_INERTIA | RARF_HUB | SUBSYNC |  | Mass Inertia: H-value. The inertia constant of each mass, either in MW's, MVA, or lbm.ft².
NAME | RARF_HUB | SUBSYNC |  | NAME- Subsync Resonance Mass (from 1 to 5 ).
STFNS_BTWN_MASSES | RARF_HUB | SUBSYNC |  | Stiffness between Masses: The stiffness (spring constant) between each two mass, either in p.u. torque/rad, or lbf.ft/rad (Coupling).
STFNS_UNITS | RARF_HUB | SUBSYNC |  | Stiffness units: p.u. torque/rad or lbf.ft/rad.
UNIT_CODE | RARF_HUB | SUBSYNC |  | Concatenated mnemonic of Resource Site Code and Unit name (e.g CBY_CBYG1) where CBY is Site_code and CBYG1 is Unit Name.
APPROVED_DATE | RARF_HUB | SUBSYNC_HIST | History of all Approved and Disapproved SUBSYNC RESONANCE data is stored. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History of all Approved and Disapproved SUBSYNC RESONANCE data is stored.
ASST_DMPG | RARF_HUB | SUBSYNC_HIST |  | Associated damping: The damping associated with each mass either in p.u. torque/p.u. speed deviation, or lbf.ft.sec/rad.
DATE_LOADED | RARF_HUB | SUBSYNC_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | SUBSYNC_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DMPG_UNITS | RARF_HUB | SUBSYNC_HIST |  | Damping units: p.u. torque/p.u. speed or lbf.ft.sec/rad.
INERTIA_UNITS | RARF_HUB | SUBSYNC_HIST |  | Inertia units:MW's, MVA, or lbm.ft².
MASS | RARF_HUB | SUBSYNC_HIST |  | Mass Identifier: Identification of the masses- HP, IP, LP1, LP2, EXC, etc
MASS_INERTIA | RARF_HUB | SUBSYNC_HIST |  | Mass Inertia: H-value. The inertia constant of each mass, either in MW's, MVA, or lbm.ft².
NAME | RARF_HUB | SUBSYNC_HIST |  | NAME- Subsync Resonance Mass (from 1 to 5 ).
STFNS_BTWN_MASSES | RARF_HUB | SUBSYNC_HIST |  | Stiffness between Masses: The stiffness (spring constant) between each two mass, either in p.u. torque/rad, or lbf.ft/rad (Coupling).
STFNS_UNITS | RARF_HUB | SUBSYNC_HIST |  | Stiffness units: p.u. torque/rad or lbf.ft/rad.
SUBMISSION_TYPE | RARF_HUB | SUBSYNC_HIST |  | Submission Type: Internal or External.
UNIT_CODE | RARF_HUB | SUBSYNC_HIST |  | Concatenated mnemonic of Resource Site Code and Unit name (e.g CBY_CBYG1) where CBY is Site_code and CBYG1 is Unit Name.
DATE_LOADED | RARF_HUB | TRAIN | Latest Approved Combined Cycle Train Information Details. | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format). |  | Latest Approved Combined Cycle Train Information Details.
DATE_SUBMITTED | RARF_HUB | TRAIN |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
FUEL_TRANSTYPE_TRN | RARF_HUB | TRAIN |  | Fuel Transportation Type.
NERC_NUM | RARF_HUB | TRAIN |  | NERC Number.
NOTES_UNIT | RARF_HUB | TRAIN |  | General Notes.
PUC_NUM | RARF_HUB | TRAIN |  | PUC Registration Number.
RES_CATG_TRN | RARF_HUB | TRAIN |  | Resource Category of the CC Train.
SITE_CODE | RARF_HUB | TRAIN |  | Unique Code for Resource Site.
TRAIN_CODE | RARF_HUB | TRAIN |  | Mnemonic for Combined Cycle Train: Unique Code for each Train in a Site, defined as the concatenation of SITE_CODE_TRAIN_NAME.
TRAIN_NAME | RARF_HUB | TRAIN |  | Train Name.
TRN_AUG_CHILLERS_FLG | RARF_HUB | TRAIN |  | Is train augmented with Chiller(s)? Y or N.
TRN_AUG_DUCTBRNRS_FLG | RARF_HUB | TRAIN |  | Is train augmented with Duct Burner(s)? Y or N.
TRN_AUG_EVAP_CLRS_FLG | RARF_HUB | TRAIN |  | Is train augmented with Evap Cooler(s)? Y or N.
TRN_OTHER_AUG | RARF_HUB | TRAIN |  | Other augmentation? Y or N.
TRN_QUAL_FACILITY_FLG | RARF_HUB | TRAIN |  | Qualifying facility Flag: Y or N.
TRN_UNIT_END_DATE | RARF_HUB | TRAIN |  | Date when the TRAIN is being stopped.
TRN_UNIT_START_DATE | RARF_HUB | TRAIN |  | Date Effective when the Train is added as part of the combined cycle plant.
LAT_CENTER_PLT | RARF_HUB | TRAIN |  | Latitude of center of Plant | Added 06/27/2012
LONG_CENTER_PLT | RARF_HUB | TRAIN |  | Longitude of center of Plant | Added 06/27/2012
NON_MOD_GEN | RARF_HUB | TRAIN |  | Non_Moldeled Generator | Added 06/27/2012
APPROVED_DATE | RARF_HUB | TRAIN_HIST | History Table: All approved and Disapproved Combined Cycle Train Information. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved and Disapproved Combined Cycle Train Information.
DATE_LOADED | RARF_HUB | TRAIN_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | TRAIN_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
FUEL_TRANSTYPE_TRN | RARF_HUB | TRAIN_HIST |  | Fuel Transportation Type.
NERC_NUM | RARF_HUB | TRAIN_HIST |  | NERC Number.
NOTES_UNIT | RARF_HUB | TRAIN_HIST |  | General Notes.
PUC_NUM | RARF_HUB | TRAIN_HIST |  | PUC Registration Number.
RES_CATG_TRN | RARF_HUB | TRAIN_HIST |  | Resource Category of the CC Train.
SITE_CODE | RARF_HUB | TRAIN_HIST |  | Unique Code for Resource Site.
SUBMISSION_TYPE | RARF_HUB | TRAIN_HIST |  | Submission Type: Internal or External.
TRAIN_CODE | RARF_HUB | TRAIN_HIST |  | Mnemonic for Combined Cycle Train: Unique Code for each Train in a Site, defined as the concatenation of SITE_CODE_TRAIN_NAME.
TRAIN_NAME | RARF_HUB | TRAIN_HIST |  | Train Name.
TRN_AUG_CHILLERS_FLG | RARF_HUB | TRAIN_HIST |  | Is train augmented with Chiller(s)? Y or N.
TRN_AUG_DUCTBRNRS_FLG | RARF_HUB | TRAIN_HIST |  | Is train augmented with Duct Burner(s)? Y or N.
TRN_AUG_EVAP_CLRS_FLG | RARF_HUB | TRAIN_HIST |  | Is train augmented with Evap Cooler(s)? Y or N.
TRN_OTHER_AUG | RARF_HUB | TRAIN_HIST |  | Other augmentation? Y or N.
TRN_QUAL_FACILITY_FLG | RARF_HUB | TRAIN_HIST |  | Qualifying facility Flag: Y or N.
TRN_UNIT_END_DATE | RARF_HUB | TRAIN_HIST |  | Date when the TRAIN is being stopped.
TRN_UNIT_START_DATE | RARF_HUB | TRAIN_HIST |  | Date Effective when the Train is added as part of the combined cycle plant.
LAT_CENTER_PLT | RARF_HUB | TRAIN_HIST |  | Latitude of center of Plant | Added 06/27/2012
LONG_CENTER_PLT | RARF_HUB | TRAIN_HIST |  | Longitude of center of Plant | Added 06/27/2012
NON_MOD_GEN | RARF_HUB | TRAIN_HIST |  | Non_Moldeled Generator | Added 06/27/2012
ACCEPT_DEV_VOLT_TARGET | RARF_HUB | TRANSFORMER | Latest Approved Transformer equipment Details. | Acceptable Deviation of Target Voltage in Percent. |  | Latest Approved Transformer equipment Details.
AUTO_VOLT_REG | RARF_HUB | TRANSFORMER |  | Automatic Voltage Regulation Flag: Y or N.
CHANGE_DESCRIPTION | RARF_HUB | TRANSFORMER |  | Description of Change, indicates if new Equipment is added; Existing Equipment is deleted or Updated
COMMENTS_TRANSFORMER | RARF_HUB | TRANSFORMER |  | General comments on the Transformer equipment.
CONTINUOUS_RTG | RARF_HUB | TRANSFORMER |  | Continuous Rating.
DATE_LOADED | RARF_HUB | TRANSFORMER |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | TRANSFORMER |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
EFF_DATE | RARF_HUB | TRANSFORMER |  | Date when the Equipment will become effective in Model
EMGCY_RTG_2HR | RARF_HUB | TRANSFORMER |  | 2-hr Emergency Rating.
FOLLOWER_NAME | RARF_HUB | TRANSFORMER |  | Follower Name (can be same as this transformer).
GSU_TRANSFORMER_FLG | RARF_HUB | TRANSFORMER |  | Generation Step-Up Transformer? Y or N.
HIGH_CONNECTION | RARF_HUB | TRANSFORMER |  | High Side Voltage Connection - Wye or Delta.
HIGH_MANU_VOLT | RARF_HUB | TRANSFORMER |  | High Side Manufactured Nominal Voltage.
HIGH_NOLOAD | RARF_HUB | TRANSFORMER |  | High Voltage Limit (no-load).
HIGH_PTI | RARF_HUB | TRANSFORMER |  | High Side Voltage Level (PTI).
LOADTAP_CHNGR_FLG | RARF_HUB | TRANSFORMER |  | Load Tap Changer (Y/N).
LOCN_TAP_CHNGR | RARF_HUB | TRANSFORMER |  | Location of tap changer.
LOW_CONNECTION | RARF_HUB | TRANSFORMER |  | Connection(WYE OR DELTA).
LOW_MANU_VOLT | RARF_HUB | TRANSFORMER |  | Low Side Manufactured Nominal Voltage.
LOW_NOLOAD | RARF_HUB | TRANSFORMER |  | Low Voltage Limit (no-load).
LOW_PTI | RARF_HUB | TRANSFORMER |  | Low Side Voltage Level (PTI).
MASTER_FOLLOW_FLG | RARF_HUB | TRANSFORMER |  | Is this transformer in Master / Follower of Current Balancing configuration? Y or N.
MASTER_NAME | RARF_HUB | TRANSFORMER |  | Master Name (can be same as this transformer).
REG_KV_BASE | RARF_HUB | TRANSFORMER |  | Base kV of Regulated Side.
REG_KV_TARGET | RARF_HUB | TRANSFORMER |  | Target kV of Regulated Side.
RTG_15MIN | RARF_HUB | TRANSFORMER |  | 15-min Rating.
SERIES_REACT | RARF_HUB | TRANSFORMER |  | Series Reactance (100 MVA Base).
SERIES_RESIST | RARF_HUB | TRANSFORMER |  | Series Reactance (100 MVA Base).
SITE_CODE | RARF_HUB | TRANSFORMER |  | Unique code for Site.
SUBSTATION_CODE | RARF_HUB | TRANSFORMER |  | Unique Code for each substation under a SITE.
TRANSFORMER_CODE | RARF_HUB | TRANSFORMER |  | Unique Code for each Transformer defined as the concatenation of SITE_CODE_SUBSTATION_CODE_TRANSFORMER_NAME.
TRANSFORMER_NAME | RARF_HUB | TRANSFORMER |  | Transformer Name.
SUBSTATION_CODE | RARF_HUB | TRANSFORMER |  | ERCOT Station Name (Station Code or Station Mnemonic) | Added 06/27/2012
TRANSFORMER_NAME | RARF_HUB | TRANSFORMER |  | Transformer Name | Added 06/27/2012
ZERO_SEQ_DATA_WINDING_CON_CODE | RARF_HUB | TRANSFORMER |  | Zero Sequence Data - Winding Connection Code (1-9) | Added 06/27/2012
ZERO_SEQ_GRUND_REACTANCE_IMPEDANCE_GRUND_TRANS_PU | RARF_HUB | TRANSFORMER |  | Zero Sequence Grounding Reactance For An Impedance Grounded Transformer In P.u. (100 Mva Base) | Added 06/27/2012
ZERO_SEQ_GRUND_RESISTANCE_IMPEDANCE_GRUND_TRANS_PU | RARF_HUB | TRANSFORMER |  | Zero Sequence Grounding Resistance For An Impedance Grounded Transformer In P.u. (100 Mva Base) | Added 06/27/2012
ZERO_SEQ_TRANS_REACTANCE_PU | RARF_HUB | TRANSFORMER |  | Zero Sequence Reactance In P.u. (100 Mva Base) | Added 06/27/2012
ZERO_SEQ_TRANS_RESISTANCE_PU | RARF_HUB | TRANSFORMER |  | Zero Sequence Resistance In P.u. (100 Mva Base) | Added 06/27/2012
DATE_LOADED | RARF_HUB | TRANSFORMER_DEVICES | Latest Approved Transformer connected Device Details. | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format). |  | Latest Approved Transformer connected Device Details.
DATE_SUBMITTED | RARF_HUB | TRANSFORMER_DEVICES |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DEVICE_NAME | RARF_HUB | TRANSFORMER_DEVICES |  | Low Side Voltage Connected device(s) (list on separate lines) and High Side Voltage Connected device(s) (list on separate lines).
HIGH_LOW_VOLT_FLG | RARF_HUB | TRANSFORMER_DEVICES |  | HIGH/LOW Voltage Flag.
TRANSFORMER_CODE | RARF_HUB | TRANSFORMER_DEVICES |  | Unique Code for each Transformer defined as the concatenation of SITE_CODE_SUBSTATION_CODE_TRANSFORMER_NAME.
APPROVED_DATE | RARF_HUB | TRANSFORMER_DEVICES_HIST | History Table: All approved/Disapproved Transformer connected Devices Details. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved/Disapproved Transformer connected Devices Details.
DATE_LOADED | RARF_HUB | TRANSFORMER_DEVICES_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | TRANSFORMER_DEVICES_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DEVICE_NAME | RARF_HUB | TRANSFORMER_DEVICES_HIST |  | Low Side Voltage Connected device(s) (list on separate lines) and High Side Voltage Connected device(s) (list on separate lines).
HIGH_LOW_VOLT_FLG | RARF_HUB | TRANSFORMER_DEVICES_HIST |  | HIGH/LOW Voltage Flag.
SUBMISSION_TYPE | RARF_HUB | TRANSFORMER_DEVICES_HIST |  | Submission Type: Internal or External.
TRANSFORMER_CODE | RARF_HUB | TRANSFORMER_DEVICES_HIST |  | Unique Code for each Transformer defined as the concatenation of SITE_CODE_SUBSTATION_CODE_TRANSFORMER_NAME.
ACCEPT_DEV_VOLT_TARGET | RARF_HUB | TRANSFORMER_HIST | History Table: All approved/Disapproved Transformer Details. | Acceptable Deviation of Target Voltage in Percent. |  | History Table: All approved/Disapproved Transformer Details.
APPROVED_DATE | RARF_HUB | TRANSFORMER_HIST |  | Date & time when the RARF is approved. NULL indicates Disapproved RARF
AUTO_VOLT_REG | RARF_HUB | TRANSFORMER_HIST |  | Automatic Voltage Regulation Flag: Y or N.
CHANGE_DESCRIPTION | RARF_HUB | TRANSFORMER_HIST |  | Description of Change, indicates if new Equipment is added; Existing Equipment is deleted or Updated
COMMENTS_TRANSFORMER | RARF_HUB | TRANSFORMER_HIST |  | General comments on the Transformer equipment.
CONTINUOUS_RTG | RARF_HUB | TRANSFORMER_HIST |  | Continuous Rating.
DATE_LOADED | RARF_HUB | TRANSFORMER_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | TRANSFORMER_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
EFF_DATE | RARF_HUB | TRANSFORMER_HIST |  | Date when the Equipment will become effective in Model
EMGCY_RTG_2HR | RARF_HUB | TRANSFORMER_HIST |  | 2-hr Emergency Rating.
FOLLOWER_NAME | RARF_HUB | TRANSFORMER_HIST |  | Follower Name (can be same as this transformer).
GSU_TRANSFORMER_FLG | RARF_HUB | TRANSFORMER_HIST |  | Generation Step-Up Transformer? Y or N.
HIGH_CONNECTION | RARF_HUB | TRANSFORMER_HIST |  | High Side Voltage Connection - Wye or Delta.
HIGH_MANU_VOLT | RARF_HUB | TRANSFORMER_HIST |  | High Side Manufactured Nominal Voltage.
HIGH_NOLOAD | RARF_HUB | TRANSFORMER_HIST |  | High Voltage Limit (no-load).
HIGH_PTI | RARF_HUB | TRANSFORMER_HIST |  | High Side Voltage Level (PTI).
LOADTAP_CHNGR_FLG | RARF_HUB | TRANSFORMER_HIST |  | Load Tap Changer (Y/N).
LOCN_TAP_CHNGR | RARF_HUB | TRANSFORMER_HIST |  | Location of tap changer.
LOW_CONNECTION | RARF_HUB | TRANSFORMER_HIST |  | Connection(WYE OR DELTA).
LOW_MANU_VOLT | RARF_HUB | TRANSFORMER_HIST |  | Low Side Manufactured Nominal Voltage.
LOW_NOLOAD | RARF_HUB | TRANSFORMER_HIST |  | Low Voltage Limit (no-load).
LOW_PTI | RARF_HUB | TRANSFORMER_HIST |  | Low Side Voltage Level (PTI).
MASTER_FOLLOW_FLG | RARF_HUB | TRANSFORMER_HIST |  | Is this transformer in Master / Follower of Current Balancing configuration? Y or N.
MASTER_NAME | RARF_HUB | TRANSFORMER_HIST |  | Master Name (can be same as this transformer).
REG_KV_BASE | RARF_HUB | TRANSFORMER_HIST |  | Base kV of Regulated Side.
REG_KV_TARGET | RARF_HUB | TRANSFORMER_HIST |  | Target kV of Regulated Side.
RTG_15MIN | RARF_HUB | TRANSFORMER_HIST |  | 15-min Rating.
SERIES_REACT | RARF_HUB | TRANSFORMER_HIST |  | Series Reactance (100 MVA Base).
SERIES_RESIST | RARF_HUB | TRANSFORMER_HIST |  | Series Reactance (100 MVA Base).
SITE_CODE | RARF_HUB | TRANSFORMER_HIST |  | Unique code for Site.
SUBMISSION_TYPE | RARF_HUB | TRANSFORMER_HIST |  | Submission Type: Internal or External.
SUBSTATION_CODE | RARF_HUB | TRANSFORMER_HIST |  | Unique Code for each substation under a SITE.
TRANSFORMER_CODE | RARF_HUB | TRANSFORMER_HIST |  | Unique Code for each Transformer defined as the concatenation of SITE_CODE_SUBSTATION_CODE_TRANSFORMER_NAME.
TRANSFORMER_NAME | RARF_HUB | TRANSFORMER_HIST |  | Transformer Name.
SUBSTATION_CODE | RARF_HUB | TRANSFORMER_HIST |  | ERCOT Station Name (Station Code or Station Mnemonic) | Added 06/27/2012
TRANSFORMER_NAME | RARF_HUB | TRANSFORMER_HIST |  | Transformer Name | Added 06/27/2012
ZERO_SEQ_DATA_WINDING_CON_CODE | RARF_HUB | TRANSFORMER_HIST |  | Zero Sequence Data - Winding Connection Code (1-9) | Added 06/27/2012
ZERO_SEQ_GRUND_REACTANCE_IMPEDANCE_GRUND_TRANS_PU | RARF_HUB | TRANSFORMER_HIST |  | Zero Sequence Grounding Reactance For An Impedance Grounded Transformer In P.u. (100 Mva Base) | Added 06/27/2012
ZERO_SEQ_GRUND_RESISTANCE_IMPEDANCE_GRUND_TRANS_PU | RARF_HUB | TRANSFORMER_HIST |  | Zero Sequence Grounding Resistance For An Impedance Grounded Transformer In P.u. (100 Mva Base) | Added 06/27/2012
ZERO_SEQ_TRANS_REACTANCE_PU | RARF_HUB | TRANSFORMER_HIST |  | Zero Sequence Reactance In P.u. (100 Mva Base) | Added 06/27/2012
ZERO_SEQ_TRANS_RESISTANCE_PU | RARF_HUB | TRANSFORMER_HIST |  | Zero Sequence Resistance In P.u. (100 Mva Base) | Added 06/27/2012
DATE_LOADED | RARF_HUB | TRANSFORMER_TAP_SETTINGS | Latest Approved Transformer Tap Setting Details. | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format). |  | Latest Approved Transformer Tap Setting Details.
DATE_SUBMITTED | RARF_HUB | TRANSFORMER_TAP_SETTINGS |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
HIGHEST_POS | RARF_HUB | TRANSFORMER_TAP_SETTINGS |  | Highest Tap Position.
HIGHEST_VOLT | RARF_HUB | TRANSFORMER_TAP_SETTINGS |  | Low Tap Settings - Voltage at Highest Tap Position & High Tap Settings - Voltage at Highest Tap Position.
LOW_HIGH_FLG | RARF_HUB | TRANSFORMER_TAP_SETTINGS |  | LOW/HIGH Flag.
LOWEST_POS | RARF_HUB | TRANSFORMER_TAP_SETTINGS |  | Lowest Tap Position.
LOWEST_VOLT | RARF_HUB | TRANSFORMER_TAP_SETTINGS |  | High Tap Settings – Voltage at Lowest Tap Position & Low Tap Settings - Voltage at Lowest Tap Position.
MANU_VOLT_TAP_POS | RARF_HUB | TRANSFORMER_TAP_SETTINGS |  | Nominal Tap Position (Neutral Step).
NORMAL_POS | RARF_HUB | TRANSFORMER_TAP_SETTINGS |  | Normal Tap Position.
STEP_VOLT | RARF_HUB | TRANSFORMER_TAP_SETTINGS |  | Percentage of tap range for each step (ex.6.25%/step.).
TOTAL_NUM | RARF_HUB | TRANSFORMER_TAP_SETTINGS |  | Total Number of Tap Positions.
TRANSFORMER_CODE | RARF_HUB | TRANSFORMER_TAP_SETTINGS |  | Unique Code for each Transformer defined as the concatenation of SITE_CODE_SUBSTATION_CODE_TRANSFORMER_NAME.
CHANGE_DESCRIPTION | RARF_HUB | TRANSFORMER_TAP_SETTINGS |  | DESCRIPTION OF CHANGE | Added 06/27/2012
APPROVED_DATE | RARF_HUB | TRANSFORMER_TAP_SETTINGS_HIST | History Table: All approved/Disapproved Transformer Tap Setting Details. | Date & time when the RARF is approved. NULL indicates Disapproved RARF |  | History Table: All approved/Disapproved Transformer Tap Setting Details.
DATE_LOADED | RARF_HUB | TRANSFORMER_TAP_SETTINGS_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | TRANSFORMER_TAP_SETTINGS_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
HIGHEST_POS | RARF_HUB | TRANSFORMER_TAP_SETTINGS_HIST |  | Highest Tap Position.
HIGHEST_VOLT | RARF_HUB | TRANSFORMER_TAP_SETTINGS_HIST |  | Low Tap Settings - Voltage at Highest Tap Position & High Tap Settings - Voltage at Highest Tap Position.
LOW_HIGH_FLG | RARF_HUB | TRANSFORMER_TAP_SETTINGS_HIST |  | LOW/HIGH Flag.
LOWEST_POS | RARF_HUB | TRANSFORMER_TAP_SETTINGS_HIST |  | Lowest Tap Position.
LOWEST_VOLT | RARF_HUB | TRANSFORMER_TAP_SETTINGS_HIST |  | High Tap Settings – Voltage at Lowest Tap Position & Low Tap Settings - Voltage at Lowest Tap Position.
MANU_VOLT_TAP_POS | RARF_HUB | TRANSFORMER_TAP_SETTINGS_HIST |  | Nominal Tap Position (Neutral Step).
NORMAL_POS | RARF_HUB | TRANSFORMER_TAP_SETTINGS_HIST |  | Normal Tap Position.
STEP_VOLT | RARF_HUB | TRANSFORMER_TAP_SETTINGS_HIST |  | Percentage of tap range for each step (ex.6.25%/step.).
SUBMISSION_TYPE | RARF_HUB | TRANSFORMER_TAP_SETTINGS_HIST |  | Submission Type: Internal or External.
TOTAL_NUM | RARF_HUB | TRANSFORMER_TAP_SETTINGS_HIST |  | Total Number of Tap Positions.
TRANSFORMER_CODE | RARF_HUB | TRANSFORMER_TAP_SETTINGS_HIST |  | Unique Code for each Transformer defined as the concatenation of SITE_CODE_SUBSTATION_CODE_TRANSFORMER_NAME.
CHANGE_DESCRIPTION | RARF_HUB | TRANSFORMER_TAP_SETTINGS_HIST |  | DESCRIPTION OF CHANGE | Added 06/27/2012
DATE_LOADED | RARF_HUB | TRANSFORMER_UNITS | Latest Approved Unit(s) associated with this transformer. | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format). |  | Latest Approved Unit(s) associated with this transformer.
DATE_SUBMITTED | RARF_HUB | TRANSFORMER_UNITS |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
TRANSFORMER_CODE | RARF_HUB | TRANSFORMER_UNITS |  | Unique Code for each Transformer defined as the concatenation of SITE_CODE_SUBSTATION_CODE_TRANSFORMER_NAME.
TRANSFORMER_UNIT_CODE | RARF_HUB | TRANSFORMER_UNITS |  | Unique Code for Each Unit associated to a Transformer
APPROVED_DATE | RARF_HUB | TRANSFORMER_UNITS_HIST | History Table: All approved/Disapproved Unit(s) associated with this transformer. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved/Disapproved Unit(s) associated with this transformer.
DATE_LOADED | RARF_HUB | TRANSFORMER_UNITS_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | TRANSFORMER_UNITS_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
SUBMISSION_TYPE | RARF_HUB | TRANSFORMER_UNITS_HIST |  | Submission Type: Internal or External.
TRANSFORMER_CODE | RARF_HUB | TRANSFORMER_UNITS_HIST |  | Unique Code for each Transformer defined as the concatenation of SITE_CODE_SUBSTATION_CODE_TRANSFORMER_NAME.
TRANSFORMER_UNIT_CODE | RARF_HUB | TRANSFORMER_UNITS_HIST |  | Unique Code for Each Unit associated to a Transformer
CONFIGCODE_FROM | RARF_HUB | TRANSITIONS | Latest Approved Combined Cycle Transitions Details. | Configuration FROM in Operational Configurations. |  | Latest Approved Combined Cycle Transitions Details.
CONFIGCODE_TO | RARF_HUB | TRANSITIONS |  | Configuration TO in Operational Configurations.
DATE_LOADED | RARF_HUB | TRANSITIONS |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | TRANSITIONS |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
ID | RARF_HUB | TRANSITIONS |  | Transition ID.
NOTES_TRANSITION | RARF_HUB | TRANSITIONS |  | General Notes.
SITE_CODE | RARF_HUB | TRANSITIONS |  | Unique Code for Resource Site.
TRAIN_CODE | RARF_HUB | TRANSITIONS |  | Unique Code for each Train in a Site, defined as the concatenation of SITE_CODE_TRAIN_NAME.
APPROVED_DATE | RARF_HUB | TRANSITIONS_HIST | History Table: All approved/Disapproved Combined Cycle Transitions Details. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved/Disapproved Combined Cycle Transitions Details.
CONFIGCODE_FROM | RARF_HUB | TRANSITIONS_HIST |  | Configuration FROM in Operational Configurations.
CONFIGCODE_TO | RARF_HUB | TRANSITIONS_HIST |  | Configuration TO in Operational Configurations.
DATE_LOADED | RARF_HUB | TRANSITIONS_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | TRANSITIONS_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
ID | RARF_HUB | TRANSITIONS_HIST |  | Transition ID.
NOTES_TRANSITION | RARF_HUB | TRANSITIONS_HIST |  | General Notes.
SITE_CODE | RARF_HUB | TRANSITIONS_HIST |  | Unique Code for Resource Site.
SUBMISSION_TYPE | RARF_HUB | TRANSITIONS_HIST |  | Submission Type: Internal or External.
TRAIN_CODE | RARF_HUB | TRANSITIONS_HIST |  | Unique Code for each Train in a Site, defined as the concatenation of SITE_CODE_TRAIN_NAME.
ARMATURE_Z_R_PU | RARF_HUB | WIND | Latest Approved WIND Generation Resources Unit Information. | Stator impedance value (R in P.U). |  | Latest Approved WIND Generation Resources Unit Information.
ARMATURE_Z_X_PU | RARF_HUB | WIND |  | Stator impedance value (X in P.U).
AVG_HGHT_ABV_GRND | RARF_HUB | WIND |  | Average Height above ground of Turbine Hub (meters).
BREAKER_INTERRUP | RARF_HUB | WIND |  | Breaker Interruption Time.
COLDSTART | RARF_HUB | WIND |  | Cold Start Time.
DATE_LOADED | RARF_HUB | WIND |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | WIND |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DIRECT_AXIS_SUBSTNT_REACTANCE | RARF_HUB | WIND |  | Direct Axis Sub transient reactance, X"di.
DIRECT_AXIS_TRANSNT_REACTANCE | RARF_HUB | WIND |  | Direct Axis Transient reactance, X'di.
DYNAMIC_REACTIVE_DVC_FLG | RARF_HUB | WIND |  | This column is not being used.
DYNAMIC_REACTIVE_DVCFORM_FLG | RARF_HUB | WIND |  | This column is not being used.
ELGBL_MCFRI_FLG | RARF_HUB | WIND |  | Eligible for McCamey Flowgate Rights (MCFRIs)? Y or N.
ERCOT_INTRCONN_PROJ_NUM | RARF_HUB | WIND |  | ERCOT Interconnection Project Number - only new units.
GRP1_TUR_MW_MDL_RTG | RARF_HUB | WIND |  | Group 1 Turbine Model Rating.
GRP1_TUR_NUM | RARF_HUB | WIND |  | Group 1 Turbine Number.
GRP1_TUR_TYPE | RARF_HUB | WIND |  | Group 1 Turbine Type.
GRP2_TUR_MW_MDL_RTG | RARF_HUB | WIND |  | Group 2 Turbine Model Rating.
GRP2_TUR_NUM | RARF_HUB | WIND |  | Group 2 Turbine Number.
GRP2_TUR_TYPE | RARF_HUB | WIND |  | Group 2 Turbine Type.
GRP3_TUR_MW_MDL_RTG | RARF_HUB | WIND |  | Group 3 Turbine Model Rating.
GRP3_TUR_NUM | RARF_HUB | WIND |  | Group 3 Turbine Number.
GRP3_TUR_TYPE | RARF_HUB | WIND |  | Group 3 Turbine Type.
GRP4_TUR_MW_MDL_RTG | RARF_HUB | WIND |  | Group 4 Turbine Model Rating.
GRP4_TUR_NUM | RARF_HUB | WIND |  | Group 4 Turbine Number.
GRP4_TUR_TYPE | RARF_HUB | WIND |  | Group 4 Turbine Type.
GRP5_TUR_MW_MDL_RTG | RARF_HUB | WIND |  | Group 5 Turbine Model Rating.
GRP5_TUR_NUM | RARF_HUB | WIND |  | Group 5 Turbine Number.
GRP5_TUR_TYPE | RARF_HUB | WIND |  | Group 5 Turbine Type.
HGHT_METG_TOW_INST | RARF_HUB | WIND |  | Height of Meteorological Instrumentation (Meters).
HOT_TO_INTMDT_TIME | RARF_HUB | WIND |  | Hot to Intermediate Time.
HOTSTART | RARF_HUB | WIND |  | The time, in hours, from the ERCOT notice to LSL, for a Resource in its hot-temperature state.
HR_LMT | RARF_HUB | WIND |  | High Reasonability Limit( MW).
HR_RAMPRATE_LMT | RARF_HUB | WIND |  | High Reasonability Ramp Rate Limit( MW).
INTERMSTART | RARF_HUB | WIND |  | Intermediate Start Time.
INTMDT_TO_COLD_TIME | RARF_HUB | WIND |  | Intermediate to Cold time.
KVBASE | RARF_HUB | WIND |  | What is the kV base that the following data is based on?.
LAT_CTR_WNDFARM | RARF_HUB | WIND |  | Latitude of center of Wind Farm ( Decimal Degrees).
LAT_METG_TOWER | RARF_HUB | WIND |  | Latitude of Meteorological Tower ( Decimal Degrees).
LONG_CTR_WNDFARM | RARF_HUB | WIND |  | Longitude of center of Wind Farm ( Decimal Degrees).
LONG_METG_TOWER | RARF_HUB | WIND |  | Longitude of Meteorological Tower (Decimal Degrees).
LR_LMT | RARF_HUB | WIND |  | Low Reasonability Limit.
LR_RAMP_RATE_LMT | RARF_HUB | WIND |  | Low Reasonability Ramp Rate Limit.
MACHINE_IMPEDANCE_R_PU | RARF_HUB | WIND |  | This column is not being used.
MACHINE_IMPEDANCE_X_PU | RARF_HUB | WIND |  | This column is not being used.
MAX_ONLINE_TIME | RARF_HUB | WIND |  | The maximum number of consecutive hours a Resource can run before it needs to be shut down
MAXDLYSTARTS | RARF_HUB | WIND |  | The maximum number of times a Resource can be started in a 24 hour period under normal operating conditions.
MAXWKLYENRGY | RARF_HUB | WIND |  | The maximum amount of energy, in MWh, a Resource can produce in seven consecutive days
MAXWKLYSTARTS | RARF_HUB | WIND |  | The maximum number of times a Resource can be started in seven consecutive days under normal operating conditions.
MIN_OFFLINE_TIME | RARF_HUB | WIND |  | Minimum Off Line Time.
MIN_ONLINE_TIME | RARF_HUB | WIND |  | Minimum On Line Time.
MODEL_SUBMITTED_FLG | RARF_HUB | WIND |  | This column is not being used.
MUTUAL_COUPLING_Z_R_PU | RARF_HUB | WIND |  | This column is not being used.
MUTUAL_COUPLING_Z_X_PU | RARF_HUB | WIND |  | This column is not being used.
MVABASE | RARF_HUB | WIND |  | What is the MVA base that the following data is based on?.
NAME_PLT_RTG | RARF_HUB | WIND |  | Name plate Rating.
NEGATIVE_SEQ_Z_R_PU | RARF_HUB | WIND |  | Negative Sequence Impedance (R in P.U).
NEGATIVE_SEQ_Z_X_PU | RARF_HUB | WIND |  | Negative Sequence Impedance (X in P.U).
NERC_NUM | RARF_HUB | WIND |  | NERC Number.
OFREQ_TRIP_HZ1 | RARF_HUB | WIND |  | Over frequency Protection Setting- HZ1.
OFREQ_TRIP_HZ2 | RARF_HUB | WIND |  | Over frequency Protection Setting- HZ2.
OFREQ_TRIP_HZ3 | RARF_HUB | WIND |  | Over frequency Protection Setting- HZ3.
OFREQ_TRIP_HZ4 | RARF_HUB | WIND |  | Over frequency Protection Setting- HZ4.
OFREQ_TRIP_INSTANT | RARF_HUB | WIND |  | Instantaneous Over frequency Trip.
OFREQ_TRIP_TIME1 | RARF_HUB | WIND |  | Over frequency Protection Setting- TIME1.
OFREQ_TRIP_TIME2 | RARF_HUB | WIND |  | Over frequency Protection Setting- TIME2.
OFREQ_TRIP_TIME3 | RARF_HUB | WIND |  | Over frequency Protection Setting- TIME3.
OFREQ_TRIP_TIME4 | RARF_HUB | WIND |  | Over frequency Protection Setting- TIME4.
OVOLT_TRIP_INSTANT | RARF_HUB | WIND |  | Instantaneous Overvoltage Trip.
OVOLT_TRIP_TIME1 | RARF_HUB | WIND |  | Overvoltage Trip Time setting 1.
OVOLT_TRIP_TIME2 | RARF_HUB | WIND |  | Overvoltage Trip Time setting 2.
OVOLT_TRIP_TIME3 | RARF_HUB | WIND |  | Overvoltage Trip Time setting 3.
OVOLT_TRIP_TIME4 | RARF_HUB | WIND |  | Overvoltage Trip Time setting 4.
OVOLT_TRIP_VOLT1 | RARF_HUB | WIND |  | Overvoltage Trip Voltage setting 1.
OVOLT_TRIP_VOLT2 | RARF_HUB | WIND |  | Overvoltage Trip Voltage setting 2.
OVOLT_TRIP_VOLT3 | RARF_HUB | WIND |  | Overvoltage Trip Voltage setting 3.
OVOLT_TRIP_VOLT4 | RARF_HUB | WIND |  | Overvoltage Trip Voltage setting 4.
PHYS_UNIT_TYPE | RARF_HUB | WIND |  | Physical Unit Type.
POSITIVE_SEQ_Z_R_PU | RARF_HUB | WIND |  | Positive Sequence (R in p.u).
POSITIVE_SEQ_Z_X_PU | RARF_HUB | WIND |  | Positive Sequence (Z in p.u).
PUC_NUM | RARF_HUB | WIND |  | PUCT Number.
QUAL_FACILITY_FLG | RARF_HUB | WIND |  | Qualifying Facility Flag.
RENEWABLE_FLG | RARF_HUB | WIND |  | Renewable Flag.
RENEWABLE_OFFSET | RARF_HUB | WIND |  | Renewable Offset Flag.
RES_CATG | RARF_HUB | WIND |  | Resource Category.
ROTOR_Z_R_PU | RARF_HUB | WIND |  | This column is not being used.
ROTOR_Z_X_PU | RARF_HUB | WIND |  | This column is not being used.
RTG_MVAR | RARF_HUB | WIND |  | Reactive Power Rating.
RTG_MW | RARF_HUB | WIND |  | Real Power Rating.
SEASON_NET_MAX_EMGY_RTG_FL | RARF_HUB | WIND |  | Seasonal Net Maximum Emergency Rating -Fall (MW).
SEASON_NET_MAX_EMGY_RTG_SM | RARF_HUB | WIND |  | Seasonal Net Maximum Emergency Rating -Summer (MW).
SEASON_NET_MAX_EMGY_RTG_SP | RARF_HUB | WIND |  | Seasonal Net Maximum Emergency Rating -Spring (MW).
SEASON_NET_MAX_EMGY_RTG_WT | RARF_HUB | WIND |  | Seasonal Net Maximum Emergency Rating -Winter (MW).
SEASON_NET_MAX_SUST_RTG_FL | RARF_HUB | WIND |  | Seasonal Net Maximum Sustainable Rating -Fall (MW).
SEASON_NET_MAX_SUST_RTG_SM | RARF_HUB | WIND |  | Seasonal Net Maximum Sustainable Rating -Summer (MW).
SEASON_NET_MAX_SUST_RTG_SP | RARF_HUB | WIND |  | Seasonal Net Maximum Sustainable Rating -Spring (MW).
SEASON_NET_MAX_SUST_RTG_WT | RARF_HUB | WIND |  | Seasonal Net Maximum Sustainable Rating -Winter (MW).
SEASON_NET_MIN_EMGY_RTG_FL | RARF_HUB | WIND |  | Seasonal Net Minimum Emergency Rating -Fall (MW).
SEASON_NET_MIN_EMGY_RTG_SM | RARF_HUB | WIND |  | Seasonal Net Minimum Emergency Rating -Summer (MW).
SEASON_NET_MIN_EMGY_RTG_SP | RARF_HUB | WIND |  | Seasonal Net Minimum Emergency Rating -Spring (MW).
SEASON_NET_MIN_EMGY_RTG_WT | RARF_HUB | WIND |  | Seasonal Net Minimum Emergency Rating -Winter (MW).
SEASON_NET_MIN_SUST_RTG_FL | RARF_HUB | WIND |  | Seasonal Net Minimum Sustainable Rating -Fall (MW).
SEASON_NET_MIN_SUST_RTG_SM | RARF_HUB | WIND |  | Seasonal Net Minimum Sustainable Rating - Summer (MW).
SEASON_NET_MIN_SUST_RTG_SP | RARF_HUB | WIND |  | Seasonal Net Minimum Sustainable Rating - Spring (MW).
SEASON_NET_MIN_SUST_RTG_WT | RARF_HUB | WIND |  | Seasonal Net Minimum Sustainable Rating - Winter (MW).
SITE_CODE | RARF_HUB | WIND |  | Unique Code for Resource Site.
TOTNUM_TURBINES | RARF_HUB | WIND |  | Total Number of Turbines.
UFREQ_TRIP_HZ1 | RARF_HUB | WIND |  | Under frequency Protection Setting- HZ1.
UFREQ_TRIP_HZ2 | RARF_HUB | WIND |  | Under frequency Protection Setting- HZ2.
UFREQ_TRIP_HZ3 | RARF_HUB | WIND |  | Under frequency Protection Setting- HZ3.
UFREQ_TRIP_HZ4 | RARF_HUB | WIND |  | Under frequency Protection Setting- HZ4.
UFREQ_TRIP_INSTANT | RARF_HUB | WIND |  | Instantaneous Under frequency Trip.
UFREQ_TRIP_TIME1 | RARF_HUB | WIND |  | Under frequency Protection Setting- TIME1.
UFREQ_TRIP_TIME2 | RARF_HUB | WIND |  | Under frequency Protection Setting- TIME2.
UFREQ_TRIP_TIME3 | RARF_HUB | WIND |  | Under frequency Protection Setting- TIME3.
UFREQ_TRIP_TIME4 | RARF_HUB | WIND |  | Under frequency Protection Setting- TIME4.
UNIT_CODE | RARF_HUB | WIND |  | Concatenated mnemonic of Resource Site Code and Unit name (e.g CBY_CBYG1) where CBY is Site_code and CBYG1 is Unit Name.
UNIT_END_DT | RARF_HUB | WIND |  | Unit Termination Date: MM/DD/YYYY format.
UNIT_KV | RARF_HUB | WIND |  | Unit Generating Voltage.
UNIT_NAME | RARF_HUB | WIND |  | Unit Name.
UNIT_START_DT | RARF_HUB | WIND |  | Unit Commercial Operations Date. It is the date on which Generator declares that the construction of the Plant has been substantially completed, Trial Operation of the Plant has been completed, and the Plant is ready for dispatch. Format is MM/DD/YYYY.
UVOLT_TRIP_INSTANT | RARF_HUB | WIND |  | Instantaneous Under voltage Trip.
UVOLT_TRIP_TIME1 | RARF_HUB | WIND |  | Under Voltage Protection Setting- TIME1.
UVOLT_TRIP_TIME2 | RARF_HUB | WIND |  | Under Voltage Protection Setting- TIME2.
UVOLT_TRIP_TIME3 | RARF_HUB | WIND |  | Under Voltage Protection Setting- TIME3.
UVOLT_TRIP_TIME4 | RARF_HUB | WIND |  | Under Voltage Protection Setting- TIME4.
UVOLT_TRIP_VOLT1 | RARF_HUB | WIND |  | Under Voltage Protection Setting- VOLT1.
UVOLT_TRIP_VOLT2 | RARF_HUB | WIND |  | Under Voltage Protection Setting- VOLT2.
UVOLT_TRIP_VOLT3 | RARF_HUB | WIND |  | Under Voltage Protection Setting- VOLT3.
UVOLT_TRIP_VOLT4 | RARF_HUB | WIND |  | Under Voltage Protection Setting- VOLT4.
ZERO_SEQ_Z_R_PU | RARF_HUB | WIND |  | Zero Sequence Impedance ( R in P.U).
ZERO_SEQ_Z_X_PU | RARF_HUB | WIND |  | Zero Sequence Impedance ( X in P.U).
AUX_LOAD_PWR_FACT | RARF_HUB | WIND |  | Auxiliary Load Power Factor | Added 06/27/2012
AUX_MVARTOTAL | RARF_HUB | WIND |  | Average Amount Of Auxiliary Reactive Power | Added 06/27/2012
AUX_MWTOTAL | RARF_HUB | WIND |  | Average Amount Of Auxiliary Real Power | Added 06/27/2012
BASE_MVA_TRANSFORMER_DATA | RARF_HUB | WIND |  | Base Mva For Transformer Data | Added 06/27/2012
DESIGN_MAX_AMB_TEMP | RARF_HUB | WIND |  | Design Max Ambient Temperature | Added 06/27/2012
DESIGN_MIN_AMB_TEMP | RARF_HUB | WIND |  | Design Min Ambient Temperature | Added 06/27/2012
DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED | RARF_HUB | WIND |  | Direct Axis Subtransient Reactance, X"dv (saturated) | Added 06/27/2012
DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED | RARF_HUB | WIND |  | Direct Axis Transient Reactance, X'dv (saturated) | Added 06/27/2012
DISCHARGE LIGHT_PER_TOT_MVAR_LOAD | RARF_HUB | WIND |  | Discharge Lighting, Percent Of Total MVAR Load | Added 06/27/2012
DISCHARGE LIGHT_PER_TOT_MW_LOAD | RARF_HUB | WIND |  | Discharge Lighting, Percent Of Total Mw Load | Added 06/27/2012
DOES_ZERO_SEQ_EXIST | RARF_HUB | WIND |  | Does Zero Sequence Z exist? | Added 06/27/2012
GOV_DEAD_BND | RARF_HUB | WIND |  | Governor Dead-Band | Added 06/27/2012
GOV_DROOP | RARF_HUB | WIND |  | Governor Droop Setting | Added 06/27/2012
HGT_MET_TWR_BAR_PRES | RARF_HUB | WIND |  | Height of Meteorological Instrumentation - Barometric Pressure | Added 06/27/2012
HGT_MET_TWR_TEMP | RARF_HUB | WIND |  | Height of Meteorological Instrumentation - Temperature | Added 06/27/2012
HGT_MET_TWR_WND_DIRT | RARF_HUB | WIND |  | Height of Meteorological Instrumentation - Wind Direction | Added 06/27/2012
HGT_MET_TWR_WND_SPD | RARF_HUB | WIND |  | Height of Meteorological Instrumentation - Wind Speed | Added 06/27/2012
HIGH_SIDE_VT_CONNT | RARF_HUB | WIND |  | High Side Voltage Connection | Added 06/27/2012
IMPEDANCE_Z | RARF_HUB | WIND |  | Impedance Z | Added 06/27/2012
LOW_SIDE_VT_CONNT | RARF_HUB | WIND |  | Low Side Voltage Connection | Added 06/27/2012
LOW_SIDE_VT_LEVL | RARF_HUB | WIND |  | Low Side Voltage Level (nominal) | Added 06/27/2012
LRG_MTR_PER_TOT_MVAR_LOAD | RARF_HUB | WIND |  | Large Motor, Percent Of Total MVAR Load | Added 06/27/2012
LRG_MTR_PER_TOT_MW_LOAD | RARF_HUB | WIND |  | Large Motor, Percent Of Total Mw Load | Added 06/27/2012
NEGATIVE_SEQ_Z_R_PU | RARF_HUB | WIND |  | Negative Sequence Z (saturated) | Added 06/27/2012
NEGATIVE_SEQ_Z_X_PU | RARF_HUB | WIND |  | Negative Sequence Z (saturated) | Added 06/27/2012
NON_MOD_GEN | RARF_HUB | WIND |  | Non_Modeled Generator | Added 06/27/2012
OTH_PER_TOT_MVAR_LOAD | RARF_HUB | WIND |  | Other, Percent Of Total MVAR Load | Added 06/27/2012
OTH_PER_TOT_MW_LOAD | RARF_HUB | WIND |  | Other, Percent Of Total Mw Load | Added 06/27/2012
POSITIVE_SEQ_Z_R_PU | RARF_HUB | WIND |  | Positive Sequence Z (saturated) | Added 06/27/2012
POSITIVE_SEQ_Z_X_PU | RARF_HUB | WIND |  | Positive Sequence Z (saturated) | Added 06/27/2012
PTI_BUS_NUM | RARF_HUB | WIND |  | PTI Bus Number | Added 06/27/2012
RESISTIVE_LOAD_PER_TOT_MW_LOAD | RARF_HUB | WIND |  | Resistive (heating) Load, Percent Of Total Mw Load | Added 06/27/2012
SGIA_SIG_DT | RARF_HUB | WIND |  | Standard Generation Interconnection Agreement (SGIA) Signature Date | Added 06/27/2012
SML_MTR_PER_TOT_MVAR_LOAD | RARF_HUB | WIND |  | Small Motor, Percent Of Total MVAR Load | Added 06/27/2012
SML_MTR_PER_TOT_MW_LOAD | RARF_HUB | WIND |  | Small Motor, Percent Of Total Mw Load | Added 06/27/2012
SUBSTAT_CODE_SUB_MNEMONIC | RARF_HUB | WIND |  | SubStation Code/SubStation Mnemonic | Added 06/27/2012
TRANS_ONLY_DT | RARF_HUB | WIND |  | Transmission Only Date (POI) | Added 06/27/2012
UNIT_MRD_ST_DT | RARF_HUB | WIND |  | Unit Start Date (Model Ready Date) | Added 06/27/2012
VOL_LEV | RARF_HUB | WIND |  | Voltage Level | Added 06/27/2012
X_R_RATIO | RARF_HUB | WIND |  | X/R Ratio | Added 06/27/2012
ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU | RARF_HUB | WIND |  | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Added 06/27/2012
ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU | RARF_HUB | WIND |  | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Added 06/27/2012
ZERO_SEQ_X_R_RATIO | RARF_HUB | WIND |  | Zero Sequence X/R Ratio | Added 06/27/2012
ZERO_SEQ_Z | RARF_HUB | WIND |  | Zero Sequence Z | Added 06/27/2012
ZERO_SEQ_Z_R_PU | RARF_HUB | WIND |  | Zero Sequence Z (saturated) | Added 06/27/2012
ZERO_SEQ_Z_X_PU | RARF_HUB | WIND |  | Zero Sequence Z (saturated) | Added 06/27/2012
APPROVED_DATE | RARF_HUB | WIND_HIST | History Table: All approved/Disapproved WIND Generation Resources. | Date & time when the RARF is approved. NULL indicates Disapproved RARF. Format: (MM/DD/YYYY). |  | History Table: All approved/Disapproved WIND Generation Resources.
ARMATURE_Z_R_PU | RARF_HUB | WIND_HIST |  | Stator impedance value (R in P.U).
ARMATURE_Z_X_PU | RARF_HUB | WIND_HIST |  | Stator impedance value (X in P.U).
AVG_HGHT_ABV_GRND | RARF_HUB | WIND_HIST |  | Average Height above ground of Turbine Hub (meters).
BREAKER_INTERRUP | RARF_HUB | WIND_HIST |  | Breaker Interruption Time.
COLDSTART | RARF_HUB | WIND_HIST |  | Cold Start Time.
DATE_LOADED | RARF_HUB | WIND_HIST |  | Date when the RARF is loaded into the Database. (MM/DD/YYYY Format).
DATE_SUBMITTED | RARF_HUB | WIND_HIST |  | Date when the RARF is submitted to ERCOT for processing. (MM/DD/YYYY Format).
DIRECT_AXIS_SUBSTNT_REACTANCE | RARF_HUB | WIND_HIST |  | Direct Axis Sub transient reactance, X"di.
DIRECT_AXIS_TRANSNT_REACTANCE | RARF_HUB | WIND_HIST |  | Direct Axis Transient reactance, X'di.
DYNAMIC_REACTIVE_DVC_FLG | RARF_HUB | WIND_HIST |  | This column is not being used.
DYNAMIC_REACTIVE_DVCFORM_FLG | RARF_HUB | WIND_HIST |  | This column is not being used.
ELGBL_MCFRI_FLG | RARF_HUB | WIND_HIST |  | Eligible for McCamey Flowgate Rights (MCFRIs)? Y or N.
ERCOT_INTRCONN_PROJ_NUM | RARF_HUB | WIND_HIST |  | ERCOT Interconnection Project Number - only new units.
GRP1_TUR_MW_MDL_RTG | RARF_HUB | WIND_HIST |  | Group 1 Turbine Model Rating.
GRP1_TUR_NUM | RARF_HUB | WIND_HIST |  | Group 1 Turbine Number.
GRP1_TUR_TYPE | RARF_HUB | WIND_HIST |  | Group 1 Turbine Type.
GRP2_TUR_MW_MDL_RTG | RARF_HUB | WIND_HIST |  | Group 2 Turbine Model Rating.
GRP2_TUR_NUM | RARF_HUB | WIND_HIST |  | Group 2 Turbine Number.
GRP2_TUR_TYPE | RARF_HUB | WIND_HIST |  | Group 2 Turbine Type.
GRP3_TUR_MW_MDL_RTG | RARF_HUB | WIND_HIST |  | Group 3 Turbine Model Rating.
GRP3_TUR_NUM | RARF_HUB | WIND_HIST |  | Group 3 Turbine Number.
GRP3_TUR_TYPE | RARF_HUB | WIND_HIST |  | Group 3 Turbine Type.
GRP4_TUR_MW_MDL_RTG | RARF_HUB | WIND_HIST |  | Group 4 Turbine Model Rating.
GRP4_TUR_NUM | RARF_HUB | WIND_HIST |  | Group 4 Turbine Number.
GRP4_TUR_TYPE | RARF_HUB | WIND_HIST |  | Group 4 Turbine Type.
GRP5_TUR_MW_MDL_RTG | RARF_HUB | WIND_HIST |  | Group 5 Turbine Model Rating.
GRP5_TUR_NUM | RARF_HUB | WIND_HIST |  | Group 5 Turbine Number.
GRP5_TUR_TYPE | RARF_HUB | WIND_HIST |  | Group 5 Turbine Type.
HGHT_METG_TOW_INST | RARF_HUB | WIND_HIST |  | Height of Meteorological Instrumentation (Meters).
HOT_TO_INTMDT_TIME | RARF_HUB | WIND_HIST |  | Hot to Intermediate Time.
HOTSTART | RARF_HUB | WIND_HIST |  | The time, in hours, from the ERCOT notice to LSL, for a Resource in its hot-temperature state.
HR_LMT | RARF_HUB | WIND_HIST |  | High Reasonability Limit( MW).
HR_RAMPRATE_LMT | RARF_HUB | WIND_HIST |  | High Reasonability Ramp Rate Limit( MW).
INTERMSTART | RARF_HUB | WIND_HIST |  | Intermediate Start Time.
INTMDT_TO_COLD_TIME | RARF_HUB | WIND_HIST |  | Intermediate to Cold time.
KVBASE | RARF_HUB | WIND_HIST |  | What is the kV base that the following data is based on?.
LAT_CTR_WNDFARM | RARF_HUB | WIND_HIST |  | Latitude of center of Wind Farm ( Decimal Degrees).
LAT_METG_TOWER | RARF_HUB | WIND_HIST |  | Latitude of Meteorological Tower ( Decimal Degrees).
LONG_CTR_WNDFARM | RARF_HUB | WIND_HIST |  | Longitude of center of Wind Farm ( Decimal Degrees).
LONG_METG_TOWER | RARF_HUB | WIND_HIST |  | Longitude of Meteorological Tower (Decimal Degrees).
LR_LMT | RARF_HUB | WIND_HIST |  | Low Reasonability Limit.
LR_RAMP_RATE_LMT | RARF_HUB | WIND_HIST |  | Low Reasonability Ramp Rate Limit.
MACHINE_IMPEDANCE_R_PU | RARF_HUB | WIND_HIST |  | This column is not being used.
MACHINE_IMPEDANCE_X_PU | RARF_HUB | WIND_HIST |  | This column is not being used.
MAX_ONLINE_TIME | RARF_HUB | WIND_HIST |  | The maximum number of consecutive hours a Resource can run before it needs to be shut down
MAXDLYSTARTS | RARF_HUB | WIND_HIST |  | The maximum number of times a Resource can be started in a 24 hour period under normal operating conditions.
MAXWKLYENRGY | RARF_HUB | WIND_HIST |  | The maximum amount of energy, in MWh, a Resource can produce in seven consecutive days
MAXWKLYSTARTS | RARF_HUB | WIND_HIST |  | The maximum number of times a Resource can be started in seven consecutive days under normal operating conditions.
MIN_OFFLINE_TIME | RARF_HUB | WIND_HIST |  | Minimum Off Line Time.
MIN_ONLINE_TIME | RARF_HUB | WIND_HIST |  | Minimum On Line Time.
MODEL_SUBMITTED_FLG | RARF_HUB | WIND_HIST |  | This column is not being used.
MUTUAL_COUPLING_Z_R_PU | RARF_HUB | WIND_HIST |  | This column is not being used.
MUTUAL_COUPLING_Z_X_PU | RARF_HUB | WIND_HIST |  | This column is not being used.
MVABASE | RARF_HUB | WIND_HIST |  | What is the MVA base that the following data is based on?.
NAME_PLT_RTG | RARF_HUB | WIND_HIST |  | Name plate Rating.
NEGATIVE_SEQ_Z_R_PU | RARF_HUB | WIND_HIST |  | Negative Sequence Impedance (R in P.U).
NEGATIVE_SEQ_Z_X_PU | RARF_HUB | WIND_HIST |  | Negative Sequence Impedance (X in P.U).
NERC_NUM | RARF_HUB | WIND_HIST |  | NERC Number.
OFREQ_TRIP_HZ1 | RARF_HUB | WIND_HIST |  | Over frequency Protection Setting- HZ1.
OFREQ_TRIP_HZ2 | RARF_HUB | WIND_HIST |  | Over frequency Protection Setting- HZ2.
OFREQ_TRIP_HZ3 | RARF_HUB | WIND_HIST |  | Over frequency Protection Setting- HZ3.
OFREQ_TRIP_HZ4 | RARF_HUB | WIND_HIST |  | Over frequency Protection Setting- HZ4.
OFREQ_TRIP_INSTANT | RARF_HUB | WIND_HIST |  | Instantaneous Over frequency Trip.
OFREQ_TRIP_TIME1 | RARF_HUB | WIND_HIST |  | Over frequency Protection Setting- TIME1.
OFREQ_TRIP_TIME2 | RARF_HUB | WIND_HIST |  | Over frequency Protection Setting- TIME2.
OFREQ_TRIP_TIME3 | RARF_HUB | WIND_HIST |  | Over frequency Protection Setting- TIME3.
OFREQ_TRIP_TIME4 | RARF_HUB | WIND_HIST |  | Over frequency Protection Setting- TIME4.
OVOLT_TRIP_INSTANT | RARF_HUB | WIND_HIST |  | Instantaneous Overvoltage Trip.
OVOLT_TRIP_TIME1 | RARF_HUB | WIND_HIST |  | Overvoltage Trip Time setting 1.
OVOLT_TRIP_TIME2 | RARF_HUB | WIND_HIST |  | Overvoltage Trip Time setting 2.
OVOLT_TRIP_TIME3 | RARF_HUB | WIND_HIST |  | Overvoltage Trip Time setting 3.
OVOLT_TRIP_TIME4 | RARF_HUB | WIND_HIST |  | Overvoltage Trip Time setting 4.
OVOLT_TRIP_VOLT1 | RARF_HUB | WIND_HIST |  | Overvoltage Trip Voltage setting 1.
OVOLT_TRIP_VOLT2 | RARF_HUB | WIND_HIST |  | Overvoltage Trip Voltage setting 2.
OVOLT_TRIP_VOLT3 | RARF_HUB | WIND_HIST |  | Overvoltage Trip Voltage setting 3.
OVOLT_TRIP_VOLT4 | RARF_HUB | WIND_HIST |  | Overvoltage Trip Voltage setting 4.
PHYS_UNIT_TYPE | RARF_HUB | WIND_HIST |  | Physical Unit Type.
POSITIVE_SEQ_Z_R_PU | RARF_HUB | WIND_HIST |  | Positive Sequence Impedance (R in P.U).
POSITIVE_SEQ_Z_X_PU | RARF_HUB | WIND_HIST |  | Positive Sequence Impedance (X in P.U).
PUC_NUM | RARF_HUB | WIND_HIST |  | PUC NUMBER.
QUAL_FACILITY_FLG | RARF_HUB | WIND_HIST |  | Qualifying Facility Flag: Y or N.
RENEWABLE_FLG | RARF_HUB | WIND_HIST |  | Renewable Flag: Y or N.
RENEWABLE_OFFSET | RARF_HUB | WIND_HIST |  | Renewable Offset Flag.
RES_CATG | RARF_HUB | WIND_HIST |  | Resource Category.
ROTOR_Z_R_PU | RARF_HUB | WIND_HIST |  | This column is not being used.
ROTOR_Z_X_PU | RARF_HUB | WIND_HIST |  | This column is not being used.
RTG_MVAR | RARF_HUB | WIND_HIST |  | Reactive Power Rating.
RTG_MW | RARF_HUB | WIND_HIST |  | Real Power Rating.
SEASON_NET_MAX_EMGY_RTG_FL | RARF_HUB | WIND_HIST |  | Seasonal Net Maximum Emergency Rating -Fall (MW).
SEASON_NET_MAX_EMGY_RTG_SM | RARF_HUB | WIND_HIST |  | Seasonal Net Maximum Emergency Rating -Summer (MW).
SEASON_NET_MAX_EMGY_RTG_SP | RARF_HUB | WIND_HIST |  | Seasonal Net Maximum Emergency Rating -Spring (MW).
SEASON_NET_MAX_EMGY_RTG_WT | RARF_HUB | WIND_HIST |  | Seasonal Net Maximum Emergency Rating -Winter (MW).
SEASON_NET_MAX_SUST_RTG_FL | RARF_HUB | WIND_HIST |  | Seasonal Net Maximum Sustainable Rating -Fall (MW).
SEASON_NET_MAX_SUST_RTG_SM | RARF_HUB | WIND_HIST |  | Seasonal Net Maximum Sustainable Rating -Summer (MW).
SEASON_NET_MAX_SUST_RTG_SP | RARF_HUB | WIND_HIST |  | Seasonal Net Maximum Sustainable Rating -Spring (MW).
SEASON_NET_MAX_SUST_RTG_WT | RARF_HUB | WIND_HIST |  | Seasonal Net Maximum Sustainable Rating -Winter (MW).
SEASON_NET_MIN_EMGY_RTG_FL | RARF_HUB | WIND_HIST |  | Seasonal Net Minimum Emergency Rating -Fall (MW).
SEASON_NET_MIN_EMGY_RTG_SM | RARF_HUB | WIND_HIST |  | Seasonal Net Minimum Emergency Rating -Summer (MW).
SEASON_NET_MIN_EMGY_RTG_SP | RARF_HUB | WIND_HIST |  | Seasonal Net Minimum Emergency Rating -Spring (MW).
SEASON_NET_MIN_EMGY_RTG_WT | RARF_HUB | WIND_HIST |  | Seasonal Net Minimum Emergency Rating -Winter (MW).
SEASON_NET_MIN_SUST_RTG_FL | RARF_HUB | WIND_HIST |  | Seasonal Net Minimum Sustainable Rating -Fall (MW).
SEASON_NET_MIN_SUST_RTG_SM | RARF_HUB | WIND_HIST |  | Seasonal Net Minimum Sustainable Rating - Summer (MW).
SEASON_NET_MIN_SUST_RTG_SP | RARF_HUB | WIND_HIST |  | Seasonal Net Minimum Sustainable Rating - Spring (MW).
SEASON_NET_MIN_SUST_RTG_WT | RARF_HUB | WIND_HIST |  | Seasonal Net Minimum Sustainable Rating - Winter (MW).
SITE_CODE | RARF_HUB | WIND_HIST |  | Unique Code for Resource Site.
SUBMISSION_TYPE | RARF_HUB | WIND_HIST |  | Submission Type: Internal or External.
TOTNUM_TURBINES | RARF_HUB | WIND_HIST |  | Total Number of Turbines.
UFREQ_TRIP_HZ1 | RARF_HUB | WIND_HIST |  | Under frequency Protection Setting- HZ1.
UFREQ_TRIP_HZ2 | RARF_HUB | WIND_HIST |  | Under frequency Protection Setting- HZ2.
UFREQ_TRIP_HZ3 | RARF_HUB | WIND_HIST |  | Under frequency Protection Setting- HZ3.
UFREQ_TRIP_HZ4 | RARF_HUB | WIND_HIST |  | Under frequency Protection Setting- HZ4.
UFREQ_TRIP_INSTANT | RARF_HUB | WIND_HIST |  | Instantaneous Under frequency Trip.
UFREQ_TRIP_TIME1 | RARF_HUB | WIND_HIST |  | Under frequency Protection Setting- TIME1.
UFREQ_TRIP_TIME2 | RARF_HUB | WIND_HIST |  | Under frequency Protection Setting- TIME2.
UFREQ_TRIP_TIME3 | RARF_HUB | WIND_HIST |  | Under frequency Protection Setting- TIME3.
UFREQ_TRIP_TIME4 | RARF_HUB | WIND_HIST |  | Under frequency Protection Setting- TIME4.
UNIT_CODE | RARF_HUB | WIND_HIST |  | Concatenated mnemonic of Resource Site Code and Unit name (e.g CBY_CBYG1) where CBY is Site_code and CBYG1 is Unit Name.
UNIT_END_DT | RARF_HUB | WIND_HIST |  | Unit Termination Date: MM/DD/YYYY format.
UNIT_KV | RARF_HUB | WIND_HIST |  | Unit Generating Voltage.
UNIT_NAME | RARF_HUB | WIND_HIST |  | Unit Name.
UNIT_START_DT | RARF_HUB | WIND_HIST |  | Unit Commercial Operations Date. It is the date on which Generator declares that the construction of the Plant has been substantially completed, Trial Operation of the Plant has been completed, and the Plant is ready for dispatch. Format is MM/DD/YYYY.
UVOLT_TRIP_INSTANT | RARF_HUB | WIND_HIST |  | Instantaneous Under voltage Trip.
UVOLT_TRIP_TIME1 | RARF_HUB | WIND_HIST |  | Under Voltage Protection Setting- TIME1.
UVOLT_TRIP_TIME2 | RARF_HUB | WIND_HIST |  | Under Voltage Protection Setting- TIME2.
UVOLT_TRIP_TIME3 | RARF_HUB | WIND_HIST |  | Under Voltage Protection Setting- TIME3.
UVOLT_TRIP_TIME4 | RARF_HUB | WIND_HIST |  | Under Voltage Protection Setting- TIME4.
UVOLT_TRIP_VOLT1 | RARF_HUB | WIND_HIST |  | Under Voltage Protection Setting- VOLT1.
UVOLT_TRIP_VOLT2 | RARF_HUB | WIND_HIST |  | Under Voltage Protection Setting- VOLT2.
UVOLT_TRIP_VOLT3 | RARF_HUB | WIND_HIST |  | Under Voltage Protection Setting- VOLT3.
UVOLT_TRIP_VOLT4 | RARF_HUB | WIND_HIST |  | Under Voltage Protection Setting- VOLT4.
ZERO_SEQ_Z_R_PU | RARF_HUB | WIND_HIST |  | Zero Sequence Impedance ( R in P.U).
ZERO_SEQ_Z_X_PU | RARF_HUB | WIND_HIST |  | Zero Sequence Impedance ( X in P.U).
AUX_LOAD_PWR_FACT | RARF_HUB | WIND_HIST |  | Auxiliary Load Power Factor | Added 06/27/2012
AUX_MVARTOTAL | RARF_HUB | WIND_HIST |  | Average Amount Of Auxiliary Reactive Power | Added 06/27/2012
AUX_MWTOTAL | RARF_HUB | WIND_HIST |  | Average Amount Of Auxiliary Real Power | Added 06/27/2012
BASE_MVA_TRANSFORMER_DATA | RARF_HUB | WIND_HIST |  | Base Mva For Transformer Data | Added 06/27/2012
DESIGN_MAX_AMB_TEMP | RARF_HUB | WIND_HIST |  | Design Max Ambient Temperature | Added 06/27/2012
DESIGN_MIN_AMB_TEMP | RARF_HUB | WIND_HIST |  | Design Min Ambient Temperature | Added 06/27/2012
DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED | RARF_HUB | WIND_HIST |  | Direct Axis Subtransient Reactance, X"dv (saturated) | Added 06/27/2012
DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED | RARF_HUB | WIND_HIST |  | Direct Axis Transient Reactance, X'dv (saturated) | Added 06/27/2012
DISCHARGE LIGHT_PER_TOT_MVAR_LOAD | RARF_HUB | WIND_HIST |  | Discharge Lighting, Percent Of Total MVAR Load | Added 06/27/2012
DISCHARGE LIGHT_PER_TOT_MW_LOAD | RARF_HUB | WIND_HIST |  | Discharge Lighting, Percent Of Total Mw Load | Added 06/27/2012
DOES_ZERO_SEQ_EXIST | RARF_HUB | WIND_HIST |  | Does Zero Sequence Z exist? | Added 06/27/2012
GOV_DEAD_BND | RARF_HUB | WIND_HIST |  | Governor Dead-Band | Added 06/27/2012
GOV_DROOP | RARF_HUB | WIND_HIST |  | Governor Droop Setting | Added 06/27/2012
HGT_MET_TWR_BAR_PRES | RARF_HUB | WIND_HIST |  | Height of Meteorological Instrumentation - Barometric Pressure | Added 06/27/2012
HGT_MET_TWR_TEMP | RARF_HUB | WIND_HIST |  | Height of Meteorological Instrumentation - Temperature | Added 06/27/2012
HGT_MET_TWR_WND_DIRT | RARF_HUB | WIND_HIST |  | Height of Meteorological Instrumentation - Wind Direction | Added 06/27/2012
HGT_MET_TWR_WND_SPD | RARF_HUB | WIND_HIST |  | Height of Meteorological Instrumentation - Wind Speed | Added 06/27/2012
HIGH_SIDE_VT_CONNT | RARF_HUB | WIND_HIST |  | High Side Voltage Connection | Added 06/27/2012
IMPEDANCE_Z | RARF_HUB | WIND_HIST |  | Impedance Z | Added 06/27/2012
LOW_SIDE_VT_CONNT | RARF_HUB | WIND_HIST |  | Low Side Voltage Connection | Added 06/27/2012
LOW_SIDE_VT_LEVL | RARF_HUB | WIND_HIST |  | Low Side Voltage Level (nominal) | Added 06/27/2012
LRG_MTR_PER_TOT_MVAR_LOAD | RARF_HUB | WIND_HIST |  | Large Motor, Percent Of Total MVAR Load | Added 06/27/2012
LRG_MTR_PER_TOT_MW_LOAD | RARF_HUB | WIND_HIST |  | Large Motor, Percent Of Total Mw Load | Added 06/27/2012
NEGATIVE_SEQ_Z_R_PU | RARF_HUB | WIND_HIST |  | Negative Sequence Z (saturated) | Added 06/27/2012
NEGATIVE_SEQ_Z_X_PU | RARF_HUB | WIND_HIST |  | Negative Sequence Z (saturated) | Added 06/27/2012
NON_MOD_GEN | RARF_HUB | WIND_HIST |  | Non_Modeled Generator | Added 06/27/2012
OTH_PER_TOT_MVAR_LOAD | RARF_HUB | WIND_HIST |  | Other, Percent Of Total MVAR Load | Added 06/27/2012
OTH_PER_TOT_MW_LOAD | RARF_HUB | WIND_HIST |  | Other, Percent Of Total Mw Load | Added 06/27/2012
POSITIVE_SEQ_Z_R_PU | RARF_HUB | WIND_HIST |  | Positive Sequence Z (saturated) | Added 06/27/2012
POSITIVE_SEQ_Z_X_PU | RARF_HUB | WIND_HIST |  | Positive Sequence Z (saturated) | Added 06/27/2012
PTI_BUS_NUM | RARF_HUB | WIND_HIST |  | PTI Bus Number | Added 06/27/2012
RESISTIVE_LOAD_PER_TOT_MW_LOAD | RARF_HUB | WIND_HIST |  | Resistive (heating) Load, Percent Of Total Mw Load | Added 06/27/2012
SGIA_SIG_DT | RARF_HUB | WIND_HIST |  | Standard Generation Interconnection Agreement (SGIA) Signature Date | Added 06/27/2012
SML_MTR_PER_TOT_MVAR_LOAD | RARF_HUB | WIND_HIST |  | Small Motor, Percent Of Total MVAR Load | Added 06/27/2012
SML_MTR_PER_TOT_MW_LOAD | RARF_HUB | WIND_HIST |  | Small Motor, Percent Of Total Mw Load | Added 06/27/2012
SUBSTAT_CODE_SUB_MNEMONIC | RARF_HUB | WIND_HIST |  | SubStation Code/SubStation Mnemonic | Added 06/27/2012
TRANS_ONLY_DT | RARF_HUB | WIND_HIST |  | Transmission Only Date (POI) | Added 06/27/2012
UNIT_MRD_ST_DT | RARF_HUB | WIND_HIST |  | Unit Start Date (Model Ready Date) | Added 06/27/2012
VOL_LEV | RARF_HUB | WIND_HIST |  | Voltage Level | Added 06/27/2012
X_R_RATIO | RARF_HUB | WIND_HIST |  | X/R Ratio | Added 06/27/2012
ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU | RARF_HUB | WIND_HIST |  | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Added 06/27/2012
ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU | RARF_HUB | WIND_HIST |  | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Added 06/27/2012
ZERO_SEQ_X_R_RATIO | RARF_HUB | WIND_HIST |  | Zero Sequence X/R Ratio | Added 06/27/2012
ZERO_SEQ_Z | RARF_HUB | WIND_HIST |  | Zero Sequence Z | Added 06/27/2012
ZERO_SEQ_Z_R_PU | RARF_HUB | WIND_HIST |  | Zero Sequence Z (saturated) | Added 06/27/2012
ZERO_SEQ_Z_X_PU | RARF_HUB | WIND_HIST |  | Zero Sequence Z (saturated) | Added 06/27/2012
Note on E751: Concatenated mnemonic of Resource Site Code and Unit name from http://www.ercot.com/gridinfo/generation/Resource_Site_Name_to_Mnemonic_Dictionary.xls
Note on E941: Concatenated mnemonic of Resource Site Code and Unit name from http://www.ercot.com/gridinfo/generation/Resource_Site_Name_to_Mnemonic_Dictionary.xls

## Sheet2 (hidden)
RARF FORM TYPE | RARF DATA FIELD | Verify Rule | LAAR VALIDATIONS ITEST | Validation and Reports ITEST GEN - 01/30/2012 | Validation ITEST CC - 01/30/2012 | ITEST Transmission | Change Description | RARF Tab | Label | TABLE | DB Field | EXCEL | Business Rules/Basic UI validations | Field/ Tab Type | Data type | Validation Type | Source | Destination Application
Generation | Non Modeled Generation | [5 empty] | ADD 04/2012 | Unit Info - GEN | Y/N | GENERATION | NON_MOD_GEN | 1.Select from the list: Y or N 2.Not Null | Select from the list: Y or N | R | Dropdown List | B,DVB
Generation | Transmission Only Date (POI) | [5 empty] | ADD 04/2012 | Unit Info - GEN | mm/dd/yyyy | GENERATION | TRANS_ONLY_DT | 1. Optional. 2. Format should be: MM/DD/YYYY | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB
Generation | Standard Generation Interconnection Agreement (SGIA) Signature Date | [5 empty] | ADD 04/2012 | Unit Info - GEN | mm/dd/yyyy | GENERATION | SGIA_SIGA_DT | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date. | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date. | R | Date | B/DVB | CDannunzio
Generation | Unit Start Date (Model Ready Date) | [5 empty] | ADD 04/2012 | Unit Info - GEN | mm/dd/yyyy | GENERATION | UNIT_MRD_ST_DT | 1.This field is not null. Format should be: MM/DD/YYYY 2.Date should be Vaild Data Base Load Date 3.Unit Start Date should be >= Site Start Date ( Site-Information Tab) | This field is not null. Format should be: MM/DD/YYYY Unit Start Date should be >= Site Start Date ( Site-Information Tab)
Generation | Substation Code/substation Mnemonic | [5 empty] | ADD 04/2012 | Unit Info - GEN | All Caps | GENERATION | SUBSTAT_CODE_SUB_MNEMONIC | SUBSTAT_CODE_SUB_MNEMONIC | 1) This field is not null (required). Data type must be Character. 2) Must match ERCOT records (unless new). Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" . 4) Must be <= 8 characters. Warning! Substation Code should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) Substation code should be in Upper case letters. Generate an error if the rule fails. | R | Character | B/DVB | CDannunzio
Generation | Voltage Level | [5 empty] | ADD 04/2012 | Unit Info - GEN | kV | GENERATION | VOL_LEV | VOL_LEV | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0. | R | Float | B/DVE | CDannunzio
Generation | Pti Bus Number | [5 empty] | ADD 04/2012 | Unit Info - GEN | # | GENERATION | PTI_BUS_NUM | PTI_BUS_NUM | 1) This field isnot null (required). Data type must be Integer. 2) The value must be > 0. | R | Integer | B/DVB | CDannunzio
Generation | Primary Fuel Type |  |  | Passed Validation |  |  | UPDATE 02/2012 | Unit Info - GEN | List | GENERATION | PRIM_FUELTYPE | Select from the list: AB, BFG, BIT, BL, DFO, GEO, JF, KER, LFG, LIG, MSW, NA, NG, NUC, OBG, OBL, OBS, OG, OO, OTH, PC, PG, RFO, SLW, STM, SUB, SUN, T, TDF, WAT, WDL, WDS, WH, WOC This field is not null. | Select from the list: AB, BFG, BIT, BL, DFO, GEO, JF, KER, LFG, LIG, MSW, NA, NG, NUC, OBG, OBL, OBS, OG, OO, OTH, PC, PG, RFO, SLW, STM, SUB, SUN, T, TDF, WAT, WDL, WDS, WH, WOC This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS
Generation | Secondary Fuel Type |  |  | Passed Validation |  |  | UPDATE 02/2012 | Unit Info - GEN | List | GENERATION | SEC_FUELTYPE | Select from the list: AB, BFG, BIT, BL, DFO, GEO, JF, KER, LFG, LIG, MSW, NA, NG, NUC, OBG, OBL, OBS, OG, OO, OTH, PC, PG, RFO, SLW, STM, SUB, SUN, T, TDF, WAT, WDL, WDS, WH, WOC. This field is not null. | Select from the list: AB, BFG, BIT, BL, DFO, GEO, JF, KER, LFG, LIG, MSW, NA, NG, NUC, OBG, OBL, OBS, OG, OO, OTH, PC, PG, RFO, SLW, STM, SUB, SUN, T, TDF, WAT, WDL, WDS, WH, WOC. This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS
Generation | Resource Category |  |  | Passed Validation |  |  | UPDATE 02/2012 | Unit Info - GEN | List | GENERATION | RES_CATG | 1)Resource Category is not null. 2)Select from the list: Nuclear,Hydro,Coal and Lignite, Gas Steam- Super Critical Boiler, Gas Steam- Reheat Boiler, Gas Steam - Non Reheat or Boiler without air preheated, Simple Cycle <= 90 MW, Simple Cycle > 90 MW, Reciprocating Engine, Solar, Energy Storage, Other | 1)Resource Category is not null. 2)Select from the list: Nuclear,Hydro,Coal and Lignite, Gas Steam- Super Critical Boiler, Gas Steam- Reheat Boiler, Gas Steam - Non Reheat or Boiler without air preheated, Simple Cycle <= 90 MW, Simple Cycle > 90 MW, Reciprocating Engine, Solar, Energy Storage, Other | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/kittiepong
Generation | Physical Unit Type |  |  | Passed Validation |  |  | UPDATE 02/2012 | Unit Info - GEN | List | GENERATION | PHYS_UNIT_TYPE | Select from the list: FC, GT, HY, IC, NA, OT, PS, PV, ST. This field is not null. | Select from the list: FC, GT, HY, IC, NA, OT, PS, PV, ST. This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Generation | Governor Droop Setting | [5 empty] | ADD 04/2012 | Unit Info - GEN | Percent | GENERATION | GOV_DROOP | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if it is not between 0 and 25. Generate Warning if > 5 (protocol requirement). | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if it is not between 0 and 25. Generate Warning if > 5 (protocol requirement). | R | Numeric | B,DVB
Generation | Governor Dead-band | [5 empty] | ADD 04/2012 | Unit Info - GEN | Hz | GENERATION | GOV_DEAD_BND | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if > 0.1. Generate Warning if > 0.03. | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if > 0.1. Generate Warning if > 0.03. | R | Numeric | B,DVB
Generation | Design Max Ambient Temperature | [5 empty] | ADD 04/2012 | Unit Info - GEN | degree F | GENERATION | DESIGN_MAX_AMB_TEMP | >100 <150 | >100 <150
Generation | Design Min Ambient Temperature | [5 empty] | ADD 04/2012 | Unit Info - GEN | degree F | GENERATION | DESIGN_MIN_AMB_TEMP | >-100 <32 | >-100 <32
Generation | Latitude Of Center Of Plant | [5 empty] | ADD 04/2012 | Unit Info - GEN | decimal degrees (N) | GENERATION | LAT_CENTER_PLT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if Latitude < 25.0 or > 37.0.
Generation | Longitude Of Center Of Plant | [5 empty] | ADD 04/2012 | Unit Info - GEN | decimal degrees (W) | GENERATION | LONG_CENTER_PLT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if <93 or > 107 .
CC | Non_Moldeled Generator | [5 empty] | ADD 04/2012 | Unit Info - Train | Y/N | Train | NON_MOD_GEN | 1.Select from the list: Y or N 2.Not Null | Select from the list: Y or N | R | Dropdown List | B,DVB
CC | Resource Category | [5 empty] | UPDATE 02/2012 | Unit Info - Train | List | Train | RES_CATG_TRN | 1. Select from the list 2. Not null. | 1.Resource type is not null. 2. Select from the list: Combined Cycle <= 90 MW, Combined Cycle >90 MW This field is not null 3. Resource Category for CCTrain is determined by the capacity of largest simple cycle combustion turbine in the train. Example if a CCTrain is combined cycle >90 MW, largest CT in the train should have real power rating>90. Audit report should generate an error if the CT's are <90 MW in this case. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/kittiepong
CC | Latitude of center of Plant | [5 empty] | ADD 04/2012 | Unit Info - Train | decimal degrees (N) | Train | LAT_CENTER_PLT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if Latitude < 25.0 or > 37.0.
CC | Longitude of center of Plant | [5 empty] | ADD 04/2012 | Unit Info - Train | decimal degrees (W) | Train | LONG_CENTER_PLT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if <93 or > 107 .
CC | SITE_CODE | [5 empty] | ADD 02/2012 | UNIT Info - CC | Automatic | CCUNIT | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
CC | Train Name | Corrected 02/23/2012 |  |  |  |  | ADD 02/2012 | Unit Info - CC | List | TRAIN CCUNIT | TRAIN_CODE | 1. This field is not null. Data type is Character | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS
CC | Non_Modeled Generator | Removed |  |  |  |  | ADD 04/2012 | Unit Info - CC | Y/N | CCUNIT | NON_MOD_GEN | 1.Select from the list: Y or N 2.Not Null | Select from the list: Y or N | R | Dropdown List | B,DVB
CC | Transmission Only Date (POI) | [5 empty] | ADD 04/2012 | Unit Info - CC | mm/dd/yyyy | CCUNIT | TRANS_ONLY_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB
CC | Standard Generation Interconnection Agreement (SGIA) Signature Date | [5 empty] | ADD 04/2012 | Unit Info - CC | mm/dd/yyyy | CCUNIT | SGIA_SIG_DT |  | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date. | R | Date | B/DVB | CDannunzio
CC | Unit Start Date (Model Ready Date) | [5 empty] | ADD 04/2012 | Unit Info - CC | mm/dd/yyyy | CCUNIT | UNIT_MRD_ST_DT |  | This field is not null. Format should be: MM/DD/YYYY Unit Start Date should be >= Site Start Date ( Site-Information Tab)
CC | SubStation Code/SubStation Mnemonic | [5 empty] | ADD 04/2012 | Unit Info - CC | All Caps | CCUNIT | SUBSTAT_CODE_SUB_MNEMONIC |  | 1) This field is not null (required). Data type must be Character. 2) Must match ERCOT records (unless new). Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" . 4) Must be <= 8 characters. Warning! Substation Code should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) Substation code should be in Upper case letters. Generate an error if the rule fails. | R | Character | B/DVB | CDannunzio
CC | Voltage Level | [5 empty] | ADD 04/2012 | Unit Info - CC | kV | CCUNIT | VOL_LEV |  | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | R | Float | B/DVE | CDannunzio
CC | PTI Bus Number | [5 empty] | ADD 04/2012 | Unit Info - CC | # | CCUNIT | PTI_BUS_NUM |  | 1) This field isnot null (required). Data type must be Integer. 2) The value must be > 0. | R | Integer | B/DVB | CDannunzio
CC | Primary Fuel Type | [5 empty] | UPDATE 02/2012 | Unit Info - CC | List | CCUNIT | PRIM_FUELTYPE | 1. Select from the list 2. Not null. | 1. Select from the list: DFO, JF, KER, NA, NG, OBG, OO, OG, TDF, WDL, WH, STM 2. Audit report should generate an error when Physical Unit type is 'ST' or 'CA' and Primary or Secondary Fuel type is 'STM'. The rule is not applicable for PUN sites | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS
CC | Secondary Fuel Type | [5 empty] | UPDATE 02/2012 | Unit Info - CC | List | CCUNIT | SEC_FUELTYPE | 1. Select from the list 2. Not null. | 1. Select from the list: DFO, JF, KER, NA, NG, OBG, OO, OG, TDF, WDL, WH, STM 2.Audit report should generate an error when Physical Unit type is 'ST' or 'CA' and Primary or Secondary Fuel type is 'STM'. The rule is not applicable for PUN sites | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS
CC | Physical Unit Type | [5 empty] | UPDATE 02/2012 | Unit Info - CC | List | CCUNIT | PHYS_UNIT_TYPE | 1. Select from the list:CA, CC, CS, CT, ST, OT 2. Not null. | Select from the list:CA, CC, CS, CT, ST, OT This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS
CC | Governor Droop Setting | [5 empty] | ADD 04/2012 | Unit Info - CC | Percent | CCUNIT | GOV_DROOP | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if it is not between 0 and 25. Generate Warning if > 5 (protocol requirement). | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if it is not between 0 and 25. Generate Warning if > 5 (protocol requirement). | R | Numeric | B,DVB
CC | Governor Dead-band | [5 empty] | ADD 04/2012 | Unit Info - CC | Hz | CCUNIT | GOV_DEAD_BND | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if > 0.1. Generate Warning if > 0.03. | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if > 0.1. Generate Warning if > 0.03. | R | Numeric | B,DVB
CC | Design Max Ambient Temperature | [5 empty] | ADD 04/2012 | Unit Info - CC | degree F | CCUNIT | DESIGN_MAX_AMB_TEMP | >100 <150 | >100 <150
CC | Design Min Ambient Temperature | [5 empty] | ADD 04/2012 | Unit Info - CC | degree F | CCUNIT | DESIGN_MIN_AMB_TEMP | >-100 <32 | >-100 <32
Wind | Non Modeled Generation | [5 empty] | ADD 04/2012 | Unit Info - Wind | Y/N | WIND | NON_MOD_GEN | 1.Select from the list: Y or N 2.Not Null | Select from the list: Y or N | R | Dropdown List | B,DVB
Wind | Transmission Only Date (POI) | [5 empty] | ADD 04/2012 | Unit Info - Wind | mm/dd/yyyy | WIND | TRANS_ONLY_DT | 1. Optional. 2. Format should be: MM/DD/YYYY | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB
Wind | Standard Generation Interconnection Agreement (SGIA) Signature Date | [5 empty] | ADD 04/2012 | Unit Info - Wind | mm/dd/yyyy | WIND | SGIA_SIG_DT | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date. | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date. | R | Date | B/DVB | CDannunzio
Wind | Unit Start Date (Model Ready Date) | [5 empty] | ADD 04/2012 | Unit Info - Wind | mm/dd/yyyy | WIND | UNIT_MRD_ST_DT | 1.This field is not null. Format should be: MM/DD/YYYY 2.Date should be Vaild Data Base Load Date 3.Unit Start Date should be >= Site Start Date ( Site-Information Tab) | This field is not null. Format should be: MM/DD/YYYY Unit Start Date should be >= Site Start Date ( Site-Information Tab)
Wind | Substation Code/substation Mnemonic | [5 empty] | ADD 04/2012 | Unit Info - Wind | All caps | Wind | SUBSTAT_CODE_SUB_MNEMONIC | 1) This field is not null (required). Data type must be Character. 2) Must match ERCOT records (unless new). Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" . 4) Must be <= 8 characters. Warning! Substation Code should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) Substation code should be in Upper case letters. Generate an error if the rule fails. | 1) This field is not null (required). Data type must be Character. 2) Must match ERCOT records (unless new). Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" . 4) Must be <= 8 characters. Warning! Substation Code should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) Substation code should be in Upper case letters. Generate an error if the rule fails. | R | Character | B/DVB | CDannunzio
Wind | Voltage Level | [5 empty] | ADD 04/2012 | Unit Info - Wind | kV | Wind | VOL_LEV | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0. | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0. | R | Float | B/DVE | CDannunzio
Wind | Pti Bus Number | [5 empty] | ADD 04/2012 | Unit Info - Wind | # | Wind | PTI_BUS_NUM | 1) This field isnot null (required). Data type must be Integer. 2) The value must be > 0. | 1) This field isnot null (required). Data type must be Integer. 2) The value must be > 0. | R | Integer | B/DVB | CDannunzio
Wind | Resource Category | [5 empty] | UPDATE 02/2012 | Unit Info - Wind | List | Wind | RES_CATG | 1. Not null. 2. Select from the list WGR, OT. | 1.Resource Category is not null. 2.Select from the list: Wind Generation Resource and OT | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/kittiepong
Wind | Physical Unit Type | [5 empty] | UPDATE 02/2012 | Unit Info - Wind | List | Wind | PHYS_UNIT_TYPE | Select from the list: OT, WT not null. | Select from the list: Wind Generation Resource, OT | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Wind | Governor Droop Setting | [5 empty] | ADD 04/2012 | Unit Info - Wind | Percent | Wind | GOV_DROOP |  | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if it is not between 0 and 25. Generate Warning if > 5 (protocol requirement). | R | Numeric | B,DVB
Wind | Governor Dead-band | [5 empty] | ADD 04/2012 | Unit Info - Wind | Hz | Wind | GOV_DEAD_BND |  | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if > 0.1. Generate Warning if > 0.03. | R | Numeric | B,DVB
Wind | Design Max Ambient Temperature | [5 empty] | ADD 04/2012 | Unit Info - Wind | Degree F | Wind | DESIGN_MAX_AMB_TEMP |  | >100 <150
Wind | Design Min Ambient Temperature | [5 empty] | ADD 04/2012 | Unit Info - Wind | Degree F | Wind | DESIGN_MIN_AMB_TEMP |  | >-100 <32
Wind | Eligible for McCamey Flow gate Rights (MCFRIs)? | [5 empty] | REMOVE | Unit Info - Wind |  | Wind |  |  | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Wind | Height of Meteorological Tower Instrumentation | [5 empty] | REMOVE | Unit Info - Wind |  | Wind | HGT_MET_TWR_INST |  | This field is not null. Data type should be character | R | Numeric | B | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
Wind | Height of Meteorological Instrumentation - Wind Speed | [5 empty] | ADD 04/2012 | Unit Info - Wind | Meters | Wind | HGT_MET_TWR_WND_SPD |  | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Float | B/DVB | CDannunzio
Wind | Height of Meteorological Instrumentation - Wind Direction | [5 empty] | ADD 04/2012 | Unit Info - Wind | Meters | Wind | HGT_MET_TWR_WND_DIRT |  | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Float | B/DVB | CDannunzio
Wind | Height of Meteorological Instrumentation - Barometric Pressure | [5 empty] | ADD 04/2012 | Unit Info - Wind | Meters | Wind | HGT_MET_TWR_BAR_PRES |  | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Float | B/DVB | CDannunzio
Wind | Height of Meteorological Instrumentation - Temperature | [5 empty] | ADD 04/2012 | Unit Info - Wind | Meters | Wind | HGT_MET_TWR_TEMP |  | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Float | B/DVB | CDannunzio
Wind | Latitude Of Center Of Wind Plant | [5 empty] | UPDATE 02/2012 | Unit Info - Wind | decimal degrees(N) | Wind | LAT_CTR_WNDFARM | 1. Not null. | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if Latitude < 25.0 or > 37.0.
Wind | Longitude Of Center Of Wind Plant | [5 empty] | UPDATE 02/2012 | Unit Info - Wind | decimal degrees(W) | Wind | LONG_CTR_WNDFARM | 1. Not null. | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if <93 or > 107 .
Wind | Resoure Name (Unit Code/Mnemonic) | [5 empty] | ADD 02/2012 | Unit Info -Wind Turbine | List | Wind | UNIT_CODE | 1. Not Null. 2. Enter Site Code and Unit Name for this field (Sitecode_Unit Name) 3. All letters must be capital | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Generation | Unit Name |  |  | UNIT_NAME field has not been added to OWNERSHIP TABLE/ FAILED |  |  | ADD 02/2012 | Ownership - GEN | List | GENERATION | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Generation | Resource Name (Unit Code/Mnemonic) |  |  | UNIT_CODE field has not been added to SITECODES TABLE/ FAILED |  |  | ADD 02/2012 | Ownership - GEN | List | OWNERSHIP | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Generation | Joint OWNER |  |  | If JOCODE is marked N then fixed ownership amount should = 100%/ FAILED (Pena) |  |  | ADD 04/2012 | Ownership - GEN | Y/N | OWNERSHIP | J0CODE |  | 1. Select from the list: Y or N 2. If N then Fixed Ownership 100% | R | Dropdown List
Generation | Market Participant (Resource) Name | [5 empty] | REMOVE | Ownership - GEN |  | OWNERSHIP |  |  | This field is conditional. Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. Data type: character. | C | Character | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0 | EMS,Lodestar,NMMS
Generation | Market Participant (Resource) Duns Number | [5 empty] | REMOVE | Ownership - GEN |  | OWNERSHIP |  |  | This field is conditional. Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. This should be either 9 or 13 digit number | C | Integer | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0 | EMS,Lodestar,NMMS
Generation | Ownership Start Date |  |  | New field to be added on 04/2012 |  |  | ADD 04/2012 | Ownership - GEN | mm/dd/yyyy | OWNERSHIP | OWNR_START_DT |  | Format should be: MM/DD/YYYY | R | Date | B/DVB
Generation | Ownership Stop Date |  |  | New field to be added on 04/2012 |  |  | ADD 04/2012 | Ownership - GEN | mm/dd/yyyy | OWNERSHIP | OWNR_END_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB
CC | Train Name | [5 empty] | ADD 02/2012 | Ownership - CC | List | TRAIN | TRAIN_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
CC | Train Code | Corrected 02/23/2012 |  |  |  |  | ADD 02/2012 | Ownership - CC | Automatic | TRAIN OWNERSHIP | TRAIN_CODE UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
CC | Resource Entity Name | Corrected |  |  |  |  | ADD 04/2012 Existing Field | Ownership - CC |  | OWNERSHIP | MKT_PRTCPT |  | This field is conditional. Required if Resource Entity represents 100% of all units. Resource Entity Name should not allow any special characters except spaces | C | Character | B | RARF Guide Version 4.0 | Lodestar,NMMS
CC | Resource Duns Number | Corrected |  |  |  |  | ADD 04/2012 Existing Field | Ownership - CC | 9-13 digits | OWNERSHIP | MKT_PRTCPT_DUNS |  | This field is conditional. Required if Resource Entity represents 100% of all units. | C | Numeric | B,DVE | RARF Guide Version 4.0 | Lodestar,NMMS
CC | Ownership-CC2 | [5 empty] | REMOVE | Ownership - CC |  | OWNERSHIP |  |  | This Section is conditional. Required for only Combined Cycle generation resources | C
CC | Resource Entity Name | [5 empty] | REMOVE | Ownership - CC |  | OWNERSHIP |  |  | This field is conditional. Required if Resource Entity represents 100% of all units. | C | Character | B | RARF Guide Version 4.0 | Lodestar,NMMS
CC | Resource Duns Number | [5 empty] | REMOVE | Ownership - CC |  | OWNERSHIP |  |  | This field is conditional. Required if Resource Entity represents 100% of all units. | C | Numeric | B,DVE | RARF Guide Version 4.0 | Lodestar,NMMS
CC | Ownership-CC3 | [5 empty] | REMOVE | Ownership - CC |  | OWNERSHIP |  |  | This Section is conditional. Required for only Combined Cycle generation resources | C |  |  | RARF Guide Version 4.0
CC | Resource Entity Name | [5 empty] | REMOVE | Ownership - CC |  | OWNERSHIP |  |  | This field is conditional. Required if Resource Entity represents 100% of all units. | C | Character | B | RARF Guide Version 4.0 | Lodestar,NMMS
CC | Resource Duns Number | [5 empty] | REMOVE | Ownership - CC |  | OWNERSHIP |  |  | This field is conditional. Required if Resource Entity represents 100% of all units. | C | Numeric | B,DVE | RARF Guide Version 4.0 | Lodestar,NMMS
CC | Ownership Start Date | [5 empty] | ADD 04/2012 | Ownership - CC | mm/dd/yyyy | OWNERSHIP | OWNR_START_DT |  | Format should be: MM/DD/YYYY | R | Date | B/DVB
CC | Ownership Stop Date | [5 empty] | ADD 04/2012 | Ownership - CC | mm/dd/yyyy | OWNERSHIP | OWNR_END_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB
Wind | Unit Name | [5 empty] | ADD 02/2012 | Ownership - WIND | List | WIND | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Wind | Resource Name (Unit Code/Mnemonic) | [5 empty] | ADD 02/2012 | Ownership - WIND | Automatic | OWNERSHIP & SITECODES | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Wind | Joint Ownership | [5 empty] | ADD 04/2012 | Ownership - WIND | Y/N | OWNERSHIP | J0CODE |  | 1. Select from the list: Y or N 2. If N then Fixed Ownership 100% | R | Dropdown List
Wind | Market Participant (Resource) Name | [5 empty] | REMOVE | Ownership - WIND |  | OWNERSHIP |  |  | This field is conditional. Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. Data type: character. | C | Character | B,DVB | RARF Guide Version 4.0 | EMS,Lodestar,NMMS
Wind | Market Participant (Resource) Duns Number | [5 empty] | REMOVE | Ownership - WIND |  | OWNERSHIP |  |  | This field is conditional. Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. This should be either 9 or 13 digit number | C | Integer | B,DVB | RARF Guide Version 4.0/Angela Moy | EMS,Lodestar,NMMS
Wind | Ownership Start Date | [5 empty] | ADD 04/2012 | Ownership - Wind | mm/dd/yyyy | OWNERSHIP | OWNR_START_DT |  | Format should be: MM/DD/YYYY | R | Date | B/DVB
Wind | Ownership Stop Date | [5 empty] | ADD 04/2012 | Ownership - Wind | mm/dd/yyyy | OWNERSHIP | OWNR_END_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB
Generation | Unit Name |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 02/2012 | Parameters - GEN | List | Generation | UNIT_NAME | 1. Not Null. 2. Must not exceed 4 characters for Jointly Owned Units 3. Maximum of 8 character allowed | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Generation | Resource Name (Unit Code/Mnemonic) |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 04/2012 | Parameters - GEN | Atomatic | Generation & DERATING | UNIT_CODE | 1. Not Null. 2. Enter Site Code and Unit Name for this field (Sitecode_Unit Name) 3. All letters must be capital | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Generation | High Reasonability Limit |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | UPDATE 02/2012 | Parameters - GEN | MW | Generation | HR_LMT | 1. High Reasonability Limit >0 2. HighReasonabilityLimit >= LowReasonablityLimit 3. Not Null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Generation | Low Reasonability Limit |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | UPDATE 02/2012 | Parameters - GEN | MW | Generation | LR_LMT | 1. Low Reasonability Limit >0 for Non PUN sites 2. Low ReasonabilityLimit <= High ReasonablityLimit 3. PUN (Private Use Network) Sites LRL should equal zero or produce a Warning 4. Not Null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Generation | High Reasonability Ramp Rate Limit |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | UPDATE 02/2012 | Parameters - GEN | MW/min | Generation | HR_RAMPRATE_LMT | 1. High Reasonability Ramp Rate Limit >= Low Reasonability Ramp Rate Limit. 2. Not null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS
Generation | Low Reasonability Ramp Rate Limit |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | UPDATE 02/2012 | Parameters - GEN | MW/min | Generation | LR_RAMP_RATE_LMT | 1. Low Reasonability Ramp Rate Limit >=0. 2. Not null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS
Generation | Seasonal Net Max Sustainable Rating - Spring | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MAX_SUST_RTG_SP | 1.Seasonal Net Max Sustainable Rating - Spring >= Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Spring > Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS
Generation | Seasonal Net Min Sustainable Rating - Spring | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MIN_SUST_RTG_SP | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS
Generation | Seasonal Net Max Emergency Rating - Spring | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MAX_EMGY_RTG_SP | 1.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS
Generation | Seasonal Net Min Emergency Rating - Spring | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MIN_EMGY_RTG_SP | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit 2. Not Null | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS
Generation | Seasonal Net Max Sustainable Rating - Summer | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MAX_SUST_RTG_SM | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Summer > Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Generation | Seasonal Net Min Sustainable Rating - Summer | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MIN_SUST_RTG_SM | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu | MMS
Generation | Seasonal Net Max Emergency Rating - Summer | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MAX_EMGY_RTG_SM | 1.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Summer > Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Generation | Seasonal Net Min Emergency Rating - Summer | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MIN_EMGY_RTG_SM | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Generation | Seasonal Net Max Sustainable Rating - Fall | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MAX_SUST_RTG_FL | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Generation | Seasonal Net Min Sustainable Rating - Fall | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MIN_SUST_RTG_FL | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall. >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Generation | Seasonal Net Max Emergency Rating - Fall | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MAX_EMGY_RTG_FL | 1.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Fall > Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Generation | Seasonal Net Min Emergency Rating - Fall | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MIN_EMGY_RTG_FL | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Generation | Seasonal Net Max Sustainable Rating - Winter | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MAX_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Generation | Seasonal Net Min Sustainable Rating - Winter | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MIN_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Generation | Seasonal Net Max Emergency Rating - Winter | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MAX_EMGY_RTG_WT | 1.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Winter > Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Generation | Seasonal Net Min Emergency Rating - Winter | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MIN_EMGY_RTG_WT | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Generation | 0°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 5°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 10°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 15°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 20°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 25°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 30°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 35°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 40°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 45°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 50°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 55°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 60°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 65°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 70°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 75°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 80°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 85°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 90°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 95°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 100°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 105°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 110°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 115°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | 120°f | [5 empty] | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | Unit Name | [5 empty] | ADD 02/2012 | Parameters - CC | List | CCUNIT | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
CC | Resource Name (Unit Code/Mnemonic) | [5 empty] | ADD 02/2012 | Parameters - CC | List | CCUNIT & DERATING | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
CC | High Reasonability Limit | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | HR_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit | R | Numeric | B,DVB | KitteiPong/Jamil Daouk | EMS,MMS,NMMS
CC | Low Reasonability Limit | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | LR_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | Numeric | B,DVB | KitteiPong/Lin Xu/ Jamil Daouk, Kenneth Ragsdale | EMS,MMS,NMMS
CC | High Reasonability Ramp Rate Limit | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW/min | CCUNIT | HR_RAMPRATE_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
CC | Low Reasonability Ramp Rate Limit | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW/min | CCUNIT | LR_RAMP_RATE_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
CC | Seasonal Net Max Sustainable Rating - Spring | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MAX_SUST_RTG_SP |  | 1.Seasonal Net Max Sustainable Rating - Spring should be > Seasonal Net Min Sustainable Rating. 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
CC | Seasonal Net Min Sustainable Rating - Spring | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MIN_SUST_RTG_SP |  | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
CC | Seasonal Net Max Emergency Rating - Spring | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MAX_EMGY_RTG_SP |  | 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
CC | Seasonal Net Min Emergency Rating - Spring | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MIN_EMGY_RTG_SP |  | 1.Seasonal Net Min Emergency Rating - Spring < = Seasonal Net Min Sustainable Rating - Spring. 2.Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
CC | Seasonal Net Max Sustainable Rating - Summer | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MAX_SUST_RTG_SM |  | 1.Seasonal Net Max Sustainable Rating - Summer > Seasonal Net Min Sustainable Rating - Summer. 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
CC | Seasonal Net Min Sustainable Rating - Summer | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MIN_SUST_RTG_SM |  | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
CC | Seasonal Net Max Emergency Rating - Summer | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MAX_EMGY_RTG_SM |  | 1.Seasonal Net Max Emergency Rating -Summer > Seasonal Net Min Emergency Rating - Summer. 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3.Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
CC | Seasonal Net Min Emergency Rating - Summer | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MIN_EMGY_RTG_SM |  | 1.Seasonal Net Min Emergency Rating - Summer < = Seasonal Net Min Sustainable Rating - Summer. 2.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
CC | Seasonal Net Max Sustainable Rating - Fall | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MAX_SUST_RTG_FL |  | 1.Seasonal Net Max Sustainable Rating - Fall > Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
CC | Seasonal Net Min Sustainable Rating - Fall | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MIN_SUST_RTG_FL |  | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall. 2.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
CC | Seasonal Net Max Emergency Rating - Fall | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MAX_EMGY_RTG_FL |  | 1.Seasonal Net Max Emergency Rating - Fall > Seasonal Net Min Emergency Rating - Fall. 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
CC | Seasonal Net Min Emergency Rating - Fall | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MIN_EMGY_RTG_FL |  | 1.Seasonal Net Min Emergency Rating - Fall < = Seasonal Net Min Sustainable Rating - Fall. 2.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
CC | Seasonal Net Max Sustainable Rating - Winter | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MAX_SUST_RTG_WT |  | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
CC | Seasonal Net Min Sustainable Rating - Winter | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MIN_SUST_RTG_WT |  | 1.Seasonal Net Min Sustainable Rating - Winter >= Seasonal Net Min Emergency Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
CC | Seasonal Net Max Emergency Rating - Winter | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MAX_EMGY_RTG_WT |  | 1.Seasonal Net Max Emergency Rating - Winter > Seasonal Net Min Emergency Rating - Winter. 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
CC | Seasonal Net Min Emergency Rating - Winter | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MIN_EMGY_RTG_WT |  | 1.Seasonal Net Min Emergency Rating - Winter < = Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
CC | 0°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 5°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 10°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 15°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 20°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 25°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 30°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 35°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 40°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 45°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 50°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 55°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 60°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 65°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 70°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 75°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 80°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 85°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 90°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 95°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 100°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 105°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 110°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 115°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 120°f | [5 empty] | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | SITECODE | [5 empty] | ADD 02/2012 | Parameters - CFG | List | CONFIGURATIONS | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
CC | Train Code | Corrected 02/23/2012 |  |  |  |  | ADD 02/2012 | Parameters - CFG | List | TRAIN | TRAIN_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
CC | Configuration Code | [5 empty] | ADD 02/2012 | Parameters - CFG | List | CONFIGURATIONS & DERATING | CONFIG_CODE
CC | High Reasonability Limit | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | HR_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
CC | Low Reasonability Limit | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | LR_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
CC | High Reasonability Ramp Rate Limit | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW/min | CONFIGURATIONS | HR_RAMPRATE_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | EMS,MMS,NMMS
CC | Low Reasonability Ramp Rate Limit | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW/min | CONFIGURATIONS | LR_RAMP_RATE_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | EMS,MMS,NMMS
CC | Seasonal Net Max Sustainable Rating - Spring | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MAX_SUST_RTG_SP |  | 1.Seasonal Net Max Sustainable Rating - Spring > Seasonal Net Min Sustainable Rating - Spring. 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS,NMMS
CC | Seasonal Net Min Sustainable Rating - Spring | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MIN_SUST_RTG_SP |  | 1.Seasonal Net Max Sustainable Rating - Spring > Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 3.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS,NMMS
CC | Seasonal Net Max Emergency Rating - Spring | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MAX_EMGY_RTG_SP |  | 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS,NMMS
CC | Seasonal Net Min Emergency Rating - Spring | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MIN_EMGY_RTG_SP |  | 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Emergency Rating - Spring < = Seasonal Net Min Sustainable Rating - Spring. 3.Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS,NMMS
CC | Seasonal Net Max Sustainable Rating - Summer | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MAX_SUST_RTG_SM |  | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer. 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
CC | Seasonal Net Min Sustainable Rating - Summer | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MIN_SUST_RTG_SM |  | 1.Seasonal Net Max Sustainable Rating - Summer > Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
CC | Seasonal Net Max Emergency Rating - Summer | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MAX_EMGY_RTG_SM |  | 1.Seasonal Net Max Emergency Rating - Summer > Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3.Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
CC | Seasonal Net Min Emergency Rating - Summer | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MIN_EMGY_RTG_SM |  | 1.Seasonal Net Max Emergency Rating - Summer > Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Emergency Rating - Summer < = Seasonal Net Min Sustainable Rating - Summer. 3.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
CC | Seasonal Net Max Sustainable Rating - Fall | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MAX_SUST_RTG_FL |  | 1.Seasonal Net Max Sustainable Rating - Fall > Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
CC | Seasonal Net Min Sustainable Rating - Fall | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MIN_SUST_RTG_FL |  | Seasonal Net Max Emergency Rating - Summer > Seasonal Net Min Emergency Rating - Summer | R | Numeric | B,DVB | Lin Xu | MMS
CC | Seasonal Net Max Emergency Rating - Fall | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MAX_EMGY_RTG_FL |  | 1.Seasonal Net Max Emergency Rating - Fall > Seasonal Net Min Emergency Rating - Fall. 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
CC | Seasonal Net Min Emergency Rating - Fall | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MIN_EMGY_RTG_FL |  | 1.Seasonal Net Max Emergency Rating - Fall > Seasonal Net Min Emergency Rating - Fall. 2.Seasonal Net Min Emergency Rating - Fall < = Seasonal Net Min Sustainable Rating - Fall. 3.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
CC | Seasonal Net Max Sustainable Rating - Winter | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MAX_SUST_RTG_WT |  | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
CC | Seasonal Net Min Sustainable Rating - Winter | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MIN_SUST_RTG_WT |  | 1.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Min Emergency Rating - Fall. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
CC | Seasonal Net Max Emergency Rating - Winter | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MAX_EMGY_RTG_WT |  | 1.Seasonal Net Max Emergency Rating - Winter > Seasonal Net Min Emergency Rating - Winter. 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
CC | Seasonal Net Min Emergency Rating - Winter | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MIN_EMGY_RTG_WT |  | 1.Seasonal Net Max Emergency Rating - Winter > Seasonal Net Min Emergency Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter < = Seasonal Net Min Sustainable Rating - Winter. 3.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
CC | 0°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 5°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 10°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 15°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 20°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 25°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 30°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 35°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 40°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 45°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 50°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 55°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 60°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 65°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 70°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 75°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 80°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 85°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 90°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 95°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 100°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 105°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 110°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 115°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
CC | 120°f | [5 empty] | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | Unit Name | [5 empty] | ADD 02/2012 | Parameters - Wind | List | WIND | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Wind | Resource Name (Unit Code/Mnemonic) | [5 empty] | ADD 02/2012 | Parameters - Wind | Automatic | WIND & DERATING | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
Wind | High Reasonability Limit | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | HR_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
Wind | Low Reasonability Limit | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | LR_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
Wind | High Reasonability Ramp Rate Limit | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW/min | WIND | HR_RAMPRATE_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | EMS,MMS,NMMS
Wind | Low Reasonability Ramp Rate Limit | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW/min | WIND | LR_RAMP_RATE_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | EMS,MMS,NMMS
Wind | Seasonal Net Max Sustainable Rating - Spring | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MAX_SUST_RTG_SP |  | 1.Seasonal Net Max Sustainable Rating - Spring > Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
Wind | Seasonal Net Min Sustainable Rating - Spring | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MIN_SUST_RTG_SP |  | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
Wind | Seasonal Net Max Emergency Rating - Spring | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MAX_EMGY_RTG_SP |  | 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
Wind | Seasonal Net Min Emergency Rating - Spring | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MIN_EMGY_RTG_SP |  | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
Wind | Seasonal Net Max Sustainable Rating - Summer | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MAX_SUST_RTG_SM |  | 1.Seasonal Net Max Sustainable Rating - Summer > Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Wind | Seasonal Net Min Sustainable Rating - Summer | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MIN_SUST_RTG_SM |  | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Wind | Seasonal Net Max Emergency Rating - Summer | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MAX_EMGY_RTG_SM |  | 1.Seasonal Net Max Emergency Rating - Summer > Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Wind | Seasonal Net Min Emergency Rating - Summer | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MIN_EMGY_RTG_SM |  | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Wind | Seasonal Net Max Sustainable Rating - Fall | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MAX_SUST_RTG_FL |  | 1.Seasonal Net Max Sustainable Rating - Fall > Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Wind | Seasonal Net Min Sustainable Rating - Fall | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MIN_SUST_RTG_FL |  | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall. >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Wind | Seasonal Net Max Emergency Rating - Fall | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MAX_EMGY_RTG_FL |  | 1.Seasonal Net Max Emergency Rating - Fall > Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Wind | Seasonal Net Min Emergency Rating - Fall | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MIN_EMGY_RTG_FL |  | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Wind | Seasonal Net Max Sustainable Rating - Winter | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MAX_SUST_RTG_WT |  | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Wind | Seasonal Net Min Sustainable Rating - Winter | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MIN_SUST_RTG_WT |  | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Wind | Seasonal Net Max Emergency Rating - Winter | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MAX_EMGY_RTG_WT |  | 1.Seasonal Net Max Emergency Rating - Winter > Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Wind | Seasonal Net Min Emergency Rating - Winter | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MIN_EMGY_RTG_WT |  | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Wind | 0°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 5°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 10°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 15°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 20°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 25°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 30°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 35°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 40°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 45°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 50°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 55°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 60°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 65°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 70°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 75°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 80°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 85°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 90°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 95°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 100°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 105°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 110°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 115°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Wind | 120°f | [5 empty] | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Generation | Unit Name |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 02/2012 | Operational Parameters - GEN | List | GENERATION | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Generation | Resource Name (Unit Code/Mnemonic) |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 02/2012 | Operational Parameters - GEN | Automatic | GENERATION | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Generation | Minimum On Line Time | Check |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN | hours | GENERATION | MIN_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum On Line Time >= 0 | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Generation | Minimum Off Line Time | Check |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN | hours | GENERATION | MIN_OFFLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum Off Line Time >= 0 | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Generation | Hot Start Time | Corrected |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN | hours | GENERATION | HOTSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot Start Time >= 0 3. Hot Start Time <= Intermediate Start Time | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Generation | Intermediate Start Time | Corrected |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN | hours | GENERATION | INTERMSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate Start Time >= 0 3. Cold Start Time >= Intermediate Start Time >= Hot Start Time | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Generation | Cold Start Time | Corrected |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN | hours | GENERATION | COLDSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Cold Start Time >= 0 3. Cold Start Time >= Intermediate Start Time | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Generation | Max Weekly Starts | Check |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN |  | GENERATION | MAXWKLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Generation | Max On Line Time | Corrected |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN | hours | GENERATION | MAX_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Max OnLine Time > 0 | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Generation | Max Daily Starts | Check |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN |  | GENERATION | MAXDLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Daily Start >= 0 3. Max Daily Start <= 999 | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Generation | Max Weekly Energy | Corrected |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN | MWh | GENERATION | MAXWKLYENRGY |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Energy >= 0 3. Max Weekly Energy < 1e10 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Generation | Hot-to-Intermediate Time | Check |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN | hours | GENERATION | HOT_TO_INTMDT_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot-to-Intermediate Time >= 0 | R | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | NMMS
Generation | Intermediate-to-Cold Time | Check |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN | hours | GENERATION | INTMDT_TO_COLD_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate-to-Cold Time >= 0 | R | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | NMMS
Generation | Unit Name |  |  | UNIT_NAME field has not been added to Ramp Rate NRRC TABLE/ FAILED |  |  | ADD 02/2012 | Operational Parameters - GEN - NRRC | List | GENERATION | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Generation | Resource Name (Unit Code/Mnemonic) |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 02/2012 | Operational Parameters - GEN - NRRC | List | RAMP_RATES_NRRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Generation | NRRC Code |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | UPDATE 02/2012 | Operational Parameters - GEN - NRRC | Automatic | RAMP_RATES_NRRC | UNIT_MW_NRRC |  | Capture Unit Code and UNIT MW Number and NRRC, prepopulate this field with UNIT_CODE_UNIT_MW_NUMBER_NRRC. | R | Character
Generation | NRRC MW (1 to X) | Corrected |  | Passed/DCSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN - NRRC | MW | RAMP_RATES_NRRC | MW_RATING_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn | R | Numeric | B | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS
Generation | Upward Ramp Rate(1 to X) | Check |  | Passed/DCSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN - NRRC | MW/min | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2.. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Generation | Downward Ramp Rate (1 to X) | Check |  | Passed/DCSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN - NRRC | MW/min | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Generation | Unit Name |  |  | UNIT_NAME field has not been added to Ramp Rate ERRC TABLE/ FAILED |  |  | ADD 02/2012 | Operational Parameters - GEN - ERRC | List | GENERATION | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Generation | Resource Name (Unit Code/Mnemonic) |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 02/2012 | Operational Parameters - GEN - ERRC | List | RAMP_RATES_ERRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Generation | ERRC Code |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | UPDATE 02/2012 | Operational Parameters - GEN - NRRC | Automatic | RAMP_RATES_ERRC | UNIT_MW_ERRC |  | Capture Unit Code and UNIT MW Number and ERRC, prepopulate this field with UNIT_CODE_UNIT_MW_NUMBER_ERRC. | R | Character
Generation | ERRC MW (1 to X) | Corrected |  | Passed/DCSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN - NRRC | MW | RAMP_RATES_NRRC | MW_RATING_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn | R | Numeric | B | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS
Generation | Upward Ramp Rate(1 to X) | Check |  | Passed/DCSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN - ERRC | MW/min | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Generation | Downward Ramp Rate (1 to X) | Check |  | Passed/DCSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN - ERRC | MW/min | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
CC | SITECODE | [5 empty] | ADD 02/2012 | Operational Parameters - CFG | List | CONFIGURATIONS | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
CC | Train Code | [5 empty] | ADD 02/2012 | Operational Parameters - CFG | List | TRAIN | TRAIN_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
CC | Configuration Code | [5 empty] | ADD 02/2012 | Operational Parameters - CFG | List | CONFIGURATIONS | CONFIG_CODE |  | Required | R
CC | Minimum On Line Time | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG | hours | CONFIGURATIONS | MIN_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum On Line Time >= 0 | R | Integer | B,DVB | KittiPong/Jamil Daouk | MMS,NMMS
CC | Minimum Off Line Time | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG | hours | CONFIGURATIONS | MIN_OFFLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum Off Line Time >= 0 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
CC | Hot Start Time | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG | hours | CONFIGURATIONS | HOTSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot Start Time >= 0 3. Hot Start Time <= Intermediate Start Time | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
CC | Intermediate Start Time | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG | hours | CONFIGURATIONS | INTERMSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate Start Time >= 0 3. Cold Start Time >= Intermediate Start Time >= Hot Start Time | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
CC | Cold Start Time | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG | hours | CONFIGURATIONS | COLDSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Cold Start Time >= 0 3. Cold Start Time >= Intermediate Start Time | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
CC | Max Weekly Starts | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG |  | CONFIGURATIONS | MAXWKLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
CC | Max On Line Time | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG | hours | CONFIGURATIONS | MAX_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Max OnLine Time > 0 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
CC | Max Daily Starts | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG |  | CONFIGURATIONS | MAXDLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Daily Start >= 0 3. Max Daily Start <= 999 | R | Numeric | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
CC | Max Weekly Energy | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG | MWh | CONFIGURATIONS | MAXWKLYENRGY |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Energy >= 0 3. Max Weekly Energy < 1e10 | R | Integer | B,DVB | Lin Xu/Kittipong | MMS,NMMS
CC | Hot-to-intermediate Time | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG | hours | CONFIGURATIONS | HOT_TO_INTMDT_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot-to-Intermediate Time >= 0 | R | Integer | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
CC | Intermediate-to-cold Time | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG | hours | CONFIGURATIONS | INTMDT_TO_COLD_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate-to-Cold Time >= 0 | R | Integer | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
CC | Train Code | Corrected 02/23/2012 |  |  |  |  | ADD 02/2012 | Operational Parameters - CFG - NRRC | List | TRAIN RAMP_RATES_NRRC | TRAIN_CODE UNIT_CODE |  | 1.This field is Not null: Capture UNIT Code and Configuration Code and prepopulate this field with TRAIN _Config_Code. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
CC | Configuration Code | [5 empty] | ADD 02/2012 | Operational Parameters - CFG - NRRC | List | CONFIGURATIONS | CONFIG_CODE |  | Required Field | R | Character | B,DVB
CC | NRRC Code | [5 empty] | UPDATE 02/2012 | Operational Parameters - CFG - NRRC | Automatic | RAMP_RATES_NRRC | UNIT_MW_NRRC |  | This Field is Not in the RARF: Capture Unit Code and UNIT MW Number and NRRC, prepopulate this field with UNIT_CODE_UNIT_MW_NUMBER_NRRC. | R | Character
CC | NRRC MW | [5 empty] | UPDATE 02/2012 | Operational Parameters - CFG - NRRC | MW | RAMP_RATES_NRRC | MW_RATING_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn | R | Numeric | B | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS
CC | Upward Ramprate | [5 empty] | UPDATE 02/2012 | Operational Parameters - CFG - NRRC | MW/min | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
CC | Downward Ramprate | [5 empty] | UPDATE 02/2012 | Operational Parameters - CFG - NRRC | MW/min | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
CC | Train Code | Corrected 02/23/2012 |  |  |  |  | ADD 02/2012 | Operational Parameters - CFG - ERRC | List | TRAIN RAMP RAMP_RATES_ERRC | TRAIN_CODE UNIT_CODE |  | 1.This field is Not null: Capture Train Code and Configuration Code and prepopulate this field with Train_Code _Config_Code. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
CC | Configuration Code | [5 empty] | ADD 02/2012 | Operational Parameters - CFG - ERRC | List | CONFIGURATIONS | CONFIG_CODE |  | Required Field | R | Character | B,DVB
CC | ERRC Code | [5 empty] | UPDATE 02/2012 | Operational Parameters - CFG - ERRC | Automatic | RAMP_RATES_ERRC | UNIT_MW_ERRC |  | Capture Unit Code and UNIT MW Number and ERRC, prepopulate this field with UNIT_CODE_UNIT_MW_NUMBER_ERRC. | R | Character
CC | ERRC MW | [5 empty] | UPDATE 02/2012 | Operational Parameters - CFG - ERRC | MW | RAMP_RATES_NRRC | MW_RATING_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn | R | Numeric | B | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS
CC | Upward Ramprate | [5 empty] | UPDATE 02/2012 | Operational Parameters - CFG - ERRC | MW/min | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
CC | Downward Ramprate | [5 empty] | UPDATE 02/2012 | Operational Parameters - CFG - ERRC | MW/min | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Wind | Unit Name | [5 empty] | ADD 02/2012 | Operational Parameters - Wind |  | WIND | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Wind | Resource Name (Unit Code/Mnemonic) | [5 empty] | ADD 02/2012 | Operational Parameters - Wind |  | WIND | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
Wind | Minimum On Line Time | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind | hours | WIND | MIN_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum On Line Time >= 0 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Wind | Minimum Off Line Time | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind | hours | WIND | MIN_OFFLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum Off Line Time >= 0 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Wind | Hot Start Time | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind | hours | WIND | HOTSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot Start Time >= 0 3. Hot Start Time <= Intermediate Start Time | O | Integer | B,DVB | Angela Moy/Jamil Daouk | NMMS
Wind | Intermediate Start Time | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind | hours | WIND | INTERMSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate Start Time >= 0 3. Cold Start Time >= Intermediate Start Time >= Hot Start Time | O | Integer | B,DVB | Angela Moy/Jamil Daouk | NMMS
Wind | Cold Start Time | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind | hours | WIND | COLDSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Cold Start Time >= 0 3. Cold Start Time >= Intermediate Start Time | O | Integer | B,DVB | Angela Moy/Jamil Daouk | NMMS
Wind | Max Weekly Starts | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind |  | WIND | MAXWKLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Integer | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
Wind | Max On Line Time | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind | hours | WIND | MAX_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Max OnLine Time > 0 | R | Integer | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
Wind | Max Daily Starts | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind |  | WIND | MAXDLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Daily Start >= 0 3. Max Daily Start <= 999 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Wind | Max Weekly Energy | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind | MWh | WIND | MAXWKLYENRGY |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Energy >= 0 3. Max Weekly Energy < 1e10 | R | Numeric | B,DVB | Lin Xu | MMS,NMMS
Wind | Hot-to-Intermediate Time | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind | hours | WIND | HOT_TO_INTMDT_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot-to-Intermediate Time >= 0 | R | Integer | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
Wind | Intermediate-to-Cold Time | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind | hours | WIND | INTMDT_TO_COLD_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate-to-Cold Time >= 0 | R | Integer | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
Wind | Unit Name | [5 empty] | ADD 02/2012 | Operational Parameters - Wind - NRRC | List | WIND | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Wind | Resource Name (Unit Code/Mnemonic) | [5 empty] | ADD 02/2012 | Operational Parameters - Wind - NRRC | List | RAMP_RATES_NRRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Wind | NRRC Code | [5 empty] | UPDATE 02/2012 | Operational Parameters - Wind - NRRC | Automatic | RAMP_RATES_NRRC | UNIT_MW_NRRC |  | Capture Unit Code and UNIT MW Number and NRRC, prepopulate this field with UNIT_CODE_UNIT_MW_NUMBER_NRRC. | R | Character
Wind | NRRC MW (1 to X) | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind - NRRC | MW | RAMP_RATES_NRRC | MW_RATING_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn | R | Numeric | B | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS
Wind | Upward Ramp Rate(1 to X) | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind - NRRC | MW/min | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Wind | Downward Ramp Rate (1 to X) | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind - NRRC | MW/min | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Wind | Unit Name | [5 empty] | ADD 02/2012 | Operational Parameters - Wind - ERRC | List | WIND | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Wind | Resource Name (Unit Code/Mnemonic) | [5 empty] | ADD 02/2012 | Operational Parameters - Wind - ERRC | List | RAMP_RATES_ERRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Wind | ERRC Code | [5 empty] | UPDATE 02/2012 | Operational Parameters - Wind - ERRC | Automatic | RAMP_RATES_ERRC | UNIT_MW_ERRC |  | Capture Unit Code and Unit MW Number and prepopulate this field with Unit CODE_UNIT_MW_NUMBER_ERRC. | R | Character
Wind | ERRC MW (1 to X) | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind - ERRC | MW | RAMP_RATES_NRRC | MW_RATING_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn | R | Numeric | B | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS
Wind | Upward Ramp Rate(1 to X) | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind - ERRC | MW/min | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Wind | Downward Ramp Rate (1 to X) | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind - ERRC | MW/min | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Generation | Unit Name |  |  | Passed/DCSES |  |  | ADD 02/2012 | Reactive Capability - GEN | List | GENERATION | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Generation | Resource Name (Unit Code/Mnemonic) |  |  | Passed/DCSES |  |  | ADD 02/2012 | Reactive Capability - GEN | Automatic | GENERATION | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Generation | Reactive Capability Data Provided Below Is Gross/net Values? | [5 empty] | ADD 04/2012 | Reactive Capability - GEN | List | GENERATION | REACT_CAPB_DATA_GROSS_NET_VAL |  | Select from the list: Y or N |  | Dropdown List
Generation | Reactive Capability Data Provided Below Is From Ndcrc Test Data? | [5 empty] | ADD 04/2012 | Reactive Capability - GEN | Y/N | GENERATION | REACT_CAPB_NDCRC_TEST_DATA |  | Select from the list: Y or N |  | Dropdown List
Generation | If Reactive Capability Data Provided Below Is From Ndcrc Test Data Then Enter The Date On Which The Test Was Performed. | [5 empty] | ADD 04/2012 | Reactive Capability - GEN | mm/dd/yyyy | GENERATION | REACT_CAPB_NDCRC_TEST_DATA_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date
CC | Unit Name | [5 empty] | ADD 02/2012 | Reactive Capability - CC | List | CCUNIT | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
CC | SITE_CODE | [5 empty] | ADD 02/2012 | Reactive Capability - CC | Automatic | CCUNIT | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
CC | Resource Name (Unit Code/Mnemonic) | [5 empty] | ADD 02/2012 | Reactive Capability - CC | Automatic | CCUNIT | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
CC | Reactive Capability Data Provided is Gross/Net Values? | [5 empty] | ADD 04/2012 | Reactive Capability - CC | List | CCUNIT | REACT_CAPB_DATA_GROSS_NET_VAL |  | Select from the list: Y or N |  | Dropdown List
CC | Reactive Capability Data Provided is from NDCRC Test Data? | [5 empty] | ADD 04/2012 | Reactive Capability - CC | Y/N | CCUNIT | REACT_CAPB_NDCRC_TEST_DATA |  | Select from the list: Y or N |  | Dropdown List
CC | If Reactive Capability Data Provided Is From NDCRC test Data Then Enter The Date On Which The Test Was Performed. | [5 empty] | ADD 04/2012 | Reactive Capability - CC | mm/dd/yyyy | CCUNIT | REACT_CAPB_NDCRC_TEST_DATA_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date
Wind | Reactive Standard? | [5 empty] | REMOVE | Reactive Capability - Wind |  | REACT_CAP_WIND |  |  | Select from the list: Y ,N, Capacitors Installed REMOVED | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 | EMS,NMMS
Wind | Unit Name | Removed From Wind Form |  |  |  |  | ADD 02/2012 | Reactive Capability - Wind | List | WIND | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Wind | Resource Name (Unit Code/Mnemonic) | [5 empty] | ADD 02/2012 | Reactive Capability - Wind | Automatic | REACT_CAP_WIND | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB
Wind | Reactive Capability Data Provided Below Is Gross/net Values? | [5 empty] | ADD 04/2012 | Reactive Capability - Wind | Y/N | REACT_CAP_WIND | REACT_CAPB_DATA_GROSS_NET_VAL |  | Select from the list: Y or N |  | Dropdown List
Wind | Reactive Capability Data Provided Below Is From Ndcrc Test Data? | [5 empty] | ADD 04/2012 | Reactive Capability - Wind | mm/dd/yyyy | REACT_CAP_WIND | REACT_CAPB_NDCRC_TEST_DATA |  | Select from the list: Y or N |  | Dropdown List
Wind | If Reactive Capability Data Provided Below Is From Ndcrc Test Data Then Enter The Date On Which The Test Was Performed. | [5 empty] | ADD 04/2012 | Reactive Capability - Wind | MW | REACT_CAP_WIND | REACT_CAPB_NDCRC_TEST_DATA_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date
Wind | MW5 - Unity Power Factor | [5 empty] | REMOVE | Reactive Capability - Wind | MVAR | REACT_CAP_WIND | MW5UNITYPF |  | 1. MW5>0 - REMOVED 2. MW5>MW4. REMOVED | R | Numeric | B | Lin Xu | MMS,NMMS
CC | TRAIN CODE | Corrected 02/23/2012 |  |  |  |  | ADD 02/2012 | CC Config | List | CCUNIT_Configuration TRAIN | TRAIN_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources
CC | SITE CODE | [5 empty] | ADD 02/2012 | CC Config | Automatic | CCUNIT_Configuration | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
CC | Resource Name (Unit Code/Mnemonic) | [5 empty] | ADD 02/2012 | CC Config | List | CCUNIT_Configuration | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0/Jamil Daouk | NMMS
CC | Configuration Code | [5 empty] | ADD 02/2012 | CC Config | Automatic | CCUNIT_Configuration | CONFIG_CODE |  | Concantanate SITE_CODE, TRAIN_CODE and CONFIG_NUM
CC | Configuration Type | [5 empty] | ADD 02/2012 | CC Config | List | CCUNIT_Configuration | CONFIG_TYPE |  | There is no limit to the no. of configurations that can be registered but they should be Operationally Unique and should Increase in number of units and MWs from left to right | R | Integer | B,DVB | RARF Guide Version 4.0/ Lin Xu | NMMS
CC | CC2 Config | [5 empty] | REMOVE | CC2 Config |  |  |  |  | This tab is conditional. Required if the Generation Type selected is 'CC'. Can register up to 3 trains at one site. Register Operationally Unique Configurations. | C
CC | Resource Name(Unit Code) | [5 empty] | REMOVE | CC2 Config |  |  |  |  | Not null. Data type: Character. Should match unit Mnemonic for CC Unit | C | Character | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0/Jamil Daouk
CC | Unit Type | [5 empty] | REMOVE | CC2 Config |  |  |  |  | Not null. Data type: Character. Should match physical unit type from unit info CC | C | Character | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0/Jamil Daouk
CC | Operational Configurations ( | [5 empty] | REMOVE | CC2 Config |  |  |  |  | There is no limit to the no. of configurations that can be registered but they should be Operationally Unique and should Increase in number of units and MWs from left to right | C | Integer | B,DVB | Lin Xu/RARF Guide Version 4.0
CC | CC3 Config | [5 empty] | REMOVE | CC3 Config |  |  |  |  | This tab is conditional. Required if the Generation Type selected is 'CC'. Can register up to 3 trains at one site. Register Operationally Unique Configurations. | C
CC | Resource Name(Unit Code) | [5 empty] | REMOVE | CC3 Config |  |  |  |  | Not null. Data type: Character. Should match unit Mnemonic for CC Unit | C | Character | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0/Jamil Daouk
CC | Unit Type | [5 empty] | REMOVE | CC3 Config |  |  |  |  | Not null. Data type: Character. Should match physical unit type from unit info CC | C | Character | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0/Jamil Daouk
CC | Operational Configurations | [5 empty] | REMOVE | CC3 Config |  |  |  |  | There is no limit to the no. of configurations that can be registered but they should be Operationally Unique and should Increase in number of units and MWs from left to right | C | Integer | B,DVB | RARF Guide Version 4.0/ Lin Xu
CC | SiteCode | [5 empty] | ADD 02/2012 | CC Transitions | List | TRANSITIONS | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
CC | Mnemonic for Combine Cyle Train | [5 empty] | ADD 02/2012 | CC Transitions | List | TRANSITIONS | TRAIN_CODE |  | CONCANTENATE SITE_CODE and TRAIN_NAME
CC | Configuration Code From | [5 empty] | UPDATE 02/2012 | CC Transitions | List | TRANSITIONS | CONFIGCODE_TO |  | 1.Each configuration in Transitions including Offline can be reached. Each configuration in CC1 Transitions including Offline can reach at least one of the other configurations including Offline . 2.Values allowed are X for Main Transition , A for Alternate Transition ,Null for Non Transition 3. 1.If a RARF is submitted that does not have the first Transition from OFFLINE, Generate an ERROR. 4. Generate a Warning if the Transitions skip. For instance the transitions table has ‘Offline’ to ‘CC1_2’ and so it skips CC1_1. This is an acceptable possibility, but the resource needs to be notified of it because they would not be in RUC until the CC1_2 configuration, in this case would only be in RUC with both units available, not just the single unit associated to CC1_1. 5) Generate a Warning if the Transition is missing for a Configuration
CC | Configuration Code To | [5 empty] | UPDATE 02/2012 | CC Transitions | List | TRANSITIONS | CONFIGCODE_FROM |  | 1.Each configuration in CC2 Transitions except Offline needs to be defined in CC2 Config. 2.Each configuration in CC2 Transitions including Offline can be reached. Each configuration in CC2 Transitions including Offline can reach at least one of the other configurations including Offline 3. 1.If a RARF is submitted that does not have the first Transition from OFFLINE, Generate an ERROR. 4. Generate a Warning if the Transitions skip. For instance the transitions table has ‘Offline’ to ‘CC1_2’ and so it skips CC1_1. This is an acceptable possibility, but the resource needs to be notified of it because they would not be in RUC until the CC1_2 configuration, in this case would only be in RUC with both units available, not just the single unit associated to CC1_1. 5. Generate a Warning if the Transition is missing for a Configuration
CC | Operational Configurations (Test_CC1_X to Test_CC1_X) | [5 empty] | REMOVE | CC1 Transitions |  |  |  |  | 1.If CC1 Transitions to CC2 , CC2 should be registered as a Configuration. 2.Each configuration in CC1 Transitions including Offline can be reached. Each configuration in CC1 Transitions including Offline can reach at least one of the other configurations including Offline . 3.Values allowed are X for Main Transition , A for Alternate Transition ,Null for Non Transition 4. 1.If a RARF is submitted that does not have the first Transition from OFFLINE, Generate an ERROR. 5. Generate a Warning if the Transitions skip. For instance the transitions table has ‘Offline’ to ‘CC1_2’ and so it skips CC1_1. This is an acceptable possibility, but the resource needs to be notified of it because they would not be in RUC until the CC1_2 configuration, in this case would only be in RUC with both units available, not just the single unit associated to CC1_1. 6) Generate a Warning if the Transition is missing for a Configuration | R | Character | B,DVB | Lin Xu/ Jamil Daouk | EMS,MMS,NMMS
CC | CC2 Transitions | [5 empty] | REMOVE | CC2 Transitions |  | Not in table | Not in table |  | CC2 Transitions tab is conditional. Required for only Combined Cycle Generation Resources | C |  |  | RARF Guide Version 4.0 | EMS,MMS
CC | Operating Transitions From offline 1-30 to offline 1-30 | [5 empty] | REMOVE | CC2 Transitions |  |  |  |  | 1.Each configuration in CC2 Transitions except Offline needs to be defined in CC2 Config. 2.Each configuration in CC2 Transitions including Offline can be reached. Each configuration in CC2 Transitions including Offline can reach at least one of the other configurations including Offline 3. 1.If a RARF is submitted that does not have the first Transition from OFFLINE, Generate an ERROR. 4. Generate a Warning if the Transitions skip. For instance the transitions table has ‘Offline’ to ‘CC1_2’ and so it skips CC1_1. This is an acceptable possibility, but the resource needs to be notified of it because they would not be in RUC until the CC1_2 configuration, in this case would only be in RUC with both units available, not just the single unit associated to CC1_1. 5. Generate a Warning if the Transition is missing for a Configuration | C |  | B,DVB | Lin Xu | EMS,MMS
CC | CC3 Transitions | [5 empty] | REMOVE | CC3 Transitions |  | Not in table | Not in table |  | CC3 Transitions tab is conditional. Required for only Combined Cycle Generation Resources | C |  |  | RARF Guide Version 4.0
CC | Operating Transitions From offline 1-30 to offline 1-30 | [5 empty] | REMOVE | CC3 Transitions |  |  |  |  | 1.Each configuration in CC3 Transitions except Offline needs to be defined in CC1 Config. 2.Each configuration in CC3 Transitions including Offline can be reached. Each configuration in CC3 Transitions including Offline can reach at least one of the other configurations including Offline 3. 1.If a RARF is submitted that does not have the first Transition from OFFLINE, Generate an ERROR. 4. Generate a Warning if the Transitions skip. For instance the transitions table has ‘Offline’ to ‘CC1_2’ and so it skips CC1_1. This is an acceptable possibility, but the resource needs to be notified of it because they would not be in RUC until the CC1_2 configuration, in this case would only be in RUC with both units available, not just the single unit associated to CC1_1. 5. Generate a Warning if the Transition is missing for a Configuration | C |  | B,DVB | Lin Xu | EMS,MMS
Generation | Unit Name |  |  | Passed/DCSES |  |  | ADD 02/2012 | Planning - GEN | List | GENERATION | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Generation | Resource Name (Unit Code/Mnemonic) |  |  | Passed/DCSES |  |  | ADD 02/2012 | Planning - GEN | Automatic | GENERATION | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Generation | Direct Axis Sub transient reactance, X"dv (saturated) | [5 empty] | ADD 04/2012 | Planning - GEN | p.u. | GENERATION | DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value.(* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team
Generation | Direct Axis Transient reactance, X'dv (saturated) | [5 empty] | ADD 04/2012 | Planning - GEN | p.u. | GENERATION | DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team
Generation | Positive Sequence Z (saturated) - (R in p.u) | [5 empty] | ADD 04/2012 | Planning - GEN | R in p.u. | GENERATION | POSITIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B | Planning Team | NMMS
Generation | Positive Sequence Z (saturated) - ( X in p.u) | [5 empty] | ADD 04/2012 | Planning - GEN | X in p.u. | GENERATION | POSITIVE_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B | Planning Team | NMMS
Generation | Negative Sequence Z (saturated) - ( R in p.u) | [5 empty] | ADD 04/2012 | Planning - GEN | R in p.u. | GENERATION | NEGATIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B | Planning Team
Generation | Negative Sequence Z (saturated) - ( X in p.u) | [5 empty] | ADD 04/2012 | Planning - GEN | X in p.u. | GENERATION | NEGATIVE_SEQ_Z_X-SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team
Generation | Zero Sequence Z (saturated) - (R in p.u) | [5 empty] | ADD 04/2012 | Planning - GEN | R in p.u. | GENERATION | ZERO_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U | R | Float | B | Planning Team | NMMS
Generation | Zero Sequence Z (saturated) - (X in p.u) | [5 empty] | ADD 04/2012 | Planning - GEN | X in p.u. | GENERATION | ZERO_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team | NMMS
Generation | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | [5 empty] | ADD 04/2012 | Planning - GEN | p.u. | GENERATION | ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Generation | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | [5 empty] | ADD 04/2012 | Planning - GEN | p.u. | GENERATION | ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Generation | Zero Sequence Resistance In P.u. (100 Mva Base) | [5 empty] | ADD 04/2012 | Planning - GEN | p.u. | GENERATION | ZERO_SEQ_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Generation | Zero Sequence Reactance In P.u. (100 Mva Base) | [5 empty] | ADD 04/2012 | Planning - GEN | p.u. | GENERATION | ZERO_SEQ_Reactance_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Generation | Auxilary Load Power Factor | [5 empty] | ADD 04/2012 | Planning - GEN |  | GENERATION | AUX_LOAD_PWR_FACT |  | Between .8 and 1.0 |  |  |  | Planning Team
CC | Unit Name | [5 empty] | ADD 02/2012 | Planning - CC | List | CCUNIT | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
CC | SITE_CODE | [5 empty] | ADD 02/2012 | Planning - CC | Automatic | CCUNIT | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
CC | Resource Name (Unit Code/mnemonic) | [5 empty] | ADD 02/2012 | Planning - CC | Automatic | CCUNIT | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
CC | Does Zero Sequence Z exist? | [5 empty] | ADD 04/2012 | Planning - CC | Y/N | CCUNIT | DOES_ZERO_SEQ_EXIST |  | Drop down list select Y/N | R | Dropdown List |  | Planning Team
CC | Direct Axis Subtransient Reactance, X"dv (saturated) | Corrected |  |  |  |  | ADD 04/2012 | Planning - CC | p.u. | CCUNIT | DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value.(* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team
CC | Direct Axis Transient Reactance, X'dv (saturated) | [5 empty] | ADD 04/2012 | Planning - CC | p.u. | CCUNIT | DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team
CC | Positive Sequence Z (saturated) | [5 empty] | ADD 04/2012 | Planning - CC | R in p.u. | CCUNIT | POSITIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B | Planning Team | NMMS
CC | Positive Sequence Z (saturated) | [5 empty] | ADD 04/2012 | Planning - CC | X in p.u. | CCUNIT | POSITIVE_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B | Planning Team | NMMS
CC | Negative Sequence Z (saturated) | [5 empty] | ADD 04/2012 | Planning - CC | R in p.u. | CCUNIT | NEGATIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B | Planning Team
CC | Negative Sequence Z (saturated) | [5 empty] | ADD 04/2012 | Planning - CC | X in p.u. | CCUNIT | NEGATIVE_SEQ_Z_X-SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team
CC | Zero Sequence Z (saturated) | [5 empty] | ADD 04/2012 | Planning - CC | R in p.u. | CCUNIT | ZERO_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U | R | Float | B | Planning Team | NMMS
CC | Zero Sequence Z (saturated) | [5 empty] | ADD 04/2012 | Planning - CC | X in p.u. | CCUNIT | ZERO_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team | NMMS
CC | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | [5 empty] | ADD 04/2012 | Planning - CC | p.u. | CCUNIT | ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
CC | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | [5 empty] | ADD 04/2012 | Planning - CC | p.u. | CCUNIT | ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
CC | Zero Sequence Resistance In P.u. (100 Mva Base) | [5 empty] | ADD 04/2012 | Planning - CC | p.u. | CCUNIT | ZERO_SEQ_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
CC | Zero Sequence Reactance In P.u. (100 Mva Base) | [5 empty] | ADD 04/2012 | Planning - CC | p.u. | CCUNIT | ZERO_SEQ_Reactance_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
CC | Auxiliary Load Power Factor | [5 empty] | ADD 04/2012 | Planning - CC |  | CCUNIT | AUX_LOAD_PWR_FACT |  | Between .8 and 1.0 |  |  |  | Planning Team
Wind | Unit Name | [5 empty] | ADD 02/2012 | Planning - Wind | List | WIND | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Wind | Resource Name (Unit Code/Mnemonic) | [5 empty] | ADD 02/2012 | Planning - Wind | Automatic | WIND | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
Wind | Type of Turbine | [5 empty] | ADD 02/2012 | Planning - Wind | List | WIND | TURBINE_TYPE |  | Dropdown list | R | Dropdown list
Wind | Does Zero Sequence Z exist? | [5 empty] | ADD 04/2012 | Planning - Wind | Y/N | Wind | DOES_ZERO_SEQ_EXIST |  | Drop down list select Y/N | R | Dropdown List |  | Planning Team
Wind | Direct Axis Sub transient reactance, X"dv (saturated)- (R in p.u) | [5 empty] | ADD 04/2012 | Planning - Wind | p.u. | WIND | DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B | Planning Team
Wind | Direct Axis Transient reactance, X'dv (saturated) - (X in p.u) | [5 empty] | ADD 04/2012 | Planning - Wind | p.u. | WIND | DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B | Planning Team
Wind | Positive Sequence Z (saturated) - (R in p.u) | [5 empty] | ADD 04/2012 | Planning - Wind | R in p.u. | WIND | POSITIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B | Planning Team | NMMS
Wind | Positive Sequence Z (saturated) - ( X in p.u) | [5 empty] | ADD 04/2012 | Planning - Wind | X in p.u. | WIND | POSITIVE_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B | Planning Team | NMMS
Wind | Negative Sequence Z (saturated) - ( R in p.u) | [5 empty] | ADD 04/2012 | Planning - Wind | R in p.u. | WIND | NEGATIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B | Planning Team
Wind | Negative Sequence Z (saturated) - ( X in p.u) | [5 empty] | ADD 04/2012 | Planning - Wind | X in p.u. | WIND | NEGATIVE_SEQ_Z_X-SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team
Wind | Zero Sequence Z (saturated) - (R in p.u) | [5 empty] | ADD 04/2012 | Planning - Wind | R in p.u. | WIND | ZERO_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U | R | Float | B | Planning Team | NMMS
Wind | Zero Sequence Z (saturated) - (X in p.u) | [5 empty] | ADD 04/2012 | Planning - Wind | X in p.u. | WIND | ZERO_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team | NMMS
Wind | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | [5 empty] | ADD 04/2012 | Planning - Wind | p.u. | WIND | ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Wind | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | [5 empty] | ADD 04/2012 | Planning - Wind | p.u. | WIND | ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Wind | Zero Sequence Resistance In P.u. (100 Mva Base) | [5 empty] | ADD 04/2012 | Planning - Wind | p.u. | WIND | ZERO_SEQ_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Wind | Zero Sequence Reactance In P.u. (100 Mva Base) | [5 empty] | ADD 04/2012 | Planning - Wind | p.u. | WIND | ZERO_SEQ_Reactance_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Wind | Average Amount Of Auxiliary Real Power | [5 empty] | ADD 04/2012 | Planning - Wind | MW | WIND | AUX_MWTOTAL |  | 1) This field is optional 2) Data type is float 3) Value must be < Parameters - GEN - High Reasonability Limit 4) Warn if value > (High Reasonability Limit) * .75 5) Error if value > (High Reasonability Limit) * .66 | R | Float | B | Planning Team
Wind | Average Amount Of Auxiliary Reactive Power | [5 empty] | ADD 04/2012 | Planning - Wind | MWAR | WIND | AUX_MVARTOTAL |  | 1) This field is optional 2) Data type is Float 3) Value must be < Reactive Capability - GEN - Maximum Lagging Operating Capability (MVAR) 4) Warn if value > ( Maximum Lagging Operating Capability) * .75 5) Error if value > ( Maximum Lagging Operating Capability) * .66 | R | Float | B | Planning Team
Wind | Auxilary Load Power Factor | [5 empty] | ADD 04/2012 | Planning - Wind |  | WIND | AUX_LOAD_PWR_FACT |  | Between .8 and 1.0 |  |  |  | Planning Team
Wind | Large Motor, Percent Of Total Mw Load | [5 empty] | ADD 04/2012 | Planning - Wind | Percent | WIND | LRG_MTR_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Planning Team
Wind | Small Motor, Percent Of Total Mw Load | [5 empty] | ADD 04/2012 | Planning - Wind | Percent | WIND | SML_MTR_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Planning Team
Wind | Resistive (heating) Load, Percent Of Total Mw Load | [5 empty] | ADD 04/2012 | Planning - Wind | Percent | WIND | RESISTIVE_LOAD_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Planning Team
Wind | Discharge Lighting, Percent Of Total Mw Load | [5 empty] | ADD 04/2012 | Planning - Wind | Percent | WIND | DISCHARGE LIGHT_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Planning Team
Wind | Other, Percent Of Total Mw Load | [5 empty] | ADD 04/2012 | Planning - Wind | Percent | WIND | OTH_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Planning Team
Wind | Large Motor, Percent Of Total Mvar Load | [5 empty] | ADD 04/2012 | Planning - Wind | Percent | WIND | LRG_MTR_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Planning Team
Wind | Small Motor, Percent Of Total Mvar Load | [5 empty] | ADD 04/2012 | Planning - Wind | Percent | WIND | SML_MTR_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | R | Numeric | B,DVB | Planning Team
Wind | Discharge Lighting, Percent Of Total Mvar Load | [5 empty] | ADD 04/2012 | Planning - Wind | Percent | WIND | DISCHARGE LIGHT_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Planning Team
Wind | Other, Percent Of Total Mvar Load | [5 empty] | ADD 04/2012 | Planning - Wind | Percent | WIND | OTH_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Planning Team
Wind | High Side Voltage Level (nominal) | [5 empty] | ADD 04/2012 | Planning - Wind | Kv | WIND | HIGH_SIDE_VT_LEVL |  | 1) This field is required 2) Data type must be real 3) Generate an Error if not between 345 and 69 | R | Real | B,DVB | Planning Team/Model Adminstration
Wind | Low Side Voltage Level (nominal) | [5 empty] | ADD 04/2012 | Planning - Wind | KV | WIND | LOW_SIDE_VT_LEVL |  | 1) This field is required 2) Data type must be real 3) Generate an Error if not < 69 | R | Real | B,DVB | Planning Team/Model Adminstration
Wind | High Side Voltage Connection - Wye / Wye - Grounded / Delta | [5 empty] | ADD 04/2012 | Planning - Wind | List | WIND | HIGH_SIDE_VT_CONNT |  | 1) This field is required 2) Data type must be from list 3) Generate an Error if blank | R | Real | B,DVB | Planning Team/Model Adminstration
Wind | Low Side Voltage Connection - Wye / Wye - Grounded / Delta | [5 empty] | ADD 04/2012 | Planning - Wind | List | WIND | LOW_SIDE_VT_CONNT |  | 1) This field is required 2) Data type must be from list 3) Generate an Error if blank | R | Real | B,DVB | Planning Team/Model Adminstration
Wind | Impedance Z | [5 empty] | ADD 04/2012 | Planning - Wind | p.u. | WIND | IMPEDANCE_Z |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0 | R | Real | B,DVB | Planning Team/Model Adminstration
Wind | X/r Ratio | [5 empty] | ADD 04/2012 | Planning - Wind |  | WIND | X_R_RATIO |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 1 | R | Real | B,DVB | Planning Team/Model Adminstration
Wind | Zero Sequence Z | [5 empty] | ADD 04/2012 | Planning - Wind | p.u. | WIND | ZERO_SEQ_Z |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0 | R | Real | B,DVB | Planning Team/Model Adminstration
Wind | Zero Sequence X/r Ratio | [5 empty] | ADD 04/2012 | Planning - Wind |  | WIND | ZERO_SEQ_X_R_RATIO |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 1 | R | Real | B,DVB | Planning Team/Model Adminstration
Wind | Base Mva For Transformer Data | [5 empty] | ADD 04/2012 | Planning - Wind | MVA | WIND | BASE_MVA_TRANSFORMER_DATA |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank, Generate Warning if > 2000 | R | Real | B,DVB | Planning Team/Model Adminstration
Generation | Unit Name |  |  | Removed Field from RARF form after sheet was split |  |  | ADD 02/2012 | Private Network - Site - GEN | List | GENERATION | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Generation | Site Code |  |  | Passed/DCSES |  |  | ADD 02/2012 | Private Network - Site - GEN | Automatic | SITECODES | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
Generation | Unit Name |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 02/2012 | Private Network - Unit - GEN | List | GENERATION | UNIT_NAME |  | 1. This field is not null. Data type: Character. | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Generation | SITE_CODE |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 02/2012 | Private Network - Unit - GEN |  | GENERATION | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
Generation | Resource Name (Unit Code/Mnemonic) |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 02/2012 | Private Network - Unit - GEN | Automatic | SITECODES | UNIT_CODE | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
CC | SITE CODE | REMOVED FROM CC FORM |  |  |  |  | ADD 02/2012 | Private Network - Site - CC | Automatic | CCUNIT | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
CC | SITE CODE | [5 empty] | ADD 02/2012 | Private Network - Unit - CC | Automatic | CCUNIT | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
CC | Resource Name (Unit Code/Mnemonic) | [5 empty] | ADD 02/2012 | Private Network - Unit - CC | Automatic | CCUNIT | UNIT_CODE | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
Wind | Unit Name | [5 empty] | ADD 02/2012 | Private Network - Site - Wind | List | WIND | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Wind | Site Code | [5 empty] | ADD 02/2012 | Private Network - Site - Wind | Automatic | SITECODES | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
Wind | Unit Name | [5 empty] | ADD 02/2012 | Private Network - Unit - Wind | List | WIND | UNIT_NAME | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | 1. This field is not null. Data type: Character. | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Wind | SITE_CODE | [5 empty] | ADD 02/2012 | Private Network - Unit - Wind | Automatic | WIND | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
Wind | Resource Name (Unit Code/Mnemonic) | [5 empty] | ADD 02/2012 | Private Network - Unit - Wind | Automatic | WIND | UNIT_CODE | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
LAAR | Unit Name | [5 empty] | REMOVE | Load Resource Information |  | LOAD_RESOURCES |  |  | This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
LAAR | ESIID Station Name | [5 empty] | REMOVE | Load Resource Information |  | LOAD_RESOURCES |  |  | REMOVE 11/11/2011 This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
LAAR | ESIID Station Code | [5 empty] | REMOVE | Load Resource Information |  | LOAD_RESOURCES |  |  | REMOVE 11/11/2011 This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
LAAR | Transmission Station Load Name in Network Operations Model |  | ADD 04/2012 |  |  |  | ADD 04/2012 | Load Resource Information | (all caps) | LOAD_RESOURCES | TRANS_STAT_LOAD_NAM_NOM |  | ALL CAPS
LAAR | QSE Name | [5 empty] | REMOVE | Load Resource Information |  | LOAD_RESOURCES |  |  | REMOVE 11/11/2011 | R | Character | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 | NMMS
LAAR | QSE Duns Number | [5 empty] | REMOVE | Load Resource Information |  | LOAD_RESOURCES |  |  | REMOVE 11/11/2011 | R | Integer | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 | NMMS
LAAR | High Set Under-frequency Relay (UFR) Setting | [5 empty] | REMOVE | Load Resource Information |  | LOAD_RESOURCES |  |  | REMOVE 11/11/2011 This field is not null. This field is conditional: Required for UFR Load Resource Type and CLR Load Resource Type where the flag is checked stating that the Resource can operate as UFR. In that case the value should not be less than 59.7 Hz. (An Interruptible Load Resource Type would not enter a value, nor would a Load Resource that was just a CLR.) | C | Numeric | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
LAAR | Maximum Interruptible Load MW |  | Field needs to be added to RARF Audit and Delta |  |  |  | ADD 02/2012 | Load Resource Information | MW | LOAD_RESOURCES | MAX_INT_LOAD_MW |  | Maximum POD Total Load >= Summer Interruptible MW.This field is not null and should be a Number
LAAR | Summer Interruptible MW |  | Created defect 20114 to remove field on Load Resource Table |  |  |  | REMOVE | Load Resource Information |  | LOAD_RESOURCES |  |  | REMOVE 11/11/2011 Maximum POD Total Load >= Summer Interruptible MW.This field is not null and should be a Number | R | Numeric | B,DVB | Lin Xu | MMS
LAAR | Winter Interruptible MW |  | Created defect 20114 to remove field on Load Resource Table |  |  |  | REMOVE | Load Resource Information |  | LOAD_RESOURCES |  |  | REMOVE 11/11/2011 Maximum POD Total Load >= Winter Interruptible MW. This field is not null and should be a Number | R | Numeric | B,DVB | Lin Xu | MMS
Generation | Unit Name |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 02/2012 | Protection - GEN | List | GENERATION | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Generation | Resource Name (Unit Code/Mnemonic) |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 02/2012 | Protection - GEN | Automatic | GENERATION | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Generation | Unit Name | [5 empty] | ADD 02/2012 | Protection - CC | List | CCUNIT | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Generation | SITE_CODE | [5 empty] | ADD 02/2012 | Protection - CC | Automatic | CCUNIT | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
Generation | Resource Name (Unit Code/mnemonic) | [5 empty] | ADD 02/2012 | Protection - CC | Automatic | CCUNIT | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Wind | Unit Name | [5 empty] | ADD 02/2012 | Protection - Wind | List | WIND | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Wind | SITE_CODE | [5 empty] | ADD 02/2012 | Protection - Wind | Automatic | WIND | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk
Wind | Resource Name (Unit Code/Mnemonic) | [5 empty] | ADD 02/2012 | Protection - Wind | Automatic | WIND | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
Wind | Cable Type | [5 empty] | ADD 04/2012 | Collector System - Wind |  | COLLECTOR_SYS | CABLE_TYPE |  | 1) This field is required 2) Data type must string 3) Generate an Warning if blank | R | String | B,DVB
Wind | Voltage Level kV | [5 empty] | ADD 04/2012 | Collector System - Wind | kv | COLLECTOR_SYS | VT_LEVEL_KV |  | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | T | Float | B/DVE
Wind | R/kft | [5 empty] | ADD 04/2012 | Collector System - Wind | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_R_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank | R | Float | B,DVB
Wind | X/kft | [5 empty] | ADD 04/2012 | Collector System - Wind | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_X_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank | R | String | B,DVB
Wind | Charging Bc/kft | [5 empty] | ADD 04/2012 | Collector System - Wind | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_CHRG_BC_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank | R | Float | B,DVB
Wind | R0/kft | [5 empty] | ADD 04/2012 | Collector System - Wind | (p.u. on 100 MVA base) | COLLECTOR_SYS | ZERO_R0_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank | R | Float | B,DVB
Wind | X0/kft | [5 empty] | ADD 04/2012 | Collector System - Wind | (p.u. on 100 MVA base) | COLLECTOR_SYS | ZERO_X0_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank | R | Float | B,DVB
Wind | Cable Type | [5 empty] | ADD 04/2012 | Collector System-Wind Seg Data | List | CABLE_SEG_DATA | CABLE_TYPE |  | 1) This field is required 2) Data type must string 3) Generate an Warning if blank | R | String | B,DVB
Wind | From | [5 empty] | ADD 04/2012 | Collector System-Wind Seg Data | Integer | CABLE_SEG_DATA | CABLE_SEG_DATA_FROM |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank | R | Integer | B,DVB
Wind | To | [5 empty] | ADD 04/2012 | Collector System-Wind Seg Data | Integer | CABLE_SEG_DATA | CABLE_SEG_DATA_TO |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank | R | Integer | B,DVB
Wind | Circuit Number | [5 empty] | ADD 04/2012 | Collector System-Wind Seg Data | Integer | CABLE_SEG_DATA | CIRCT_NUM |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank | R | Integer | B,DVB
Wind | Voltage Level | [5 empty] | ADD 04/2012 | Collector System-Wind Seg Data | kV | CABLE_SEG_DATA | VT_LEVL |  | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0. | T | Float | B/DVE
Wind | Cable Segment Length | [5 empty] | ADD 04/2012 | Collector System-Wind Seg Data | in kft | CABLE_SEG_DATA | CABLE_SEG_LENTH |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank | R | Float | B,DVB
Wind | Number of Turbines on cable segment | [5 empty] | ADD 04/2012 | Collector System-Wind Seg Data | Integer | CABLE_SEG_DATA | NUM_TURBIN_ON_CABLE_SEG |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank | R | Integer | B,DVB
Transmission | Zero Sequence Line Resistance In P.u. (100mva Base) | [5 empty] | ADD 04/2012 | Line Data | p.u. | LINE | ZERO_SEQ_LINE_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R
Transmission | Zero Sequence Line Reactance In P.u. (100mva Base) | [5 empty] | ADD 04/2012 | Line Data | p.u. | LINE | ZERO_SEQ_LINE_REACTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R
Transmission | Zero Sequence Charging Susceptance In P.u. (100mva Base) | [5 empty] | ADD 04/2012 | Line Data | p.u. | LINE | ZERO_ SEQ_ CHRG_ SUSECPTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R
Transmission | Line Code | [5 empty] | ADD 02/2012 | Line Data | List | LINE | LINE_CODE |  | Concantenate (Site Code_Substation Code_ERCOT_LINE_NAME) | R
Transmission | Line Name | [5 empty] | ADD 02/2012 | Line Temperture | Automatic | LINE_TEMP | ERCOT_LINE_NAME |  | 1) This field is required 2) This field may not have any special characters, except an underscore "_" and a dash "-" 3) Warn if > 14 characters. Warning! ERCOT Line Name () should not be > 14 characters long or the name will be truncated in the model which requires uniqueness. 4) Line Name can not be duplicated in a Station
Transmission | Line Code | [5 empty] | ADD 02/2012 | Line Temperture | Automatic | LINE_TEMP | LINE_CODE |  | Concantenate (Site Code_Substation Code_ERCOT_LINE_NAME)
Transmission | Line Rating | [5 empty] | ADD 02/2012 | Line Temperture | (Static or Dynamic) | LINE_TEMP | LINE_RATING |  | 1) Field is required 2) Field must be from the following list: STATIC, DYNAMIC | T | Alpha | B | Joel Koepke
Transmission | Planning Rate C | [5 empty] | ADD 04/2012 | Line Temperture | MVA | LINE_TEMP | PLANNING_RATE_C |  | Must by >= Emergency Rating (2HR Rating) |  |  |  | Model Adminstration
Transmission | Switch Code | [5 empty] | UPDATE 02/2012 | Breaker Switch Data | Automatic | BREAKER_SWITCH | BREAKER_CODE | SUBSTATION_CODE | Concantenate (Site Code_Substation Code_Switch Name)
Transmission | Continuous Ratings | [5 empty] | ADD 04/2012 | Breaker Switch Data | MVA | BREAKER_SWITCH | CONTINUOUS_RTG |  | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be <= Nominal (Static) - 2-hr Emergency Rating 3) Value must be <= Nominal (Static) - 15-min Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - Continuous Rating AND value must be >= 115 °F Continuous Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Integer | B/DVE | Model Adminstration
Transmission | 2HR Rating Emergency Rating | [5 empty] | ADD 04/2012 | Breaker Switch Data | MVA | BREAKER_SWITCH | EMGCY_RTG_2HR |  | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be >= Nominal (Static) - Continuous Rating 3) Value must be <= Nominal (Static) - 15-min Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 2-hr Emergency Rating AND value must be >= 115 °F 2-hr Emergency Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Integer | B/DVE | Model Adminstration
Transmission | 15 Min Rating | [5 empty] | ADD 04/2012 | Breaker Switch Data | MVA | BREAKER_SWITCH | RTG_15MIN |  | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be >= Nominal (Static) - Continuous Rating 3) Value must be >= Nominal (Static) - 2-hr Emergency Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 15-min Rating AND value must be >= 115 °F 15-min Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Integer | B/DVE | Model Adminstration
Transmission | ERCOT Station Code Mnemonic | [5 empty] | UPDATE 02/2012 | Capacitor and Reactor Data | enter all caps | CAPREACT | SUBSTATION_CODE |  | 1) This field is required 2) Must match ERCOT records (unless new).Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3)This field may not have any special characters, except an underscore "_" and a dash "-" 4) Value must be <= 8 characters. Warning! Station Code () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) substation code should be in Upper case letters. Generate an error if the rule fails | T | Alpha | B | Joel Koepke
Transmission | Device Code | [5 empty] | UPDATE 02/2012 | Capacitor and Reactor Data | Automatic | CAPREACT | DEVICE_CODE |  | Concantenate (Site Code_Substation Code_Device Code)
Transmission | Zero Sequence Reactance Increment In P.u. | [5 empty] | ADD 04/2012 | Capacitor and Reactor Data | p.u. | CAPREACT | ZERO_SEQ_REACTANCE_INCRMENT_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Model Adminstration
Transmission | SVC CODE | [5 empty] | UPDATE 02/2012 | Static Var Compensator Data | Automatic | STATIC_VAR_COMP | SVC_CODE |  | Concantenate (Site Code_Substation Code_SVC Name)
Transmission | Fixed MVAR (VAR injection at nominal voltage) | [5 empty] | UPDATE 02/2012 | Static Var Compensator Data | MVAR | STATIC_VAR_COMP | FIXED_MVAR |  | 1) This field is required | T | Float | B/DVE | Joel Koepke/Planning 11/08/11
Transmission | Minimum Admittance Limits (100 MVA Base) | [5 empty] | UPDATE 02/2012 | Static Var Compensator Data | p.u. | STATIC_VAR_COMP | MIN_ADM_LIMIT |  | 1) This field is required 2) Value must be <= Maximum Admittance | T | Float | B/DVE | Joel Koepke/Planning 11/08/11
Transmission | Maximum Admittance Limits (100 MVA Base) | [5 empty] | UPDATE 02/2012 | Static Var Compensator Data | p.u. | STATIC_VAR_COMP | MAX_ADM_LIMIT |  | 1) This field is required 2) Value must be >= Minimum Admittance | T | Float | B/DVE | Joel Koepke/Planning 11/08/11
Transmission | Maximum Threshold (post contingency) Reactive Power Limits | [5 empty] | UPDATE 02/2012 | Static Var Compensator Data | MVAR | STATIC_VAR_COMP | MAX_THRESH_REACT |  | 1) This field is required 2) Value must be <= Maximum Steady State Reactive Power Limits | T | Float | B/DVE | Joel Koepke/Planning 11/08/11
Transmission | Minimum Voltage Threshold | [5 empty] | UPDATE 02/2012 | Static Var Compensator Data | kV | STATIC_VAR_COMP | MIN_VOLT_THRESH |  | 1) This field is required 2) Value must be <= Maximum Voltage Threshold (100 MVA Base) 3) The value may not exceed 370 3) The value must be > 0 4) Warn if Max / Min exceed 50% of one another | T | Float | B/DVE | Joel Koepke/Planning 11/08/11
Transmission | Maximum Voltage Threshold | [5 empty] | UPDATE 02/2012 | Static Var Compensator Data | kV | STATIC_VAR_COMP | MAX_VOLT_THRESH |  | 1) This field is required 2) Value must be >= Minimum Voltage Threshold (100 MVA Base) 3) The value may not exceed 370 4) The value must be > 0 5) Warn if Max / Min exceed 50% of one another | T | Float | B/DVE | Joel Koepke/Planning 11/08/11
Transmission | SD CODE | [5 empty] | UPDATE 02/2012 | Series Device Data | Automatic |  |  |  | Concantenate (Site Code_Substation Code_SD Name)
Transmission | Transformer Code | [5 empty] | UPDATE 02/2012 | Transformer Data | Automatic | TRANSFORMER | TRANSFORMER_CODE |  | Concantenate (Site Code_Substation Code_Transformer Name)
Transmission | Zero Sequence Data - Winding Connection Code (1-8) | [5 empty] | ADD 04/2012 | Transformer Data | p.u. | TRANSFORMER | ZERO_SEQ_DATA_WINDING_CON_CODE |  | 1) This field is optional 2) Data type must be string | R | real | B,DVB | Model Adminstration
Transmission | Zero Sequence Grounding Resistance For An Impedance Grounded Transformer In P.u. (100 Mva Base) | [5 empty] | ADD 04/2012 | Transformer Data | p.u. | TRANSFORMER | ZERO_SEQ_GRUND_RESISTANCE_IMPEDANCE_GRUND_TRANS_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Model Adminstration
Transmission | Zero Sequence Grounding Reactance For An Impedance Grounded Transformer In P.u. (100 Mva Base) | [5 empty] | ADD 04/2012 | Transformer Data | p.u. | TRANSFORMER | ZERO_SEQ_GRUND_REACTANCE_IMPEDANCE_GRUND_TRANS_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Model Adminstration
Transmission | Zero Sequence Resistance In P.u. (100 Mva Base) | [5 empty] | ADD 04/2012 | Transformer Data | p.u. | TRANSFORMER | ZERO_SEQ_TRANS_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Model Adminstration
Transmission | Zero Sequence Reactance In P.u. (100 Mva Base) | [5 empty] | ADD 04/2012 | Transformer Data | p.u. | TRANSFORMER | ZERO_SEQ_TRANS_REACTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Model Adminstration
Transmission | Positive Sequence Resistance (100 MVA Base) | [5 empty] | UPDATE 02/2012 | Transformer Data | p.u. | TRANSFORMER | SERIES_ RESIST |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Model Adminstration
Transmission | Positive Sequence Reactance (100 MVA Base) | [5 empty] | UPDATE 02/2012 | Transformer Data | p.u. | TRANSFORMER | SERIES_ REACT |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Model Adminstration
Transmission | Transformer Code | [5 empty] | Added to RARF Form for 02/2012 | Transformer Tap Settings | Automatic | TRANSFORMER_TAP_SETTINGS | TRANSFORMER_CODE |  | Concantenate (Site Code_Substation Code_Transformer Name)
Transmission | High-Low Flag | [5 empty] | Added to RARF Form for 02/2012 | Transformer Tap Settings | List | TRANSFORMER_TAP_SETTINGS | LOW_HIGH_FLG |  | 1) This field is conditioally reguired.This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be of the following: High or Low
Transmission | Load Code | [5 empty] | UPDATE 02/2012 | Load Data |  | LOADS | LOAD_CODE |  | Concantenate (Site Code_Substation Code_Lode Name
Transmission | Station Code | [5 empty] | ADD 04/2012 | PUN Load |  | PUN_LOAD | SUBSTATION_CODE
Transmission | Load Name | [5 empty] | ADD 04/2012 | PUN Load |  | PUN_LOAD | LOAD_NAME |  | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Value should following the following convention SiteCode_LoadName. Load Name (Load Name) should be as it appears in the ERCOT Model | L | Alpha | B
Transmission | Load Code | [5 empty] | ADD 04/2012 | PUN Load |  | PUN_LOAD | LOAD_CODE
Transmission | Hour Ending | [5 empty] | ADD 04/2012 | PUN Load |  | PUN_LOAD | HR_ENDING
Transmission | Day of Week | [5 empty] | ADD 04/2012 | PUN Load |  | PUN_LOAD | DAY_WEEK |  | 1) These fields are conditionally required if "Private Network - Private Network?" = 'Y' and for each Load identified 2) Value must be >= 0 (for zero load, place a 0 in that space)
Transmission | MW | [5 empty] | ADD 04/2012 | PUN Load |  | PUN_LOAD | MW

## ESG Validations (hidden)
Field/Section Type: R- Required( Not null),O= Optional ,C =Conditional
Validation Type: B = Basic Validation , DVB = Data Validation based on Business Rules , DVE = Data Validation with the existing record in ERCOT
Format /Data type: Numeric, Integer , Character, Date, Dropdown List
Source--> Represents the source of the Validation Rules
RARF DATA FIELD | RARF FORM TYPE | Corrections and Updates | LAAR VALIDATIONS ITEST | Validation and Reports ITEST GEN - 01/30/2012 | Validation ITEST CC - 01/30/2012 | ITEST Transmission | Change Description | RARF Tab | Label | TABLE | DB Field | EXCEL | Business Rules/Basic UI validations | Field/ Tab Type | Data type | Validation Type | Source | Destination Application
General and Site Information | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | Not in table | Not in table |  | This tab is Required for all Resource Entities (Load and Generation Resources) | R |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
This submittal is for | GEN, CC, Wind, ESG and Solar | Updated 03/09/2012 validation rule to match view | [5 empty] | General and Site Information |  | SITECODES | SUBMIT_REASON | Not null. Select from the list: New Site, Revision, Addition of Units, Deletion of Units | Not null. Select from the list: New Site, Revision, Addition of Unit(s), Deletion of Unit(s)* | R | Dropdown List | B,DVB
Submittal Information | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | Not in table | Not in table | Not null. Select from the list: New Site, Revision, Addition of Units, Deletion of Units | Not null. Select from the list: New Site, Revision, Addition of Units, Deletion of Units | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 4/RARF Guide version 4.0/ Angela Moy
Date Form Completed: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | SITECODES | FORM_COMP_DT | Optional | Not null. Equal to the System Date. Date Format should be mm/dd/yyyy | R | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Resource Entity Submitting Form: | GEN, CC, Wind, ESG and Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | General and Site Information |  | RE_RARF | RE_NAME | 1. Not null. 2. Name must match ERCOT records (SIEBEL) | This field should not be null. Resource Entity Name must match with the data existing in Siebel. Resource Entity Name should not allow any special characters except spaces 1.This field is not null. 2. All should be capital letters 3.No Special characters except spaces and dashes. | R | Character | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
Resource Entity DUNS #: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | SITECODES & RE_RARF | RE_DUNS | 1. Not null. 2. DUNS number must match ERCOT records (SIEBEL) | Not null. Data type should be varchar (as sometimes the value contains # with a leading zero). Duns# is either 9 digit or 13 digit .Should match with RE Duns# IN Siebel | R | Character | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk
Site Information | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | Not in table | Not in table |  | This tab is Conditional: Required if the Generation Type is ' WIND or CC or GEN' , where GEN is non-cc non-wind generation resources. This tab is not required for Load Resources. | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,MMS,Lodestar
Resource Site Name: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | SITECODES | SITE_NAME | 1. Not null. 2. Validate with ERCOT records (Lodestar). 3. All should be capital letters | 1.This field is not null. Validate with the existing record in ERCOT?? 2. All should be capital letters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | EMS,Lodestar
Resource Site Code: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | SITECODES | SITE_CODE | 1. Not null. 2. Validate with ERCOT records (Lodestar). 3. All should be capital letters | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk
Street Address: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | SITECODES | STREET_ADDRESS | Not null | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
City: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | SITECODES | CITY | Not null | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
State | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | SITECODES | STATE | Not null | This is Required field (can not be null) Data type should be character, no numbers or commas are allowed. | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
Zip Code | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | SITECODES | ZIPCODE | Not null | This is a Required field and can not be null. Only numbers are allowed | R | Number | B |  | Siebel
County: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | SITECODES | COUNTY | Not null | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
Site In-Service Date: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | SITECODES | SITE_IN_SRVC_DT | 1. Must be earlier than Site-Stop Service Date. 2. mm/dd/yy format. 3. Not null. | Site-In Service Date is earlier than Site-Stop Service Date. Enter the date in mm/dd/yy format. This field is not null. | R | Date | B,DVB | Lin Xu | Lodestar,MMS
Site Stop Service Date: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | SITECODES | SITE_STOP_SRVC_DT | 1. Must be later than Site In-Service Date. 2. mm/dd/yy format. 3. Not null. | Site Stop Service Date should be later than Site-In Service Date. Format is mm/dd/yyy. This field is optional. NA is not valid , Leave it blank if not applicable. | O | Date | B,DVB | Lin Xu | Lodestar,MMS
Congestion Management Zone for 2003: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | SITECODES | CMZ_2003 | 1. Select from the list: North,South,Houston,West. 2. Not Null | Select from the list: North,South,Houston,West. This field is Required | O | Dropdown List | B,DVB | RARF Glossary Version 4.0/ Angela Moy
Resource owned by NOIE? | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | SITECODES | RE_OWNED_NOIE_FLG | 1. Select from the list: Y or N 2. Not Null | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Is Resource behind a NOIE Settlement Meter Point? | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | SITECODES | RE_BHND_NOIE_SMP_FLG | 1. Select from the list: Y or N 2. Not Null | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Number of EPS Primary meters: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | SITECODES | NUM_EPS_METERS | Not null | This field is required and it should be an integer | R | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Primary Contact (name of person ERCOT can contact with questions regarding this form) | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | Not in table | Not in table
Printed Name: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | SITECODES | NAME_PC | Not null | Not null. Validate that the Authorized rep has valid digital certificate to access the User Interface | R | Character | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
Title: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | SITECODES | TITLE_PC | Not null | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Phone Number: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | SITECODES | PHONE_PC | Not null | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
E-mail Address: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | SITECODES | EMAIL_PC | Not null | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Fax Number: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | SITECODES | FAX_PC | Optional | Optional | O | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Secondary Contact (if available) | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | Not in table | Not in table |  | Optional
Printed Name: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | Not in table | Not in table |  | Optional
Title: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | Not in table | Not in table |  | Optional
Phone Number: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | Not in table | Not in table |  | Optional
E-mail Address: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | Not in table | Not in table |  | Optional
Fax Number: | GEN, CC, Wind, ESG and Solar | [6 empty] | General and Site Information |  | Not in table | Not in table |  | Optional
GEN Load Split -ESIID | GEN, CC, Wind, ESG and Solar | [6 empty] | GEN Load Split -ESIID |  | Not in table | Not in table
GENERATION SITE LOAD DETAILS | GEN, CC, Wind, ESG and Solar | [6 empty] | GEN Load Split -ESIID |  | Not in table | Not in table
ESIID_NUMBER | GEN, CC, Wind, ESG and Solar |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  | ADD 02/2012 to RARF FORM | GEN Load Split - ESIID |  | SITE_LOAD_SPLIT | ESIID_NUMBER | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2. Must have minimum of 2 ESI ID's entered 3. Data type is character | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Generate ESIID Number + 1 (ex. ESIID_1, ESIID_2, ESIID_3)
SITECODE_ESIID | GEN, CC, Wind, ESG and Solar |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  | ADD 02/2012 to RARF FORM | GEN Load Split - ESIID |  | SITE_LOAD_SPLIT | SITECODE_ESIID | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2.Concantanate SITE_CODE and ESIID_NUMBER | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Concantanate SITECODE_ESIID_Number
Generation Load Split? | GEN, CC, Wind, ESG and Solar | Corrected 02/29/2012 | [5 empty] | GEN Load Split - ESIID | Y/N | SITECODES & SITE_LOAD_SPLIT | GEN_LOAD_SPLIT_FLG | 1.This field is conditional. Required only if Generation Load Split is 'N'. 2. Not Required of Resource Behind NOIE Settlement point is 'Y' 2. Data type is character | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
ERCOT Read Meter? | GEN, CC, Wind, ESG and Solar | [6 empty] | GEN Load Split - ESIID | Y/N | SITECODES | ERCOT_READ_FLG | 1. Select from the list: Y or N 2. Not Null | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
SITECODE | GEN, CC, Wind, ESG and Solar |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  | ADD 02/2012 | GEN Load Split - ESIID | Automatic | SITECODES & SITE_LOAD_SPLIT | SITE_CODE | 1. Not null. 2. Validate with ERCOT records (Lodestar). 3. All should be capital letters | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk
ESI ID: | GEN, CC, Wind, ESG and Solar | Corrected |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  | UPDATE 02/2012 | GEN Load Split - ESIID |  | SITECODES & SITE_LOAD_SPLIT | ESI_ID |  | 1.This field is Required. 2.Data type is character 3.If Generation Load Split is 'N' only 1 ESIID is required. 4. If Generation Load Split is 'Y' more the 1 ESIID is required. | C | Character | B | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
TDSP Providing Service To Resource: | GEN, CC, Wind, ESG and Solar | Corrected | [5 empty] | GEN Load Split - ESIID | List | SITECODES & SITE_LOAD_SPLIT | TDSP_PROVIDING_SVC | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Select From drop down list provided. | This field is conditional. Required only if If the Generation Load Split question is answered as 'N' . Validate with the existing record in ERCOT?? | C | Character | B,DVE | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
TDSP DUNS Number: | GEN, CC, Wind, ESG and Solar | 03/09/2012 Updated Validation | [5 empty] | GEN Load Split - ESIID | Automatic | SITECODES & SITE_LOAD_SPLIT | TDSP_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Prepopulated with DUNS of TDSP provided in cell above | This field is conditional. Required only if If the Generation Load Split question is answered as 'N' . It should be either 9 or 13 digit number 1. Not null 2. Must match with the data existing in Siebel 3. Data type: varchar (as sometimes the value contains # with a leading zero) 4. Either a 9 or 13 digit DUNS number | R | Integer | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 | Lodestar
Fixed Load Splitting % | GEN, CC, Wind, ESG and Solar | [6 empty] | GEN Load Split - ESIID | Percent | SITE_LOAD_SPLIT | FIXED_LD_SPLIT | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2. Must have minimum of 2 ESI ID's entered | 1.This field is optional/conditional. Required only if Gen Site is split among multiple ESI Id's.If entered, cross check the data with Lodestar. 2. Sum of the Fixed Load Splitting % (corresponding to each ESIID) should be 100. Generate an error if the rule fails | C/O | Numeric | B | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 | Lodestar
Load Serving Entity | GEN, CC, Wind, ESG and Solar | [6 empty] | GEN Load Split - ESIID | List | SITE_LOAD_SPLIT | COMP_RETAILER | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Select From drop down list provided. | This field is optional/conditional. Required only if Gen Site is split among multiple ESI Id's. | C | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
Load Serving Entity Duns# | GEN, CC, Wind, ESG and Solar | [6 empty] | GEN Load Split - ESIID | Automatic | SITE_LOAD_SPLIT | COMP_RETAILER_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Prepopulated with DUNS of Competitive Retailer provided in cell above | This field is optional/conditional. Required only if Gen Site is split among multiple ESI Id's. If entered it should be either 9 or 13 digit number AND should match with the existing record in Lodestar? | C | Integer | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 | Lodestar
Unit Info - GEN | Generation | [6 empty] | Unit Info - GEN |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type Selected is 'GEN' where GEN is non-CC non-wind Generation Resources. | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,MMS,NMMS
GENERATOR DETAILS | Generation | [6 empty] | Unit Info - GEN |  | Not in table | Not in table
Unit Name | Generation | [6 empty] | Unit Info - GEN | All Caps | GENERATION | UNIT_NAME | 1. Not Null. 2. Must not exceed 4 characters for Jointly Owned Units 3. Maximum of 8 character allowed | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Generation | [6 empty] | Unit Info - GEN | Automatic | GENERATION | UNIT_CODE | 1. Not Null. 2. Enter Site Code and Unit Name for this field (Sitecode_Unit Name) 3. All letters must be capital | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Non Modeled Generation | Generation | [5 empty] | ADD 04/2012 | Unit Info - GEN | Y/N | GENERATION | NON_MOD_GEN | 1.Select from the list: Y or N 2.Not Null | Select from the list: Y or N | R | Dropdown List | B,DVB
Number of Generators in this Unit? (AGR Only) | Generation | Added field which is needed for PRR437 |  |  |  |  | ADD 04/2012 | Unit Info - GEN |  | GENERATION | NUM_AGR_UNITS
PUC Registration Number | Generation | [6 empty] | Unit Info - GEN |  | GENERATION | PUC_NUM | 1. Optional. | This field is optional. Enter a Valid Number or leave it blank if not applicable | O | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
ERCOT Interconnection Project Number - only new units | Generation | [6 empty] | Unit Info - GEN |  | GENERATION | ERCOT_INTRCONN_PROJ_NUM | 1. Required for new sites only | 1.This field is optional. Required only for new units. Enter a Valid Number or leave it blank if not applicable 2. Cross check with the data entered in the field 'This submittal is for' in General Information Tab. If the value is 'New Site' then only this field is required. | O | Character | B,DVE | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Angela Moy
NERC Number | Generation | [6 empty] | Unit Info - GEN |  | GENERATION | NERC_NUM | 1. Optional. | This field is optional. Enter a Valid Number or leave it blank if not applicable | O | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Qualifying facility | Generation | [6 empty] | Unit Info - GEN | Y/N | GENERATION | QUAL_FACILITY_FLG | 1. Not null. 2. Select Y or N | QF flag is not null. Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/kittiepong | Lodestar
SITE AND UNIT DATES | Generation | [6 empty] | Unit Info - GEN |  | Not in table | Not in table
Transmission Only Date (POI) | Generation | [5 empty] | ADD 04/2012 | Unit Info - GEN | mm/dd/yyyy | GENERATION | TRANS_ONLY_DT | 1. Optional. 2. Format should be: MM/DD/YYYY | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB
Standard Generation Interconnection Agreement (SGIA) Signature Date | Generation | [5 empty] | ADD 04/2012 | Unit Info - GEN | mm/dd/yyyy | GENERATION | SGIA_SIGA_DT | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date. | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date. | R | Date | B/DVB | CDannunzio
Unit Start Date (Model Ready Date) | Generation | 03/13/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Unit Info - GEN | mm/dd/yyyy | GENERATION | UNIT_MRD_ST_DT | 1.This field is not null. Format should be: MM/DD/YYYY 2.Date should be Vaild Data Base Load Date 3.Unit Start Date should be >= Site Start Date ( Site-Information Tab) | This field is optional. Format should be: MM/DD/YYYY
Unit Commercial Date | Generation | [6 empty] | Unit Info - GEN | mm/dd/yyyy | GENERATION | UNIT_START_DT | 1. Not null. 2. Format should be: MM/DD/YYYY 3. Must be equal to or greater than Site In-Service Date. | This field is not null. Format should be: MM/DD/YYYY Unit Start Date should be >= Site Start Date ( Site-Information Tab) | R | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,NMMS
Unit End Date | Generation | [6 empty] | Unit Info - GEN | mm/dd/yyyy | GENERATION | UNIT_END_DT | 1. Not null. 2. Format should be: MM/DD/YYYY 3. Must be greater than Unit Start Date. | This field is optional. Format should be: MM/DD/YYYY | O | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,NMMS
POINT OF INTERCONNECTION | Generation | [6 empty] | Unit Info - GEN |  | Not in table | Not in table
Substation Code/substation Mnemonic | Generation | [5 empty] | ADD 04/2012 | Unit Info - GEN | All Caps | GENERATION | SUBSTAT_CODE_SUB_MNEMONIC | SUBSTAT_CODE_SUB_MNEMONIC | 1) This field is not null (required). Data type must be Character. 2) Must match ERCOT records (unless new). Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" . 4) Must be <= 8 characters. Warning! Substation Code should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) Substation code should be in Upper case letters. Generate an error if the rule fails. | R | Character | B/DVB | CDannunzio
Voltage Level | Generation | [5 empty] | ADD 04/2012 | Unit Info - GEN | kV | GENERATION | VOL_LEV | VOL_LEV | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0. | R | Float | B/DVE | CDannunzio
Pti Bus Number | Generation | [5 empty] | ADD 04/2012 | Unit Info - GEN | # | GENERATION | PTI_BUS_NUM | PTI_BUS_NUM | 1) This field isnot null (required). Data type must be Integer. 2) The value must be > 0. | R | Integer | B/DVB | CDannunzio
FUEL INFORMATION | Generation | [6 empty] | Unit Info - GEN |  | Not in table | Not in table
Primary Fuel Type | Generation |  |  | Passed Validation |  |  | UPDATE 02/2012 | Unit Info - GEN | List | GENERATION | PRIM_FUELTYPE | Select from the list: AB, BFG, BIT, BL, DFO, GEO, JF, KER, LFG, LIG, MSW, NA, NG, NUC, OBG, OBL, OBS, OG, OO, OTH, PC, PG, RFO, SLW, STM, SUB, SUN, T, TDF, WAT, WDL, WDS, WH, WOC This field is not null. | Select from the list: AB, BFG, BIT, BL, DFO, GEO, JF, KER, LFG, LIG, MSW, NA, NG, NUC, OBG, OBL, OBS, OG, OO, OTH, PC, PG, RFO, SLW, STM, SUB, SUN, T, TDF, WAT, WDL, WDS, WH, WOC This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS
Secondary Fuel Type | Generation |  |  | Passed Validation |  |  | UPDATE 02/2012 | Unit Info - GEN | List | GENERATION | SEC_FUELTYPE | Select from the list: AB, BFG, BIT, BL, DFO, GEO, JF, KER, LFG, LIG, MSW, NA, NG, NUC, OBG, OBL, OBS, OG, OO, OTH, PC, PG, RFO, SLW, STM, SUB, SUN, T, TDF, WAT, WDL, WDS, WH, WOC. This field is not null. | Select from the list: AB, BFG, BIT, BL, DFO, GEO, JF, KER, LFG, LIG, MSW, NA, NG, NUC, OBG, OBL, OBS, OG, OO, OTH, PC, PG, RFO, SLW, STM, SUB, SUN, T, TDF, WAT, WDL, WDS, WH, WOC. This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS
Fuel Transportation Type | Generation | [6 empty] | Unit Info - GEN | List | GENERATION | FUEL_TRANSTYPE | 1. Select from the list 2. Not null. | Select from the list: CV, PL, RR, TK, NA. This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Resource Category | Generation |  |  | Passed Validation |  |  | UPDATE 02/2012 | Unit Info - GEN | List | GENERATION | RES_CATG | 1)Resource Category is not null. 2)Select from the list: Nuclear,Hydro,Coal and Lignite, Gas Steam- Super Critical Boiler, Gas Steam- Reheat Boiler, Gas Steam - Non Reheat or Boiler without air preheated, Simple Cycle <= 90 MW, Simple Cycle > 90 MW, Reciprocating Engine, Solar, Energy Storage, Other | 1)Resource Category is not null. 2)Select from the list: Nuclear,Hydro,Coal and Lignite, Gas Steam- Super Critical Boiler, Gas Steam- Reheat Boiler, Gas Steam - Non Reheat or Boiler without air preheated, Simple Cycle <= 90 MW, Simple Cycle > 90 MW, Reciprocating Engine, Solar, Energy Storage, Other | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/kittiepong
RATINGS AND DESIGNS | Generation | [6 empty] | Unit Info - GEN |  | Not in table | Not in table
Renewable | Generation | [6 empty] | Unit Info - GEN | Y/N | GENERATION | RENEWABLE_FLG | 1. Not null. 2. Select Y or N | Renewable Flag is not null. Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar
Renewable/Offset | Generation | [6 empty] | Unit Info - GEN | List | GENERATION | RENEWABLE_OFFSET | 1. Not null. 2. Select from the list | Select from the list : RN, OS, NA. This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
Physical Unit Type | Generation |  |  | Passed Validation |  |  | UPDATE 02/2012 | Unit Info - GEN | List | GENERATION | PHYS_UNIT_TYPE | Select from the list: FC, GT, HY, IC, NA, OT, PS, PV, ST. This field is not null. | Select from the list: FC, GT, HY, IC, NA, OT, PS, PV, ST. This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Name Plate Rating | Generation | [6 empty] | Unit Info - GEN | MVA | GENERATION | NAME_PLT_RTG | 1. Name Plate Rating must be >= Real Power Rating | Name Plate Rating should be >= Real Power Rating | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS
Real Power Rating | Generation | [6 empty] | Unit Info - GEN | MW | GENERATION | RTG_MW | 1. Real Power Rating must be > Reactive Power Rating | Real Power Rating should be > Reactive Power Rating | R | Numeric | B,DVB | Lin Xu | MMS,NMMS
Reactive Power Rating | Generation | [6 empty] | Unit Info - GEN | MVAR | GENERATION | RTG_MVAR | 1. Reactive Power Rating must be <= Name Plate Rating | Name Plate Rating should be >= Reactive Power Rating | R | Numeric | B,DVB | Lin Xu | MMS,NMMS
Turbine Rating | Generation | [6 empty] | Unit Info - GEN | MW | GENERATION | TURBINE_RTG | 1. Optional. | This field is optional. Enter Numeric value or leave it blank if not applicable. | O | Numeric | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Unit Generating Voltage | Generation | [6 empty] | Unit Info - GEN | kV | GENERATION | UNIT_KV | 1. Numeric entry only 2. Not null. | 1. This field is not null and it should be a number 2. Unit Generating voltage can not be below 4.16 KV | R | Numeric | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS
Governor Droop Setting | Generation | [5 empty] | ADD 04/2012 | Unit Info - GEN | Percent | GENERATION | GOV_DROOP | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if it is not between 0 and 25. Generate Warning if > 5 (protocol requirement). | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if it is not between 0 and 25. Generate Warning if > 5 (protocol requirement). | R | Numeric | B,DVB
Governor Dead-band | Generation | [5 empty] | ADD 04/2012 | Unit Info - GEN | Hz | GENERATION | GOV_DEAD_BND | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if > 0.1. Generate Warning if > 0.03. | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if > 0.1. Generate Warning if > 0.03. | R | Numeric | B,DVB
Design Max Ambient Temperature | Generation | [5 empty] | ADD 04/2012 | Unit Info - GEN | degree F | GENERATION | DESIGN_MAX_AMB_TEMP | >100 <150 | >100 <150
Design Min Ambient Temperature | Generation | [5 empty] | ADD 04/2012 | Unit Info - GEN | degree F | GENERATION | DESIGN_MIN_AMB_TEMP | >-100 <32 | >-100 <32
GEOGRAPHIC LOCATION (CENTER OF PLANT) | Generation | [6 empty] | Unit Info - GEN |  | Not in table | Not in table
Latitude Of Center Of Plant | Generation | [5 empty] | ADD 04/2012 | Unit Info - GEN | decimal degrees (N) | GENERATION | LAT_CENTER_PLT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if Latitude < 25.0 or > 37.0.
Longitude Of Center Of Plant | Generation | [5 empty] | ADD 04/2012 | Unit Info - GEN | decimal degrees (W) | GENERATION | LONG_CENTER_PLT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if <93 or > 107 .
Unit Info - Train | CC | [6 empty] | Unit Info - Train |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type selected is 'CC' | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,MMS,NMMS
CC Train Details | CC | [6 empty] | Unit Info - Train |  | Not in table | Not in table
Train Name | CC | [6 empty] | Unit Info - Train | List | Train | TRAIN_NAME | Data type: Character | This field is not null. Data type: Character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Train Code | CC | [6 empty] | Unit Info - Train | Automatic | Train | TRAIN_CODE | 1. This field is not null. Data type is Character | 1. This field is not null. Data type is Character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS
Non_Moldeled Generator | CC | [5 empty] | ADD 04/2012 | Unit Info - Train | Y/N | Train | NON_MOD_GEN | 1.Select from the list: Y or N 2.Not Null | Select from the list: Y or N | R | Dropdown List | B,DVB
PUC Registration Number | CC | [6 empty] | Unit Info - Train |  | Train | PUC_NUM | 1. Optional | This field is optional. NA is not valid , Leave it blank if not applicable. | O | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
NERC Number | CC | [6 empty] | Unit Info - Train |  | Train | NERC_NUM | 1. Optional | This field is optional. NA is not valid , Leave it blank if not applicable. | O | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Qualifying Facility? | CC | [6 empty] | Unit Info - Train | Y/N | Train | TRN_QUAL_FACILITY_FLG | 1. Select from the list 2. Not null. | QF Flag is not null. Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/kittiepong | Lodestar
SITE AND UNIT DATES | CC | [6 empty] | Unit Info - Train |  | Not in table | Not in table
Train Unit Commercial Date | CC | [6 empty] | Unit Info - Train | mm/dd/yyyy | Train | TRN_UNIT_START_DATE | 1. Not null. 2. Format should be: MM/DD/YYYY 3. Must be >= Site In-Service Date | This field is not null. Format should be: MM/DD/YYYY Unit Start Date should be >= Site Start Date ( Site-Information Tab) | R | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,NMMS
Train Unit End Date | CC | [6 empty] | Unit Info - Train | mm/dd/yyyy | Train | TRN_UNIT_END_DATE | 1. Not null. 2. Format should be: MM/DD/YYYY 3. Must be > Unit Start Date | This field is optional. Format should be MM/DD/YYYY.NA is not valid , Leave it blank if not applicable. | O | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,NMMS
FUEL INFORMATION | CC | [6 empty] | Unit Info - Train |  | Not in table | Not in table
Fuel Transportation Type | CC | [6 empty] | Unit Info - Train | List | Train | FUEL_TRANSTYPE_TRN | 1. Select from the list 2. Not null. | Select from the list: CV, PL, RR, TK, NA. This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Resource Category | CC | [5 empty] | UPDATE 02/2012 | Unit Info - Train | List | Train | RES_CATG_TRN | 1. Select from the list 2. Not null. | 1.Resource type is not null. 2. Select from the list: Combined Cycle <= 90 MW, Combined Cycle >90 MW This field is not null 3. Resource Category for CCTrain is determined by the capacity of largest simple cycle combustion turbine in the train. Example if a CCTrain is combined cycle >90 MW, largest CT in the train should have real power rating>90. Audit report should generate an error if the CT's are <90 MW in this case. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/kittiepong
POWER AUGMENTATION | CC | [6 empty] | Unit Info - Train |  | Not in table | Not in table
Is Train Augmented With Duct Burner(s)? | CC | [6 empty] | Unit Info - Train | Y/N | Train | TRN_AUG_DUCTBRNRS_FLG | 1. Select from the list 2. Not null. | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Is Train Augmented with Evap Cooler(s)? | CC | [6 empty] | Unit Info - Train | Y/N | Train | TRN_AUG_EVAP_CLRS_FLG | 1. Select from the list 2. Not null. | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Is Train augmented with Chiller(s)? | CC | [6 empty] | Unit Info - Train | Y/N | Train | TRN_AUG_CHILLERS_FLG | 1. Select from the list 2. Not null. | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Other Augmentation? | CC | [6 empty] | Unit Info - Train | Y/N | Train | TRN_OTHER_AUG | 1. Select from the list 2. Not null. | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
GEOGRAPHIC LOCATION (CENTER OF PLANT) | CC | [6 empty] | Unit Info - Train |  | Not in table | Not in table
Latitude of center of Plant | CC | [5 empty] | ADD 04/2012 | Unit Info - Train | decimal degrees (N) | Train | LAT_CENTER_PLT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if Latitude < 25.0 or > 37.0.
Longitude of center of Plant | CC | [5 empty] | ADD 04/2012 | Unit Info - Train | decimal degrees (W) | Train | LONG_CENTER_PLT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if <93 or > 107 .
Unit Info - CC | CC | [6 empty] | Unit Info - CC |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type selected is 'CC' | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,MMS,NMMS
GENERATOR DETAILS | CC | [6 empty] | Unit Info - CC |  | Not in table | Not in table
Unit Name | CC | [6 empty] | Unit Info - CC | All Caps | CCUNIT | UNIT_NAME | 1. Not Null. 2. Must not exceed 4 characters for Jointly Owned Units 3. Maximum of 8 character allowed | 1.This field is not null. Data type: Character. | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
SITE_CODE | CC | [5 empty] | ADD 02/2012 | UNIT Info - CC | Automatic | CCUNIT | SITE_CODE
Resource Name (Unit Code/Mnemonic) | CC | [6 empty] | Unit Info - CC | Automatic | CCUNIT | UNIT_CODE | 1. Not Null. 2. Enter Site Code and Unit Name for this field (Sitecode_Unit Name) 3. All letters must be capital | 2. Can not exceed 8 characters for single owner units | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Train Name | CC | Corrected 02/23/2012 |  |  |  |  | ADD 02/2012 | Unit Info - CC | List | TRAIN CCUNIT | TRAIN_CODE | 1. This field is not null. Data type is Character | 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS
Non_Modeled Generator | CC | Removed |  |  |  |  | ADD 04/2012 | Unit Info - CC | Y/N | CCUNIT | NON_MOD_GEN | 1.Select from the list: Y or N 2.Not Null | Select from the list: Y or N | R | Dropdown List | B,DVB
ERCOT Interconnection Project Number - Only New Units | CC | [6 empty] | Unit Info - CC |  | CCUNIT | ERCOT_INTRCONN_PROJ_NUM | 1. Required for new sites only | 1.This field is optional. Required only for new units. 2.Cross check with the data entered in the field 'This submittal is for' in General Information Tab. If the value is 'New Site' then only this field is required. | O | Character | B,DVE | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Angela Moy
SITE AND UNIT DATES | CC | [6 empty] | Unit Info - CC |  | Not in table | Not in table
Transmission Only Date (POI) | CC | [5 empty] | ADD 04/2012 | Unit Info - CC | mm/dd/yyyy | CCUNIT | TRANS_ONLY_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB
Standard Generation Interconnection Agreement (SGIA) Signature Date | CC | [5 empty] | ADD 04/2012 | Unit Info - CC | mm/dd/yyyy | CCUNIT | SGIA_SIG_DT |  | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date. | R | Date | B/DVB | CDannunzio
Unit Start Date (Model Ready Date) | CC | 03/13/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Unit Info - CC | mm/dd/yyyy | CCUNIT | UNIT_MRD_ST_DT |  | This field is optional. Format should be: MM/DD/YYYY
Unit Commercial Date | CC | [6 empty] | Unit Info - CC | mm/dd/yyyy | CCUNIT | UNIT_START_DT |  | This field is not null. Format should be: MM/DD/YYYY Unit Start Date should be >= Site Start Date ( Site-Information Tab) | R | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,NMMS
Unit End Date | CC | [6 empty] | Unit Info - CC | mm/dd/yyyy | CCUNIT | UNIT_END_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,NMMS
POINT OF INTERCONNECTION | CC | [6 empty] | Unit Info - CC |  | Not in table | Not in table
SubStation Code/SubStation Mnemonic | CC | [5 empty] | ADD 04/2012 | Unit Info - CC | All Caps | CCUNIT | SUBSTAT_CODE_SUB_MNEMONIC |  | 1) This field is not null (required). Data type must be Character. 2) Must match ERCOT records (unless new). Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" . 4) Must be <= 8 characters. Warning! Substation Code should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) Substation code should be in Upper case letters. Generate an error if the rule fails. | R | Character | B/DVB | CDannunzio
Voltage Level | CC | [5 empty] | ADD 04/2012 | Unit Info - CC | kV | CCUNIT | VOL_LEV |  | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | R | Float | B/DVE | CDannunzio
PTI Bus Number | CC | [5 empty] | ADD 04/2012 | Unit Info - CC | # | CCUNIT | PTI_BUS_NUM |  | 1) This field isnot null (required). Data type must be Integer. 2) The value must be > 0. | R | Integer | B/DVB | CDannunzio
FUEL INFORMATION | CC | [6 empty] | Unit Info - CC |  | Not in table | Not in table
Primary Fuel Type | CC | [5 empty] | UPDATE 02/2012 | Unit Info - CC | List | CCUNIT | PRIM_FUELTYPE | 1. Select from the list 2. Not null. | 1. Select from the list: DFO, JF, KER, NA, NG, OBG, OO, OG, TDF, WDL, WH, STM 2. Audit report should generate an error when Physical Unit type is 'ST' or 'CA' and Primary or Secondary Fuel type is 'STM'. The rule is not applicable for PUN sites | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS
Secondary Fuel Type | CC | [5 empty] | UPDATE 02/2012 | Unit Info - CC | List | CCUNIT | SEC_FUELTYPE | 1. Select from the list 2. Not null. | 1. Select from the list: DFO, JF, KER, NA, NG, OBG, OO, OG, TDF, WDL, WH, STM 2.Audit report should generate an error when Physical Unit type is 'ST' or 'CA' and Primary or Secondary Fuel type is 'STM'. The rule is not applicable for PUN sites | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS
RATINGS AND DESIGNS | CC | [6 empty] | Unit Info - CC |  | Not in table | Not in table
Physical Unit Type | CC | [5 empty] | UPDATE 02/2012 | Unit Info - CC | List | CCUNIT | PHYS_UNIT_TYPE | 1. Select from the list:CA, CC, CS, CT, ST, OT 2. Not null. | Select from the list:CA, CC, CS, CT, ST, OT This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS
Name Plate Rating | CC | [6 empty] | Unit Info - CC | MVA | CCUNIT | NAME_PLT_RTG | 1. Name Plate Rating must be >= Real Power Rating | Name Plate Rating should be >= Real Power Rating | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS
Real Power Rating | CC | [6 empty] | Unit Info - CC | MW | CCUNIT | RTG_MW | 1. Real Power Rating must be > Reactive Power Rating | Real Power Rating should be > Reactive Power Rating | R | Numeric | B,DVB | Lin Xu | MMS,NMMS
Reactive Power Rating | CC | [6 empty] | Unit Info - CC | MVAR | CCUNIT | RTG_MVAR | 1. Reactive Power Rating must be <= Name Plate Rating | Name Plate Rating should be >= Reactive Power Rating | R | Numeric | B,DVB | Lin Xu | MMS,NMMS
Turbine Rating | CC | [6 empty] | Unit Info - CC | MW | CCUNIT | TURBINE_RTG | 1. Optional. | This field is optional. NA is not valid , Leave it blank if not applicable. | O | Numeric | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Unit Generating Voltage | CC | [6 empty] | Unit Info - CC | kV | CCUNIT | UNIT_KV | 1. Numeric entry only 2. Not null. | 1. This field is not null and it should be a number 2. Unit Generating voltage can not be below 4.16 KV | R | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS
Governor Droop Setting | CC | [5 empty] | ADD 04/2012 | Unit Info - CC | Percent | CCUNIT | GOV_DROOP | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if it is not between 0 and 25. Generate Warning if > 5 (protocol requirement). | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if it is not between 0 and 25. Generate Warning if > 5 (protocol requirement). | R | Numeric | B,DVB
Governor Dead-band | CC | [5 empty] | ADD 04/2012 | Unit Info - CC | Hz | CCUNIT | GOV_DEAD_BND | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if > 0.1. Generate Warning if > 0.03. | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if > 0.1. Generate Warning if > 0.03. | R | Numeric | B,DVB
Design Max Ambient Temperature | CC | [5 empty] | ADD 04/2012 | Unit Info - CC | degree F | CCUNIT | DESIGN_MAX_AMB_TEMP | >100 <150 | >100 <150
Design Min Ambient Temperature | CC | [5 empty] | ADD 04/2012 | Unit Info - CC | degree F | CCUNIT | DESIGN_MIN_AMB_TEMP | >-100 <32 | >-100 <32
Unit Info - Wind | Wind | [6 empty] | Unit Info - Wind |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type selected is 'WIND ' | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,MMS,NMMS
GENERATOR Details | Wind | [6 empty] | Unit Info - Wind |  | Not in table | Not in table
Unit Name | Wind | [6 empty] | Unit Info - Wind | All Caps | WIND | UNIT_NAME | 1. Not Null. 2. Must not exceed 4 characters for Jointly Owned Units 3. Maximum of 8 character allowed | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Wind | [6 empty] | Unit Info - Wind | Automatic | Wind | UNIT_CODE | 1. Not Null. 2. Enter Site Code and Unit Name for this field (Sitecode_Unit Name) 3. All letters must be capital | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
Non Modeled Generation | Wind | [5 empty] | ADD 04/2012 | Unit Info - Wind | Y/N | WIND | NON_MOD_GEN | 1.Select from the list: Y or N 2.Not Null | Select from the list: Y or N | R | Dropdown List | B,DVB
PUC Registration Number (Docket Number) | Wind | [6 empty] | Unit Info - Wind |  | Wind | PUC_NUM | 1. Optional. | This field is optional and it should be a number. NA is not valid , Leave it blank if not applicable. | O | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
ERCOT Interconnection Project Number - only new units | Wind | [6 empty] | Unit Info - Wind |  | Wind | ERCOT_INTRCONN_PROJ_NUM | 1. Required for new sites only | 1.This field is optional. Required only for new units. NA is not valid , Leave it blank if not applicable. 2. Cross check with the data entered in the field 'This submittal is for' in General Information Tab. If the value is 'New Site' then only this field is required. | O | Character | B,DVE | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Angela Moy
NERC Number (NERC ID#) | Wind | [6 empty] | Unit Info - Wind |  | Wind | NERC_NUM | 1. Optional. | This field is optional. NA is not valid , Leave it blank if not applicable. | O | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Qualifying facility | Wind | [6 empty] | Unit Info - Wind | Y/N | Wind | QUAL_FACILITY_FLG | 1. Not null. 2. Select Y or N | Select from the list: Y or N. QF Flag is not null | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/kittiepong | Lodestar
SITE AND UNIT DATES | Wind | [6 empty] | Unit Info - Wind |  | Not in table | Not in table
Transmission Only Date (POI) | Wind | [5 empty] | ADD 04/2012 | Unit Info - Wind | mm/dd/yyyy | WIND | TRANS_ONLY_DT | 1. Optional. 2. Format should be: MM/DD/YYYY | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB
Standard Generation Interconnection Agreement (SGIA) Signature Date | Wind | [5 empty] | ADD 04/2012 | Unit Info - Wind | mm/dd/yyyy | WIND | SGIA_SIG_DT | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date. | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date. | R | Date | B/DVB | CDannunzio
Unit Start Date (Model Ready Date) | Wind | 03/13/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Unit Info - Wind | mm/dd/yyyy | WIND | UNIT_MRD_ST_DT | 1.This field is not null. Format should be: MM/DD/YYYY 2.Date should be Vaild Data Base Load Date 3.Unit Start Date should be >= Site Start Date ( Site-Information Tab) | This field is optional. Format should be: MM/DD/YYYY
Unit Start Date (Commercial Date) | Wind | [6 empty] | Unit Info - Wind | mm/dd/yyyy | Wind | UNIT_START_DT | 1. Not null. 2. Format should be: MM/DD/YYYY 3. Must be equal to or greater than Site In-Service Date. | This field is not null. Format should be: MM/DD/YYYY Unit Start Date should be >= Site Start Date ( Site-Information Tab) | R | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar
Unit End Date | Wind | [6 empty] | Unit Info - Wind | mm/dd/yyyy | Wind | UNIT_END_DT | 1. Not null. 2. Format should be: MM/DD/YYYY 3. Must be greater than Unit Start Date. | This field is optional. Format Should be: MM/DD/YYYY. NA is not valid , Leave it blank if not applicable. | O | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar
POINT OF INTERCONNECTION | Wind | [6 empty] | Unit Info - Wind |  | Not in table | Not in table
Substation Code/substation Mnemonic | Wind | [5 empty] | ADD 04/2012 | Unit Info - Wind | All caps | Wind | SUBSTAT_CODE_SUB_MNEMONIC | 1) This field is not null (required). Data type must be Character. 2) Must match ERCOT records (unless new). Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" . 4) Must be <= 8 characters. Warning! Substation Code should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) Substation code should be in Upper case letters. Generate an error if the rule fails. | 1) This field is not null (required). Data type must be Character. 2) Must match ERCOT records (unless new). Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" . 4) Must be <= 8 characters. Warning! Substation Code should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) Substation code should be in Upper case letters. Generate an error if the rule fails. | R | Character | B/DVB | CDannunzio
Voltage Level | Wind | [5 empty] | ADD 04/2012 | Unit Info - Wind | kV | Wind | VOL_LEV | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0. | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0. | R | Float | B/DVE | CDannunzio
Pti Bus Number | Wind | [5 empty] | ADD 04/2012 | Unit Info - Wind | # | Wind | PTI_BUS_NUM | 1) This field isnot null (required). Data type must be Integer. 2) The value must be > 0. | 1) This field isnot null (required). Data type must be Integer. 2) The value must be > 0. | R | Integer | B/DVB | CDannunzio
FUEL INFORMATION | Wind | [6 empty] | Unit Info - Wind |  | Not in table | Not in table
Renewable | Wind | [6 empty] | Unit Info - Wind | Y/N | Wind | RENEWABLE_FLG | 1. Not null. 2. Select Y or N | Select from the list: Y or N. This field is not null | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar
Renewable/Offset | Wind | [6 empty] | Unit Info - Wind | List | Wind | RENEWABLE_OFFSET | 1. Not null. 2. Select from the list | Select from the list : RN, OS, NA. This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
Resource Category | Wind | [5 empty] | UPDATE 02/2012 | Unit Info - Wind | List | Wind | RES_CATG | 1. Not null. 2. Select from the list WGR, OT. | 1.Resource Category is not null. 2.Select from the list: Wind Generation Resource and OT | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/kittiepong
RATINGS AND DESIGNS | Wind | [6 empty] | Unit Info - Wind |  | Not in table | Not in table
Physical Unit Type | Wind | [5 empty] | UPDATE 02/2012 | Unit Info - Wind | List | Wind | PHYS_UNIT_TYPE | Select from the list: OT, WT not null. | Select from the list: Wind Generation Resource, OT | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Name Plate Rating | Wind | [6 empty] | Unit Info - Wind | MVA | Wind | NAME_PLT_RTG | 1. Name Plate Rating must be >= Real Power Rating | Name Plate Rating should be >= Real Power Rating | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS
Real Power Rating | Wind | [6 empty] | Unit Info - Wind | MW | Wind | RTG_MW | 1. Real Power Rating must be > Reactive Power Rating | Real Power Rating should be > Reactive Power Rating | R | Numeric | B,DVB | Lin Xu | MMS,NMMS
Reactive Power Rating | Wind | [6 empty] | Unit Info - Wind | MVAR | Wind | RTG_MVAR | 1. Reactive Power Rating must be <= Name Plate Rating | Name Plate Rating should be >= Reactive Power Rating | R | Numeric | B,DVB | Lin Xu | MMS,NMMS
Unit Generating Voltage (collection voltage?) | Wind | [6 empty] | Unit Info - Wind | kV | Wind | UNIT_KV | 1. Numeric entry only 2. Not null. | Data type is Numeric. Unit Generating voltage can not be below 4.16 KV | R | Numeric | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS
Governor Droop Setting | Wind | [5 empty] | ADD 04/2012 | Unit Info - Wind | Percent | Wind | GOV_DROOP |  | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if it is not between 0 and 25. Generate Warning if > 5 (protocol requirement). | R | Numeric | B,DVB
Governor Dead-band | Wind | [5 empty] | ADD 04/2012 | Unit Info - Wind | Hz | Wind | GOV_DEAD_BND |  | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if > 0.1. Generate Warning if > 0.03. | R | Numeric | B,DVB
Design Max Ambient Temperature | Wind | [5 empty] | ADD 04/2012 | Unit Info - Wind | Degree F | Wind | DESIGN_MAX_AMB_TEMP |  | >100 <150
Design Min Ambient Temperature | Wind | [5 empty] | ADD 04/2012 | Unit Info - Wind | Degree F | Wind | DESIGN_MIN_AMB_TEMP |  | >-100 <32
Eligible for McCamey Flow gate Rights (MCFRIs)? | Wind | [5 empty] | REMOVE | Unit Info - Wind |  | Wind |  |  | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
METEOROLOGICAL TOWER AND INSTRUMENTATION INFORMATION | Wind | [6 empty] | Unit Info - Wind |  | Not in table | Not in table
Average Height above ground of Turbine Hub | Wind | [6 empty] | Unit Info - Wind | Meters | Wind | AVG_HGHT_ABV_GRND | 1. Not null. | This field is not null and it should be a number | R | Numeric | B | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
Latitude of Meteorological Tower | Wind | [6 empty] | Unit Info - Wind | decimal degrees(N) | Wind | LAT_METG_TOWER | 1. Not null. | 1. This field is not null. Data type must be Float 2. Latitude of Meteorological Tower : Must be <= 90 decimal degrees | R | Numeric | B | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
Longitude of Meteorological Tower | Wind | [6 empty] | Unit Info - Wind | decimal degrees(W) | Wind | LONG_METG_TOWER | 1. Not null. | 1. This field is not null. Data type must be Float 2.Longitude of Meteorological Tower: Must be <= 180 decimal degrees | R | Numeric | B | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
Height of Meteorological Tower Instrumentation | Wind | [5 empty] | REMOVE | Unit Info - Wind |  | Wind | HGT_MET_TWR_INST |  | This field is not null. Data type should be character | R | Numeric | B | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
Height of Meteorological Instrumentation - Wind Speed | Wind | [5 empty] | ADD 04/2012 | Unit Info - Wind | Meters | Wind | HGT_MET_TWR_WND_SPD |  | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Float | B/DVB | CDannunzio
Height of Meteorological Instrumentation - Wind Direction | Wind | [5 empty] | ADD 04/2012 | Unit Info - Wind | Meters | Wind | HGT_MET_TWR_WND_DIRT |  | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Float | B/DVB | CDannunzio
Height of Meteorological Instrumentation - Barometric Pressure | Wind | [5 empty] | ADD 04/2012 | Unit Info - Wind | Meters | Wind | HGT_MET_TWR_BAR_PRES |  | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Float | B/DVB | CDannunzio
Height of Meteorological Instrumentation - Temperature | Wind | [5 empty] | ADD 04/2012 | Unit Info - Wind | Meters | Wind | HGT_MET_TWR_TEMP |  | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Float | B/DVB | CDannunzio
GEOGRAPHIC LOCATION (CENTER OF PLANT) | Wind | [6 empty] | Unit Info - Wind |  | Not in table | Not in table
Latitude Of Center Of Wind Plant | Wind | [5 empty] | UPDATE 02/2012 | Unit Info - Wind | decimal degrees(N) | Wind | LAT_CTR_WNDFARM | 1. Not null. | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if Latitude < 25.0 or > 37.0.
Longitude Of Center Of Wind Plant | Wind | [5 empty] | UPDATE 02/2012 | Unit Info - Wind | decimal degrees(W) | Wind | LONG_CTR_WNDFARM | 1. Not null. | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if <93 or > 107 .
GENERATOR Details | Wind | [6 empty] | Unit Info -Wind Turbine |  | Not in table | Not in table
Resoure Name (Unit Code/Mnemonic) | Wind | [5 empty] | ADD 02/2012 | Unit Info -Wind Turbine | List | Wind | UNIT_CODE | 1. Not Null. 2. Enter Site Code and Unit Name for this field (Sitecode_Unit Name) 3. All letters must be capital | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Total number of turbines | Wind | Keep in Database but no longer mapped 02/28/2012 | [5 empty] | Unit Info -Wind Turbine | # | Wind | TOTNUM_TURBINES | 1. Numeric entry only 2. Not null. | This is not null and it should be an Integer | R | Integer | B | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
GROUP 1 - TURBINE DETAILS | Wind | [6 empty] | Unit Info -Wind Turbine |  | Not in table | Not in table
Type of Turbine (Manufacturer/Model) | Wind | Added 02/28/2012 Updated 02/29/2012 Removed all caps | [5 empty] | Unit Info -Wind Turbine |  | Wind | TUR_TYPE | 1. Not null. | This field is not null and the Data type should be character. | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
MW Rating for this model of Turbine | Wind | Added 02/28/2012 | [5 empty] | Unit Info -Wind Turbine | MW | Wind | TUR_MW_MDL_RTG | 1. Not null. | This field is not null and the Data type should be Numeric | R | Numeric | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Number of this type of Turbine | Wind | Added 02/28/2012 | [5 empty] | Unit Info -Wind Turbine | # | Wind | TUR_NUM | 1. Not null. | This field is not null and it should be an integer | R | Numeric | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Group 1 - Type of Turbine (Manufacturer/Model) | Wind | Keep in Database but no longer mapped 02/28/2012 | [5 empty] | Unit Info -Wind Turbine | all caps | Wind | GRP1_TUR_TYPE | 1. Not null. | This field is not null and the Data type should be character. | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Group 1- MW Rating for this model of Turbine | Wind | Keep in Database but no longer mapped 02/28/2012 | [5 empty] | Unit Info -Wind Turbine | MW | Wind | GRP1_TUR_MW_MDL_RTG | 1. Not null. | This field is not null and the Data type should be Numeric | R | Numeric | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Group 1 - Number of this type of Turbine | Wind | Keep in Database but no longer mapped 02/28/2012 | [5 empty] | Unit Info -Wind Turbine | # | Wind | GRP1_TUR_NUM | 1. Not null. | This field is not null and it should be an integer | R | Numeric | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
GROUP 2 - TURBINE DETAILS | Wind | Keep in Database but no longer mapped 02/28/2012 | [5 empty] | Unit Info -Wind Turbine |  | Not in table | Not in table
Group 2 - Type of Turbine (Manufacturer/Model) | Wind | Keep in Database but no longer mapped 02/28/2012 | [5 empty] | Unit Info -Wind Turbine | all caps | Wind | GRP2_TUR_TYPE | 1. Optional. 2. Group2 reactive capability-Wind Tab should have values for this group. | 1. This field is optional. If entered it should be a character. If the data is entered for Group2, then reactive capability-Wind Tab should have values for this group. 2. Wind groups of turbines within a unit must be of the same type and size. RARF Audit report should generate a warning if this rule fails | O | Character | B | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
Group 2- MW Rating for this model of Turbine | Wind | Keep in Database but no longer mapped 02/28/2012 | [5 empty] | Unit Info -Wind Turbine | MW | Wind | GRP2_TUR_MW_MDL_RTG | 1. Conditional required if Type of turbine info is entered for Group2 2. Data type should be numeric. | This field is optional/conditional. Required if Type of turbine info is entered for Group2 otherwise it is optional. Data type should be numeric. If the data is entered for Group2, then reactive capability-Wind Tab should have values for this group. | C/O | Numeric | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
Group 2 - Number of this type of Turbine | Wind | Keep in Database but no longer mapped 02/28/2012 | [5 empty] | Unit Info -Wind Turbine | # | Wind | GRP2_TUR_NUM | 1. Conditional required if Type of turbine info is entered for Group2 2. Data type should be numeric. | This field is optional/conditional. Required if Type of turbine info is entered for Group2 otherwise it is optional. Data type should be Integer. If the data is entered for Group2, then reactive capability-Wind Tab should have values for this group. | C/O | Integer | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
GROUP 3 - TURBINE DETAILS | Wind | Keep in Database but no longer mapped 02/28/2012 | [5 empty] | Unit Info -Wind Turbine |  | Not in table | Not in table
Group 3 - Type of Turbine (Manufacturer/Model) | Wind | Keep in Database but no longer mapped 02/28/2012 | [5 empty] | Unit Info -Wind Turbine | all caps | Wind | GRP3_TUR_TYPE | 1. Optional. 2. Group3 reactive capability-Wind Tab should have values for this group. | 1. This field is optional. If entered it should be a character. If the data is entered for Group3, then reactive capability-Wind Tab should have values for this group. 2. Wind groups of turbines within a unit must be of the same type and size. RARF Audit report should generate a warning if this rule fails | O | Character | B | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
Group 3- MW Rating for this model of Turbine | Wind | Keep in Database but no longer mapped 02/28/2012 | [5 empty] | Unit Info -Wind Turbine | MW | Wind | GRP3_TUR_MW_MDL_RTG | 1. Conditional required if Type of turbine info is entered for Group3 2. Data type should be numeric. | This field is optional/conditional. Required if Type of turbine info is entered for Group3 otherwise it is optional. Data type should be numeric. If the data is entered for Group2, then reactive capability-Wind Tab should have values for this group. | C/O | Numeric | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
Group 3 - Number of this type of Turbine | Wind | Keep in Database but no longer mapped 02/28/2012 | [5 empty] | Unit Info -Wind Turbine | # | Wind | GRP3_TUR_NUM | 1. Conditional required if Type of turbine info is entered for Group3 2. Data type should be numeric. | 1.This field is optional/conditional. Required if Type of turbine info is entered for Group3 otherwise it is optional. Data type should be Integer. If the data is entered for Group2, then reactive capability-Wind Tab should have values for this group. | C/O | Integer | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
GROUP 4 - TURBINE DETAILS | Wind | Keep in Database but no longer mapped 02/28/2012 | [5 empty] | Unit Info -Wind Turbine |  | Not in table | Not in table
Group 4 - Type of Turbine (Manufacturer/Model) | Wind | Keep in Database but no longer mapped 02/28/2012 | [5 empty] | Unit Info -Wind Turbine | all caps | Wind | GRP4_TUR_TYPE | 1. Optional. 2. Group4 reactive capability-Wind Tab should have values for this group. | 1.This field is optional. If entered it should be a character. If the data is entered for Group2, then reactive capability-Wind Tab should have values for this group. 2. Wind groups of turbines within a unit must be of the same type and size. RARF Audit report should generate a warning if this rule fails | O | Character | B | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
Group 4- MW Rating for this model of Turbine | Wind | Keep in Database but no longer mapped 02/28/2012 | [5 empty] | Unit Info -Wind Turbine | MW | Wind | GRP4_TUR_MW_MDL_RTG | 1. Conditional required if Type of turbine info is entered for Group4 2. Data type should be numeric. | This field is optional/conditional. Required if Type of turbine info is entered for Group4 otherwise it is optional. Data type should be numeric. If the data is entered for Group2, then reactive capability-Wind Tab should have values for this group. | C/O | Numeric | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
Group 4 - Number of this type of Turbine | Wind | Keep in Database but no longer mapped 02/28/2012 | [5 empty] | Unit Info -Wind Turbine | # | Wind | GRP4_TUR_NUM | 1. Conditional required if Type of turbine info is entered for Group4 2. Data type should be numeric. | This field is optional/conditional. Required if Type of turbine info is entered for Group4 otherwise it is optional. Data type should be Integer. If the data is entered for Group4, then reactive capability-Wind Tab should have values for this group. | C/O | Integer | B | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
GROUP 5 - TURBINE DETAILS | Wind | Keep in Database but no longer mapped 02/28/2012 | [5 empty] | Unit Info -Wind Turbine |  | Not in table | Not in table
Group 5 - Type of Turbine (Manufacturer/Model) | Wind | Keep in Database but no longer mapped 02/28/2012 | [5 empty] | Unit Info -Wind Turbine | all caps | Wind | GRP5_TUR_TYPE | 1. Optional. 2. Group5 reactive capability-Wind Tab should have values for this group. | 1.This field is optional. If entered it should be a character. If the data is entered for Group5, then reactive capability-Wind Tab should have values for this group. 2. Wind groups of turbines within a unit must be of the same type and size. RARF Audit report should generate a warning if this rule fails | O | Character | B | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
Group 5- MW Rating for this model of Turbine | Wind | Keep in Database but no longer mapped 02/28/2012 | [5 empty] | Unit Info -Wind Turbine | MW | Wind | GRP5_TUR_MW_MDL_RTG | 1. Conditional required if Type of turbine info is entered for Group5 2. Data type should be numeric. | This field is optional/conditional. Required if Type of turbine info is entered for Group5 otherwise it is optional. Data type should be numeric. If the data is entered for Group2, then reactive capability-Wind Tab should have values for this group. | C/O | Numeric | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
Group 5 - Number of this type of Turbine | Wind | Keep in Database but no longer mapped 02/28/2012 | [5 empty] | Unit Info -Wind Turbine | # | Wind | GRP5_TUR_NUM | 1. Conditional required if Type of turbine info is entered for Group5 2. Data type should be numeric. | This field is optional/conditional. Required if Type of turbine info is entered for Group5 otherwise it is optional. Data type should be Integer. If the data is entered for Group5, then reactive capability-Wind Tab should have values for this group. | C/O | Integer | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
Ownership-GEN | Generation | [6 empty] | Ownership - GEN |  | Not in table | Not in table |  | This tab is conditional. Required if single entity represents the Resource. | C
Unit Name | Generation | Do not show Message on Audit or Delta |  | UNIT_NAME field has not been added to OWNERSHIP TABLE/ FAILED |  |  | ADD 02/2012 | Ownership - GEN | List | GENERATION | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Generation |  |  | UNIT_CODE field has not been added to SITECODES TABLE/ FAILED |  |  | ADD 02/2012 | Ownership - GEN | List | OWNERSHIP | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Ownership Percentages | Generation | [6 empty] | Ownership - GEN |  | Not in table | Not in table
Joint OWNER | Generation |  |  | If JOCODE is marked N then fixed ownership amount should = 100%/ FAILED (Pena) |  |  | ADD 04/2012 | Ownership - GEN | Y/N | OWNERSHIP | J0CODE |  | 1. Select from the list: Y or N 2. If N then Fixed Ownership 100% | R | Dropdown List
Resource Entity Name | Generation |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  |  | Ownership - GEN |  | OWNERSHIP | MKT_PRTCPT |  | This field is conditional: Required if single entity represents the Resource. Data type: Character. Resource Entity Name should not allow any special characters except spaces. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | C | Character | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0 | EMS,Lodestar,NMMS
Resource Duns Number | Generation |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  |  | Ownership - GEN | 9-13 digits | OWNERSHIP | MKT_PRTCPT_DUNS |  | This field is Conditional : Required if single entity represents the Resource. This should be either 9 or 13 digit number | C | Integer | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0 | EMS,Lodestar,NMMS
Market Participant (Resource) Name | Generation | [5 empty] | REMOVE | Ownership - GEN |  | OWNERSHIP |  |  | This field is conditional. Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. Data type: character. | C | Character | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0 | EMS,Lodestar,NMMS
Market Participant (Resource) Duns Number | Generation | [5 empty] | REMOVE | Ownership - GEN |  | OWNERSHIP |  |  | This field is conditional. Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. This should be either 9 or 13 digit number | C | Integer | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0 | EMS,Lodestar,NMMS
Fixed Ownership % | Generation |  |  | Fixed Ownership should = 100%, if it does not then an ERROR will occur. / FAILED (Pena) |  |  |  | Ownership - GEN | Percent | OWNERSHIP | FIX_OWNRSHP_PCT |  | Sum of the Ownership percentage should be 100. Up to 4 decimal places only are valid (limit submission to 4 places after the point) | C | Numeric | B,DVB | Lin Xu/Art Deller | EMS,Lodestar,MMS,NMMS
Master Owner (Y or N) | Generation |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  |  | Ownership - GEN | Y/N | OWNERSHIP | MASTR_OWNR_FLG |  | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 | EMS,Lodestar,NMMS
Ownership Start Date | Generation |  |  | New field to be added on 04/2012 |  |  | ADD 04/2012 | Ownership - GEN | mm/dd/yyyy | OWNERSHIP | OWNR_START_DT |  | Format should be: MM/DD/YYYY | R | Date | B/DVB
Ownership Stop Date | Generation |  |  | New field to be added on 04/2012 |  |  | ADD 04/2012 | Ownership - GEN | mm/dd/yyyy | OWNERSHIP | OWNR_END_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB
Ownership-CC | CC | [6 empty] | Ownership - CC |  | Not in table | Not in table |  | This Section is conditional. Required for only Combined Cycle generation resources. Required if Resource Entity represents 100% of all units. | C
Generator Details | CC | [6 empty] | Ownership - CC |  | Not in table | Not in table |  | This Section is conditional. Required for only Combined Cycle generation resources. Required if Resource Entity represents 100% of all units. | C
Train Name | CC | [5 empty] | ADD 02/2012 | Ownership - CC | List | TRAIN | TRAIN_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Train Code | CC | Corrected 02/23/2012 |  |  |  |  | ADD 02/2012 | Ownership - CC | Automatic | TRAIN OWNERSHIP | TRAIN_CODE UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Resource Entity Name | CC | Corrected |  |  |  |  | ADD 04/2012 Existing Field | Ownership - CC |  | OWNERSHIP | MKT_PRTCPT |  | This field is conditional. Required if Resource Entity represents 100% of all units. Resource Entity Name should not allow any special characters except spaces | C | Character | B | RARF Guide Version 4.0 | Lodestar,NMMS
Resource Duns Number | CC | Corrected |  |  |  |  | ADD 04/2012 Existing Field | Ownership - CC | 9-13 digits | OWNERSHIP | MKT_PRTCPT_DUNS |  | This field is conditional. Required if Resource Entity represents 100% of all units. | C | Numeric | B,DVE | RARF Guide Version 4.0 | Lodestar,NMMS
Fixed Ownership | CC | Added Back 02/29/2012 |  |  |  |  | Ownership - CC | Ownership - CC | Percent | OWNERSHIP | FIX_OWNRSHP_PCT |  | This field is conditional. Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. Data type: character. | C | Character | B,DVB | RARF Guide Version 4.0 | EMS,Lodestar,NMMS
Master Owner | CC | Added Back 02/29/2012 |  |  |  |  | Ownership - CC | Ownership - CC | Y/N | OWNERSHIP | MASTR_OWNR_FLG |  | This field is conditional. Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. This should be either 9 or 13 digit number | C | Integer | B,DVB | RARF Guide Version 4.0/Angela Moy | EMS,Lodestar,NMMS
Ownership-CC2 | CC | [5 empty] | REMOVE | Ownership - CC |  | OWNERSHIP |  |  | This Section is conditional. Required for only Combined Cycle generation resources | C
Resource Entity Name | CC | [5 empty] | REMOVE | Ownership - CC |  | OWNERSHIP |  |  | This field is conditional. Required if Resource Entity represents 100% of all units. | C | Character | B | RARF Guide Version 4.0 | Lodestar,NMMS
Resource Duns Number | CC | [5 empty] | REMOVE | Ownership - CC |  | OWNERSHIP |  |  | This field is conditional. Required if Resource Entity represents 100% of all units. | C | Numeric | B,DVE | RARF Guide Version 4.0 | Lodestar,NMMS
Ownership-CC3 | CC | [5 empty] | REMOVE | Ownership - CC |  | OWNERSHIP |  |  | This Section is conditional. Required for only Combined Cycle generation resources | C |  |  | RARF Guide Version 4.0
Resource Entity Name | CC | [5 empty] | REMOVE | Ownership - CC |  | OWNERSHIP |  |  | This field is conditional. Required if Resource Entity represents 100% of all units. | C | Character | B | RARF Guide Version 4.0 | Lodestar,NMMS
Resource Duns Number | CC | [5 empty] | REMOVE | Ownership - CC |  | OWNERSHIP |  |  | This field is conditional. Required if Resource Entity represents 100% of all units. | C | Numeric | B,DVE | RARF Guide Version 4.0 | Lodestar,NMMS
Ownership Start Date | CC | [5 empty] | ADD 04/2012 | Ownership - CC | mm/dd/yyyy | OWNERSHIP | OWNR_START_DT |  | Format should be: MM/DD/YYYY | R | Date | B/DVB
Ownership Stop Date | CC | [5 empty] | ADD 04/2012 | Ownership - CC | mm/dd/yyyy | OWNERSHIP | OWNR_END_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB
Ownership - WIND | Wind | [6 empty] | Ownership - WIND |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type selected is 'WIND ' | C |  |  | RARF Guide Version 4.0
Generator Details | Wind | [6 empty] | Ownership - WIND |  | Not in table | Not in table
Unit Name | Wind | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Ownership - WIND | List | WIND | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Wind | [5 empty] | ADD 02/2012 | Ownership - WIND | Automatic | OWNERSHIP & SITECODES | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Ownership Percentages | Wind | [6 empty] | Ownership - WIND |  | Not in table | Not in table
Joint Ownership | Wind | [5 empty] | ADD 04/2012 | Ownership - WIND | Y/N | OWNERSHIP | J0CODE |  | 1. Select from the list: Y or N 2. If N then Fixed Ownership 100% | R | Dropdown List
Resource Entity Name | Wind | [6 empty] | Ownership - WIND |  | OWNERSHIP | MKT_PRTCPT |  | This field is conditional: Required if single entity represents the Resource. Data type: Character. Resource Entity Name should not allow any special characters except spaces. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | C | Character | B,DVB | RARF Guide Version 4.0 | Lodestar,NMMS
Resource Duns Number | Wind | [6 empty] | Ownership - WIND | 9-13 digits | OWNERSHIP | MKT_PRTCPT_DUNS |  | This field is Conditional : Required if single entity represents the Resource. This should be either 9 or 13 digit number | C | Integer | B,DVE | RARF Guide Version 4.0 | Lodestar,NMMS
Market Participant (Resource) Name | Wind | [5 empty] | REMOVE | Ownership - WIND |  | OWNERSHIP |  |  | This field is conditional. Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. Data type: character. | C | Character | B,DVB | RARF Guide Version 4.0 | EMS,Lodestar,NMMS
Market Participant (Resource) Duns Number | Wind | [5 empty] | REMOVE | Ownership - WIND |  | OWNERSHIP |  |  | This field is conditional. Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. This should be either 9 or 13 digit number | C | Integer | B,DVB | RARF Guide Version 4.0/Angela Moy | EMS,Lodestar,NMMS
Fixed Ownership % | Wind | [6 empty] | Ownership - WIND | Percent | OWNERSHIP | FIX_OWNRSHP_PCT |  | Sum of the Ownership percentage should be 100. Up to 4 decimal places are valid (limit submission to 4 places after the point) | C | Numeric | B,DVB | RARF Guide Version 4.0 | EMS,Lodestar,MMS,NMMS
Master Owner (Y or N) | Wind | [6 empty] | Ownership - WIND | Y/N | OWNERSHIP | MASTR_OWNR_FLG |  | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | R | Dropdown List | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0 | EMS,Lodestar,NMMS
Ownership Start Date | Wind | [5 empty] | ADD 04/2012 | Ownership - Wind | mm/dd/yyyy | OWNERSHIP | OWNR_START_DT |  | Format should be: MM/DD/YYYY | R | Date | B/DVB
Ownership Stop Date | Wind | [5 empty] | ADD 04/2012 | Ownership - Wind | mm/dd/yyyy | OWNERSHIP | OWNR_END_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB
Parameters - GEN | Generation | [6 empty] | Parameters - GEN |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type Selected is 'GEN' where GEN is non-CC non-wind Generation Resources. | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,MMS,NMMS
Generator Details | Generation | [6 empty] | Parameters - GEN |  | Not in table | Not in table
Unit Name | Generation | Do not show Message on Audit or Delta |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 02/2012 | Parameters - GEN | List | Generation | UNIT_NAME | 1. Not Null. 2. Must not exceed 4 characters for Jointly Owned Units 3. Maximum of 8 character allowed | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Generation |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 04/2012 | Parameters - GEN | Atomatic | Generation & DERATING | UNIT_CODE | 1. Not Null. 2. Enter Site Code and Unit Name for this field (Sitecode_Unit Name) 3. All letters must be capital | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Reasonability Limits | Generation | [6 empty] | Parameters - GEN |  | Not in table | Not in table
High Reasonability Limit | Generation |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | UPDATE 02/2012 | Parameters - GEN | MW | Generation | HR_LMT | 1. High Reasonability Limit >0 2. HighReasonabilityLimit >= LowReasonablityLimit 3. Not Null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Low Reasonability Limit | Generation |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | UPDATE 02/2012 | Parameters - GEN | MW | Generation | LR_LMT | 1. Low Reasonability Limit >0 for Non PUN sites 2. Low ReasonabilityLimit <= High ReasonablityLimit 3. PUN (Private Use Network) Sites LRL should equal zero or produce a Warning 4. Not Null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
High Reasonability Ramp Rate Limit | Generation |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | UPDATE 02/2012 | Parameters - GEN | MW/min | Generation | HR_RAMPRATE_LMT | 1. High Reasonability Ramp Rate Limit >= Low Reasonability Ramp Rate Limit. 2. Not null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS
Low Reasonability Ramp Rate Limit | Generation |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | UPDATE 02/2012 | Parameters - GEN | MW/min | Generation | LR_RAMP_RATE_LMT | 1. Low Reasonability Ramp Rate Limit >=0. 2. Not null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS
Seasonal Ratings Spring | Generation | [6 empty] | Parameters - GEN |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Spring | Generation | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MAX_SUST_RTG_SP | 1.Seasonal Net Max Sustainable Rating - Spring >= Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Spring > Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS
Seasonal Net Min Sustainable Rating - Spring | Generation | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MIN_SUST_RTG_SP | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS
Seasonal Net Max Emergency Rating - Spring | Generation | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MAX_EMGY_RTG_SP | 1.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS
Seasonal Net Min Emergency Rating - Spring | Generation | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MIN_EMGY_RTG_SP | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit 2. Not Null | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS
Seasonal Ratings Summer | Generation | [6 empty] | Parameters - GEN |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Summer | Generation | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MAX_SUST_RTG_SM | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Summer > Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Sustainable Rating - Summer | Generation | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MIN_SUST_RTG_SM | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu | MMS
Seasonal Net Max Emergency Rating - Summer | Generation | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MAX_EMGY_RTG_SM | 1.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Summer > Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Emergency Rating - Summer | Generation | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MIN_EMGY_RTG_SM | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Ratings Fall | Generation | [6 empty] | Parameters - GEN |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Fall | Generation | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MAX_SUST_RTG_FL | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Sustainable Rating - Fall | Generation | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MIN_SUST_RTG_FL | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall. >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Max Emergency Rating - Fall | Generation | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MAX_EMGY_RTG_FL | 1.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Fall > Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Emergency Rating - Fall | Generation | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MIN_EMGY_RTG_FL | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Ratings Winter | Generation | [6 empty] | Parameters - GEN |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Winter | Generation | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MAX_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Sustainable Rating - Winter | Generation | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MIN_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Max Emergency Rating - Winter | Generation | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MAX_EMGY_RTG_WT | 1.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Winter > Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Emergency Rating - Winter | Generation | [5 empty] | UPDATE 02/2012 | Parameters - GEN | MW | Generation | SEASON_NET_MIN_EMGY_RTG_WT | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES | Generation | [6 empty] | Parameters - GEN |  | Not in table | Not in table
0°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
5°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
10°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
15°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
20°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
25°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
30°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
35°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
40°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
45°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
50°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
55°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
60°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
65°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
70°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
75°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
80°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
85°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
90°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
95°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
100°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
105°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
110°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
115°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
120°f | Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - GEN | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
Parameters - CC | CC | [6 empty] | Parameters - CC |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type selected is 'CC'. Can register up to 3 trains at one site. | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | MMS,NMMS
GENERATOR DETAILS | CC | [6 empty] | Parameters - CC |  | Not in table | Not in table
Unit Name | CC | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Parameters - CC | List | CCUNIT | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | CC | [5 empty] | ADD 02/2012 | Parameters - CC | List | CCUNIT & DERATING | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
REASONABILITY LIMITS | CC | [6 empty] | Parameters - CC |  | Not in table | Not in table
High Reasonability Limit | CC | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | HR_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit | R | Numeric | B,DVB | KitteiPong/Jamil Daouk | EMS,MMS,NMMS
Low Reasonability Limit | CC | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | LR_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | Numeric | B,DVB | KitteiPong/Lin Xu/ Jamil Daouk, Kenneth Ragsdale | EMS,MMS,NMMS
High Reasonability Ramp Rate Limit | CC | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW/min | CCUNIT | HR_RAMPRATE_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
Low Reasonability Ramp Rate Limit | CC | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW/min | CCUNIT | LR_RAMP_RATE_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
SEASONAL RATINGS - SPRING | CC | [6 empty] | Parameters - CC |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Spring | CC | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MAX_SUST_RTG_SP |  | 1.Seasonal Net Max Sustainable Rating - Spring should be > Seasonal Net Min Sustainable Rating. 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
Seasonal Net Min Sustainable Rating - Spring | CC | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MIN_SUST_RTG_SP |  | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
Seasonal Net Max Emergency Rating - Spring | CC | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MAX_EMGY_RTG_SP |  | 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
Seasonal Net Min Emergency Rating - Spring | CC | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MIN_EMGY_RTG_SP |  | 1.Seasonal Net Min Emergency Rating - Spring < = Seasonal Net Min Sustainable Rating - Spring. 2.Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
SEASONAL RATINGS - SUMMER | CC | [6 empty] | Parameters - CC |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Summer | CC | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MAX_SUST_RTG_SM |  | 1.Seasonal Net Max Sustainable Rating - Summer > Seasonal Net Min Sustainable Rating - Summer. 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
Seasonal Net Min Sustainable Rating - Summer | CC | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MIN_SUST_RTG_SM |  | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
Seasonal Net Max Emergency Rating - Summer | CC | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MAX_EMGY_RTG_SM |  | 1.Seasonal Net Max Emergency Rating -Summer > Seasonal Net Min Emergency Rating - Summer. 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3.Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
Seasonal Net Min Emergency Rating - Summer | CC | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MIN_EMGY_RTG_SM |  | 1.Seasonal Net Min Emergency Rating - Summer < = Seasonal Net Min Sustainable Rating - Summer. 2.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
SEASONAL RATINGS - FALL | CC | [6 empty] | Parameters - CC |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Fall | CC | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MAX_SUST_RTG_FL |  | 1.Seasonal Net Max Sustainable Rating - Fall > Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
Seasonal Net Min Sustainable Rating - Fall | CC | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MIN_SUST_RTG_FL |  | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall. 2.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
Seasonal Net Max Emergency Rating - Fall | CC | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MAX_EMGY_RTG_FL |  | 1.Seasonal Net Max Emergency Rating - Fall > Seasonal Net Min Emergency Rating - Fall. 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
Seasonal Net Min Emergency Rating - Fall | CC | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MIN_EMGY_RTG_FL |  | 1.Seasonal Net Min Emergency Rating - Fall < = Seasonal Net Min Sustainable Rating - Fall. 2.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
SEASONAL RATINGS - WINTER | CC | [6 empty] | Parameters - CC |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Winter | CC | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MAX_SUST_RTG_WT |  | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
Seasonal Net Min Sustainable Rating - Winter | CC | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MIN_SUST_RTG_WT |  | 1.Seasonal Net Min Sustainable Rating - Winter >= Seasonal Net Min Emergency Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
Seasonal Net Max Emergency Rating - Winter | CC | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MAX_EMGY_RTG_WT |  | 1.Seasonal Net Max Emergency Rating - Winter > Seasonal Net Min Emergency Rating - Winter. 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
Seasonal Net Min Emergency Rating - Winter | CC | [5 empty] | UPDATE 02/2012 | Parameters - CC | MW | CCUNIT | SEASON_NET_MIN_EMGY_RTG_WT |  | 1.Seasonal Net Min Emergency Rating - Winter < = Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES | CC | [6 empty] | Parameters - CC |  | Not in table | Not in table
0°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
5°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
10°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
15°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
20°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
25°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
30°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
35°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
40°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
45°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
50°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
55°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
60°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
65°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
70°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
75°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
80°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
85°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
90°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
95°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
100°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
105°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
110°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
115°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
120°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CC | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
Parameters - CFG | CC | [6 empty] | Parameters - CFG |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type selected is 'CC'. This tab is required for Configurations. | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,MMS,NMMS
GENERATOR DETAILS | CC | [6 empty] | Parameters - CFG |  | Not in table | Not in table
SITECODE | CC | [5 empty] | ADD 02/2012 | Parameters - CFG | List | CONFIGURATIONS | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
Train Code | CC | Corrected 02/23/2012 |  |  |  |  | ADD 02/2012 | Parameters - CFG | List | TRAIN | TRAIN_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Configuration Code | CC | [5 empty] | ADD 02/2012 | Parameters - CFG | List | CONFIGURATIONS & DERATING | CONFIG_CODE
REASONABILITY LIMITS | CC | [6 empty] | Parameters - CFG |  | Not in table | Not in table
High Reasonability Limit | CC | PHASE II Updated 03/06/2012 Added Step 4, 5 and 6 |  |  |  |  | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | HR_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit 4. Generate a warning if HRL (NET) is greater than Real Power Rating(Gross). 5. Sum (HRL) of PRIMARY physical CCU component within the combined cycle configuration must be greater than or equal to the HRL of configuration itself. | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
Low Reasonability Limit | CC | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | LR_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
High Reasonability Ramp Rate Limit | CC | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW/min | CONFIGURATIONS | HR_RAMPRATE_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | EMS,MMS,NMMS
Low Reasonability Ramp Rate Limit | CC | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW/min | CONFIGURATIONS | LR_RAMP_RATE_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | EMS,MMS,NMMS
SEASONAL RATINGS - SPRING | CC | [6 empty] | Parameters - CFG |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Spring | CC | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MAX_SUST_RTG_SP |  | 1.Seasonal Net Max Sustainable Rating - Spring > Seasonal Net Min Sustainable Rating - Spring. 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS,NMMS
Seasonal Net Min Sustainable Rating - Spring | CC | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MIN_SUST_RTG_SP |  | 1.Seasonal Net Max Sustainable Rating - Spring > Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 3.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS,NMMS
Seasonal Net Max Emergency Rating - Spring | CC | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MAX_EMGY_RTG_SP |  | 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS,NMMS
Seasonal Net Min Emergency Rating - Spring | CC | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MIN_EMGY_RTG_SP |  | 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Emergency Rating - Spring < = Seasonal Net Min Sustainable Rating - Spring. 3.Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS,NMMS
SEASONAL RATINGS - SUMMER | CC | [6 empty] | Parameters - CFG |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Summer | CC | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MAX_SUST_RTG_SM |  | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer. 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
Seasonal Net Min Sustainable Rating - Summer | CC | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MIN_SUST_RTG_SM |  | 1.Seasonal Net Max Sustainable Rating - Summer > Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
Seasonal Net Max Emergency Rating - Summer | CC | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MAX_EMGY_RTG_SM |  | 1.Seasonal Net Max Emergency Rating - Summer > Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3.Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
Seasonal Net Min Emergency Rating - Summer | CC | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MIN_EMGY_RTG_SM |  | 1.Seasonal Net Max Emergency Rating - Summer > Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Emergency Rating - Summer < = Seasonal Net Min Sustainable Rating - Summer. 3.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
SEASONAL RATINGS - FALL | CC | [6 empty] | Parameters - CFG |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Fall | CC | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MAX_SUST_RTG_FL |  | 1.Seasonal Net Max Sustainable Rating - Fall > Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
Seasonal Net Min Sustainable Rating - Fall | CC | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MIN_SUST_RTG_FL |  | Seasonal Net Max Emergency Rating - Summer > Seasonal Net Min Emergency Rating - Summer | R | Numeric | B,DVB | Lin Xu | MMS
Seasonal Net Max Emergency Rating - Fall | CC | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MAX_EMGY_RTG_FL |  | 1.Seasonal Net Max Emergency Rating - Fall > Seasonal Net Min Emergency Rating - Fall. 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
Seasonal Net Min Emergency Rating - Fall | CC | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MIN_EMGY_RTG_FL |  | 1.Seasonal Net Max Emergency Rating - Fall > Seasonal Net Min Emergency Rating - Fall. 2.Seasonal Net Min Emergency Rating - Fall < = Seasonal Net Min Sustainable Rating - Fall. 3.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
SEASONAL RATINGS - WINTER | CC | [6 empty] | Parameters - CFG |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Winter | CC | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MAX_SUST_RTG_WT |  | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
Seasonal Net Min Sustainable Rating - Winter | CC | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MIN_SUST_RTG_WT |  | 1.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Min Emergency Rating - Fall. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
Seasonal Net Max Emergency Rating - Winter | CC | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MAX_EMGY_RTG_WT |  | 1.Seasonal Net Max Emergency Rating - Winter > Seasonal Net Min Emergency Rating - Winter. 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
Seasonal Net Min Emergency Rating - Winter | CC | [5 empty] | UPDATE 02/2012 | Parameters - CFG | MW | CONFIGURATIONS | SEASON_NET_MIN_EMGY_RTG_WT |  | 1.Seasonal Net Max Emergency Rating - Winter > Seasonal Net Min Emergency Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter < = Seasonal Net Min Sustainable Rating - Winter. 3.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Wei Hui | MMS
UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES | CC | [6 empty] | Parameters - CFG |  | Not in table | Not in table
0°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
5°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
10°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
15°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
20°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
25°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
30°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
35°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
40°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
45°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
50°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
55°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
60°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
65°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
70°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
75°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
80°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
85°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
90°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
95°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
100°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
105°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
110°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
115°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
120°f | CC | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - CFG | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
Parameters - WIND | Wind | [6 empty] | Parameters - Wind |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type selected is 'WIND ' | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,MMS,NMMS
Generator Details | Wind | [6 empty] | Parameters - Wind |  | Not in table | Not in table
Unit Name | Wind | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Parameters - Wind | List | WIND | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Wind | [5 empty] | ADD 02/2012 | Parameters - Wind | Automatic | WIND & DERATING | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
Reasonability Limits | Wind | [6 empty] | Parameters - Wind |  | Not in table | Not in table
High Reasonability Limit | Wind | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | HR_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
Low Reasonability Limit | Wind | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | LR_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
High Reasonability Ramp Rate Limit | Wind | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW/min | WIND | HR_RAMPRATE_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | EMS,MMS,NMMS
Low Reasonability Ramp Rate Limit | Wind | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW/min | WIND | LR_RAMP_RATE_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | Lin Xu/Jamil Daouk | EMS,MMS,NMMS
Seasonal Ratings Spring | Wind | [6 empty] | Parameters - Wind |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Spring | Wind | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MAX_SUST_RTG_SP |  | 1.Seasonal Net Max Sustainable Rating - Spring > Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
Seasonal Net Min Sustainable Rating - Spring | Wind | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MIN_SUST_RTG_SP |  | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
Seasonal Net Max Emergency Rating - Spring | Wind | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MAX_EMGY_RTG_SP |  | 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
Seasonal Net Min Emergency Rating - Spring | Wind | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MIN_EMGY_RTG_SP |  | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS,NMMS
Seasonal Ratings Summer | Wind | [6 empty] | Parameters - Wind |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Summer | Wind | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MAX_SUST_RTG_SM |  | 1.Seasonal Net Max Sustainable Rating - Summer > Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Seasonal Net Min Sustainable Rating - Summer | Wind | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MIN_SUST_RTG_SM |  | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Seasonal Net Max Emergency Rating - Summer | Wind | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MAX_EMGY_RTG_SM |  | 1.Seasonal Net Max Emergency Rating - Summer > Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Seasonal Net Min Emergency Rating - Summer | Wind | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MIN_EMGY_RTG_SM |  | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Seasonal Ratings Fall | Wind | [6 empty] | Parameters - Wind |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Fall | Wind | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MAX_SUST_RTG_FL |  | 1.Seasonal Net Max Sustainable Rating - Fall > Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Seasonal Net Min Sustainable Rating - Fall | Wind | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MIN_SUST_RTG_FL |  | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall. >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Seasonal Net Max Emergency Rating - Fall | Wind | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MAX_EMGY_RTG_FL |  | 1.Seasonal Net Max Emergency Rating - Fall > Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Seasonal Net Min Emergency Rating - Fall | Wind | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MIN_EMGY_RTG_FL |  | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Seasonal Ratings Winter | Wind | [6 empty] | Parameters - Wind |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Winter | Wind | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MAX_SUST_RTG_WT |  | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Seasonal Net Min Sustainable Rating - Winter | Wind | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MIN_SUST_RTG_WT |  | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Seasonal Net Max Emergency Rating - Winter | Wind | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MAX_EMGY_RTG_WT |  | 1.Seasonal Net Max Emergency Rating - Winter > Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
Seasonal Net Min Emergency Rating - Winter | Wind | [5 empty] | UPDATE 02/2012 | Parameters - Wind | MW | WIND | SEASON_NET_MIN_EMGY_RTG_WT |  | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/WeiHui | MMS
UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES | Wind | [6 empty] | Parameters - Wind |  | Not in table | Not in table
0°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
5°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
10°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
15°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
20°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
25°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
30°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
35°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
40°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
45°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
50°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
55°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
60°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
65°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
70°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
75°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
80°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
85°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
90°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
95°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
100°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
105°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
110°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
115°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
120°f | Wind | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Wind | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
Operational Parameters - GEN | Generation | [6 empty] | Operational Parameters - GEN |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type Selected is 'GEN' where GEN is non-CC non-wind Generation Resources. | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | MMS,NMMS
GENERATOR DETAILS | Generation | [6 empty] | Operational Parameters - GEN |  | Not in table | Not in table
Unit Name | Generation | Do not show Message on Audit or Delta |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 02/2012 | Operational Parameters - GEN | List | GENERATION | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Generation |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 02/2012 | Operational Parameters - GEN | Automatic | GENERATION | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
RESOURCE PARAMETERS | Generation | [6 empty] | Operational Parameters - GEN |  | Not in table | Not in table
Minimum On Line Time | Generation | Check |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN | hours | GENERATION | MIN_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum On Line Time >= 0 | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Minimum Off Line Time | Generation | Check |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN | hours | GENERATION | MIN_OFFLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum Off Line Time >= 0 | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Hot Start Time | Generation | Corrected |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN | hours | GENERATION | HOTSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot Start Time >= 0 3. Hot Start Time <= Intermediate Start Time | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Intermediate Start Time | Generation | Corrected |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN | hours | GENERATION | INTERMSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate Start Time >= 0 3. Cold Start Time >= Intermediate Start Time >= Hot Start Time | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Cold Start Time | Generation | Corrected |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN | hours | GENERATION | COLDSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Cold Start Time >= 0 3. Cold Start Time >= Intermediate Start Time | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Max Weekly Starts | Generation | Check |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN |  | GENERATION | MAXWKLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Max On Line Time | Generation | Corrected |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN | hours | GENERATION | MAX_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Max OnLine Time > 0 | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Max Daily Starts | Generation | Check |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN |  | GENERATION | MAXDLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Daily Start >= 0 3. Max Daily Start <= 999 | R | Integer | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Max Weekly Energy | Generation | Corrected |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN | MWh | GENERATION | MAXWKLYENRGY |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Energy >= 0 3. Max Weekly Energy < 1e10 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Hot-to-Intermediate Time | Generation | Check |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN | hours | GENERATION | HOT_TO_INTMDT_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot-to-Intermediate Time >= 0 | R | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | NMMS
Intermediate-to-Cold Time | Generation | Check |  | Passed/MNSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN | hours | GENERATION | INTMDT_TO_COLD_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate-to-Cold Time >= 0 | R | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | NMMS
Operational Parameters - GEN - NRRC | Generation | [6 empty] | Operational Parameters - GEN - NRRC |  | Not in table | Not in table
Generator Details | Generation | [6 empty] | Operational Parameters - GEN - NRRC |  | Not in table | Not in table
Unit Name | Generation | Do not show Message on Audit or Delta |  | UNIT_NAME field has not been added to Ramp Rate NRRC TABLE/ FAILED |  |  | ADD 02/2012 | Operational Parameters - GEN - NRRC | List | GENERATION | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Generation |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 02/2012 | Operational Parameters - GEN - NRRC | List | RAMP_RATES_NRRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Normal Ramp Rate Curve | Generation | [6 empty] | Operational Parameters - GEN - NRRC |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit. |  |  |  |  | NMMS
MW Number | Generation | [6 empty] | Operational Parameters - GEN - NRRC | List | RAMP_RATES_NRRC | MW_NUMBER_NRRC
NRRC Code | Generation |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | UPDATE 02/2012 | Operational Parameters - GEN - NRRC | Automatic | RAMP_RATES_NRRC | UNIT_MW_NRRC |  | Capture Unit Code and UNIT MW Number and NRRC, prepopulate this field with UNIT_CODE_UNIT_MW_NUMBER_NRRC. | R | Character
NRRC MW | Generation | PHASE II Updated 03/06/2012 Added Step 5 and 6 |  | Passed/DCSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN - NRRC | MW | RAMP_RATES_NRRC | MW_RATING_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric | B | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS
Upward Ramprate | Generation | Check |  | Passed/DCSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN - NRRC | MW/min | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2.. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Downward Ramprate | Generation | Check |  | Passed/DCSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN - NRRC | MW/min | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Operational Parameters - GEN - ERRC | Generation | [6 empty] | Operational Parameters - GEN - ERRC |  | Not in table | Not in table
Generator Details | Generation | [6 empty] | Operational Parameters - GEN - ERRC |  | Not in table | Not in table
Unit Name | Generation | Do not show Message on Audit or Delta |  | UNIT_NAME field has not been added to Ramp Rate ERRC TABLE/ FAILED |  |  | ADD 02/2012 | Operational Parameters - GEN - ERRC | List | GENERATION | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Generation |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 02/2012 | Operational Parameters - GEN - ERRC | List | RAMP_RATES_ERRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Emergency Ramp Rate Curve | Generation | [6 empty] | Operational Parameters - GEN - ERRC |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit. |  |  |  | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS
MW Number | Generation | [6 empty] | Operational Parameters - GEN - NRRC | List | RAMP_RATES_ERRC | MW_NUMBER_ERRC
ERRC Code | Generation |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | UPDATE 02/2012 | Operational Parameters - GEN - NRRC | Automatic | RAMP_RATES_ERRC | UNIT_MW_ERRC |  | Capture Unit Code and UNIT MW Number and ERRC, prepopulate this field with UNIT_CODE_UNIT_MW_NUMBER_ERRC. | R | Character
ERRC MW | Generation | PHASE II Updated 03/06/2012 Added Step 5 and 6 |  | Passed/DCSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN - NRRC | MW | RAMP_RATES_NRRC | MW_RATING_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric | B | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS
Upward Ramprate | Generation | Updated 03/06/2012 |  | Passed/DCSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN - ERRC | MW/min | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Downward Ramprate | Generation |  |  | Passed/DCSES |  |  | UPDATE 02/2012 | Operational Parameters - GEN - ERRC | MW/min | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Operational Parameters - CFG | CC | [6 empty] | Operational Parameters - CFG |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type selected is 'CC'. Can register up to 3 trains at one site. This tab is required for Configurations. | C |  |  | RARF Guide Version 4.0 | MMS,NMMS
GENERATOR DETAILS | CC | [6 empty] | Operational Parameters - CFG |  | Not in table | Not in table
SITECODE | CC | [5 empty] | ADD 02/2012 | Operational Parameters - CFG | List | CONFIGURATIONS | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
Train Code | CC | [5 empty] | ADD 02/2012 | Operational Parameters - CFG | List | TRAIN | TRAIN_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Configuration Code | CC | [5 empty] | ADD 02/2012 | Operational Parameters - CFG | List | CONFIGURATIONS | CONFIG_CODE |  | Required | R
RESOURCE PARAMETERS | CC | [6 empty] | Operational Parameters - CFG |  | Not in table | Not in table
Minimum On Line Time | CC | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG | hours | CONFIGURATIONS | MIN_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum On Line Time >= 0 | R | Integer | B,DVB | KittiPong/Jamil Daouk | MMS,NMMS
Minimum Off Line Time | CC | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG | hours | CONFIGURATIONS | MIN_OFFLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum Off Line Time >= 0 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Hot Start Time | CC | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG | hours | CONFIGURATIONS | HOTSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot Start Time >= 0 3. Hot Start Time <= Intermediate Start Time | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Intermediate Start Time | CC | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG | hours | CONFIGURATIONS | INTERMSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate Start Time >= 0 3. Cold Start Time >= Intermediate Start Time >= Hot Start Time | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Cold Start Time | CC | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG | hours | CONFIGURATIONS | COLDSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Cold Start Time >= 0 3. Cold Start Time >= Intermediate Start Time | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Max Weekly Starts | CC | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG |  | CONFIGURATIONS | MAXWKLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Max On Line Time | CC | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG | hours | CONFIGURATIONS | MAX_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Max OnLine Time > 0 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Max Daily Starts | CC | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG |  | CONFIGURATIONS | MAXDLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Daily Start >= 0 3. Max Daily Start <= 999 | R | Numeric | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Max Weekly Energy | CC | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG | MWh | CONFIGURATIONS | MAXWKLYENRGY |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Energy >= 0 3. Max Weekly Energy < 1e10 | R | Integer | B,DVB | Lin Xu/Kittipong | MMS,NMMS
Hot-to-intermediate Time | CC | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG | hours | CONFIGURATIONS | HOT_TO_INTMDT_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot-to-Intermediate Time >= 0 | R | Integer | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
Intermediate-to-cold Time | CC | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG | hours | CONFIGURATIONS | INTMDT_TO_COLD_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate-to-Cold Time >= 0 | R | Integer | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
Operational Parameters - NRRC | CC | [6 empty] | Operational Parameters - CFG - NRRC |  | Not in table | Not in table
Generator Details | CC | [6 empty] | Operational Parameters - CFG - NRRC |  | Not in table | Not in table
Train Code | CC | Corrected 02/23/2012 |  |  |  |  | ADD 02/2012 | Operational Parameters - CFG - NRRC | List | TRAIN RAMP_RATES_NRRC | TRAIN_CODE UNIT_CODE |  | 1.This field is Not null: Capture UNIT Code and Configuration Code and prepopulate this field with TRAIN _Config_Code. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Configuration Code | CC | [5 empty] | ADD 02/2012 | Operational Parameters - CFG - NRRC | List | CONFIGURATIONS | CONFIG_CODE |  | Required Field | R | Character | B,DVB
NORMAL RAMP RATE CURVE | CC | [6 empty] | Operational Parameters - CFG - NRRC |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit. |  | Numeric | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS
MW Number | CC | [7 empty] | List | RAMP_RATES_NRRC | MW_NUMBER_NRRC
NRRC Code | CC | [5 empty] | UPDATE 02/2012 | Operational Parameters - CFG - NRRC | Automatic | RAMP_RATES_NRRC | UNIT_MW_NRRC |  | This Field is Not in the RARF: Capture Unit Code and UNIT MW Number and NRRC, prepopulate this field with UNIT_CODE_UNIT_MW_NUMBER_NRRC. | R | Character
NRRC MW | CC | PHASE II Updated 03/06/2012 Added Step 5 and 6 |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG - NRRC | MW | RAMP_RATES_NRRC | MW_RATING_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric | B | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS
Upward Ramprate | CC | Updated 03/06/2012 |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG - NRRC | MW/min | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Downward Ramprate | CC | [5 empty] | UPDATE 02/2012 | Operational Parameters - CFG - NRRC | MW/min | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Operational Parameters - ERRC | CC | [6 empty] | Operational Parameters - CFG - ERRC |  | Not in table | Not in table
Generator Details | CC | [6 empty] | Operational Parameters - CFG - ERRC |  | Not in table | Not in table
Train Code | CC | Corrected 02/23/2012 |  |  |  |  | ADD 02/2012 | Operational Parameters - CFG - ERRC | List | TRAIN RAMP RAMP_RATES_ERRC | TRAIN_CODE UNIT_CODE |  | 1.This field is Not null: Capture Train Code and Configuration Code and prepopulate this field with Train_Code _Config_Code. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Configuration Code | CC | [5 empty] | ADD 02/2012 | Operational Parameters - CFG - ERRC | List | CONFIGURATIONS | CONFIG_CODE |  | Required Field | R | Character | B,DVB
EMERGENCY RAMP RATE CURVE | CC | [6 empty] | Operational Parameters - CFG - ERRC |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit. |  |  |  | RARF Guide Version 4.0 | NMMS
MW Number | CC | [6 empty] | Operational Parameters - CFG - ERRC | List | RAMP_RATES_ERRC | MW_NUMBER_ERRC
ERRC Code | CC | [5 empty] | UPDATE 02/2012 | Operational Parameters - CFG - ERRC | Automatic | RAMP_RATES_ERRC | UNIT_MW_ERRC |  | Capture Unit Code and UNIT MW Number and ERRC, prepopulate this field with UNIT_CODE_UNIT_MW_NUMBER_ERRC. | R | Character
ERRC MW | CC | PHASE II Updated 03/06/2012 Added Step 5 and 6 |  |  |  |  | UPDATE 02/2012 | Operational Parameters - CFG - ERRC | MW | RAMP_RATES_NRRC | MW_RATING_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric | B | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS
Upward Ramprate | CC | [5 empty] | UPDATE 02/2012 | Operational Parameters - CFG - ERRC | MW/min | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Downward Ramprate | CC | [5 empty] | UPDATE 02/2012 | Operational Parameters - CFG - ERRC | MW/min | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Operational Parameters - WIND | Wind | [6 empty] | Operational Parameters - Wind |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Resource Type Selected is 'WIND units' | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | MMS,NMMS
Unit Name | Wind | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Operational Parameters - Wind |  | WIND | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Wind | [5 empty] | ADD 02/2012 | Operational Parameters - Wind |  | WIND | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
RESOURCE PARAMETERS | Wind | [6 empty] | Operational Parameters -Wind |  | Not in table | Not in table
Minimum On Line Time | Wind | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind | hours | WIND | MIN_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum On Line Time >= 0 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Minimum Off Line Time | Wind | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind | hours | WIND | MIN_OFFLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum Off Line Time >= 0 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Hot Start Time | Wind | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind | hours | WIND | HOTSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot Start Time >= 0 3. Hot Start Time <= Intermediate Start Time | O | Integer | B,DVB | Angela Moy/Jamil Daouk | NMMS
Intermediate Start Time | Wind | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind | hours | WIND | INTERMSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate Start Time >= 0 3. Cold Start Time >= Intermediate Start Time >= Hot Start Time | O | Integer | B,DVB | Angela Moy/Jamil Daouk | NMMS
Cold Start Time | Wind | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind | hours | WIND | COLDSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Cold Start Time >= 0 3. Cold Start Time >= Intermediate Start Time | O | Integer | B,DVB | Angela Moy/Jamil Daouk | NMMS
Max Weekly Starts | Wind | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind |  | WIND | MAXWKLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Integer | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
Max On Line Time | Wind | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind | hours | WIND | MAX_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Max OnLine Time > 0 | R | Integer | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
Max Daily Starts | Wind | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind |  | WIND | MAXDLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Daily Start >= 0 3. Max Daily Start <= 999 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Max Weekly Energy | Wind | Corrected |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind | MWh | WIND | MAXWKLYENRGY |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Energy >= 0 3. Max Weekly Energy < 1e10 | R | Numeric | B,DVB | Lin Xu | MMS,NMMS
Hot-to-Intermediate Time | Wind | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind | hours | WIND | HOT_TO_INTMDT_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot-to-Intermediate Time >= 0 | R | Integer | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
Intermediate-to-Cold Time | Wind | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind | hours | WIND | INTMDT_TO_COLD_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate-to-Cold Time >= 0 | R | Integer | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
Operational Parameters - Wind - NRRC | Wind | [6 empty] | Operational Parameters - Wind - NRRC |  | Not in table | Not in table
Generator Details | Wind | [6 empty] | Operational Parameters - Wind - NRRC |  | Not in table | Not in table
Unit Name | Wind | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Operational Parameters - Wind - NRRC | List | WIND | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Wind | [5 empty] | ADD 02/2012 | Operational Parameters - Wind - NRRC | List | RAMP_RATES_NRRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Normal Ramp Rate Curve | Wind | [6 empty] | Operational Parameters - Wind - NRRC |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit.
MW Number | Wind | [6 empty] | Operational Parameters - Wind - NRRC | List | RAMP_RATES_NRRC | MW_NUMBER_NRRC
NRRC Code | Wind | [5 empty] | UPDATE 02/2012 | Operational Parameters - Wind - NRRC | Automatic | RAMP_RATES_NRRC | UNIT_MW_NRRC |  | Capture Unit Code and UNIT MW Number and NRRC, prepopulate this field with UNIT_CODE_UNIT_MW_NUMBER_NRRC. | R | Character
NRRC MW | Wind | PHASE II Updated 03/06/2012 Added Step 5 and 6 |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind - NRRC | MW | RAMP_RATES_NRRC | MW_RATING_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric | B | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS
Upward Ramprate | Wind | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind - NRRC | MW/min | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Downward Ramprate | Wind | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind - NRRC | MW/min | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Operational Parameters - Wind - ERRC | Wind | [6 empty] | Operational Parameters - Wind - ERRC |  | Not in table | Not in table
Generator Details | Wind | [6 empty] | Operational Parameters - Wind - ERRC |  | Not in table | Not in table
Unit Name | Wind | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Operational Parameters - Wind - ERRC | List | WIND | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Wind | [5 empty] | ADD 02/2012 | Operational Parameters - Wind - ERRC | List | RAMP_RATES_ERRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Emergency Ramp Rate Curve | Wind | [6 empty] | Operational Parameters - Wind - ERRC |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit.
MW Number | Wind | [6 empty] | Operational Parameters - Wind - ERRC | List | RAMP_RATES_ERRC | MW_NUMBER_ERRC
ERRC Code | Wind | [5 empty] | UPDATE 02/2012 | Operational Parameters - Wind - ERRC | Automatic | RAMP_RATES_ERRC | UNIT_MW_ERRC |  | Capture Unit Code and Unit MW Number and prepopulate this field with Unit CODE_UNIT_MW_NUMBER_ERRC. | R | Character
ERRC MW | Wind | PHASE II Updated 03/06/2012 Added Step 5 and 6 |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind - ERRC | MW | RAMP_RATES_NRRC | MW_RATING_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric | B | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk/KittiPong 11/08/11 | NMMS
Upward Ramprate | Wind | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind - ERRC | MW/min | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Downward Ramprate | Wind | Check |  |  |  |  | UPDATE 02/2012 | Operational Parameters - Wind - ERRC | MW/min | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Reactive Capability - GEN | Generation | [6 empty] | Reactive Capability - GEN |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type Selected is 'GEN' where GEN is non-CC non-wind Generation Resources. All the fields in this tab should be filled in. | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,MMS,NMMS
GENERATOR DETAILS | Generation | [6 empty] | Reactive Capability - GEN |  | Not in table | Not in table
Unit Name | Generation | Do not show Message on Audit or Delta |  | Passed/DCSES |  |  | ADD 02/2012 | Reactive Capability - GEN | List | GENERATION | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Generation |  |  | Passed/DCSES |  |  | ADD 02/2012 | Reactive Capability - GEN | Automatic | GENERATION | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
REACTIVE CAPABILITY CURVES DETAILS | Generation | [6 empty] | Reactive Capability - GEN |  | Not in table | Not in table
Reactive Capability Data Provided Below Is Gross/net Values? | Generation | [5 empty] | ADD 04/2012 | Reactive Capability - GEN | List | GENERATION | REACT_CAPB_DATA_GROSS_NET_VAL |  | Select from the list: Y or N |  | Dropdown List
Reactive Capability Data Provided Below Is From Ndcrc Test Data? | Generation | [5 empty] | ADD 04/2012 | Reactive Capability - GEN | Y/N | GENERATION | REACT_CAPB_NDCRC_TEST_DATA |  | Select from the list: Y or N |  | Dropdown List
If Reactive Capability Data Provided Below Is From Ndcrc Test Data Then Enter The Date On Which The Test Was Performed. | Generation | [5 empty] | ADD 04/2012 | Reactive Capability - GEN | mm/dd/yyyy | GENERATION | REACT_CAPB_NDCRC_TEST_DATA_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date
MW1 | Generation | [6 empty] | Reactive Capability - GEN | MW | GENERATION | MW1 |  | 1. MW1 >=0 .1 2. MW1<MW2. 3. X(1) <= WMN(Unit Minimal output) where X(1) represents MW1( Generate a Warning Only when Business Rule#2 fails) | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS
Lagging MVAR limit associated with MW1 output | Generation | [6 empty] | Reactive Capability - GEN | MVAR | GENERATION | MVAR1LAG |  | 1. Lagging MVAR limit associated with MW1 output >=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS
Leading MVAR limit associated with MW1 output | Generation | [6 empty] | Reactive Capability - GEN | MVAR | GENERATION | MVAR1LEAD |  | 1. Leading MVAR limit associated with MW1 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS
MW2 | Generation | [6 empty] | Reactive Capability - GEN | MW | GENERATION | MW2 |  | 1. MW2>0 2. MW2<MW3 | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS
Lagging MVAR limit associated with MW2 output | Generation | [6 empty] | Reactive Capability - GEN | MVAR | GENERATION | MVAR2LAG |  | 1.Lagging MVAR limit associated with MW2 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS
Leading MVAR limit associated with MW2 output | Generation | [6 empty] | Reactive Capability - GEN | MVAR | GENERATION | MVAR2LEAD |  | 1. Leading MVAR limit associated with MW2 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS
MW3 | Generation | [6 empty] | Reactive Capability - GEN | MW | GENERATION | MW3 |  | 1. MW3 >0 2. MW3<MW4 | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS
Lagging MVAR limit associated with MW3 output | Generation | [6 empty] | Reactive Capability - GEN | MVAR | GENERATION | MVAR3LAG |  | 1. Lagging MVAR limit associated with MW3 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS
Leading MVAR limit associated with MW3 output | Generation | [6 empty] | Reactive Capability - GEN | MVAR | GENERATION | MVAR3LEAD |  | 1.Leading MVAR limit associated with MW3 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS
MW4 | Generation | [6 empty] | Reactive Capability - GEN | MW | GENERATION | MW4 |  | 1. MW4 >0 2. MW4<MW5 3. X(n) > = WMX (Unit Max output) where n is the last MW value in the curve. If the curve has 4 points, X(n) is X(4) [ Generate a Warning Only When Business Rule#2 Fails] | R | Numeric | B,DVB | Lin Xu/ WeiHui | EMS,NMMS
Lagging MVAR limit associated with MW4 output | Generation | [6 empty] | Reactive Capability - GEN | MVAR | GENERATION | MVAR4LAG |  | 1. Lagging MVAR limit associated with MW4 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS
Leading MVAR limit associated with MW4 output | Generation | [6 empty] | Reactive Capability - GEN | MVAR | GENERATION | MVAR4LEAD |  | 1.Leading MVAR limit associated with MW4 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS
MW5 - Unity Power Factor | Generation | [6 empty] | Reactive Capability - GEN | MW | GENERATION | MW5UNITYPF |  | 1. MW5 >0 2. MW5 >MW4 | R | Numeric | B,DVB | Lin Xu | MMS,NMMS
If hydrogen cooled, indicate hydrogen pressure (psi) associated with your Reactive Curve submitted for ERCOT studies | Generation | [6 empty] | Reactive Capability - GEN | PSI | GENERATION | HYDROCOOLED |  | Data type is Numeric | O | Numeric | B | Angela Moy\RARF Guide Version 4.0/RARF Glossary Version 4.0
Maximum Leading Operating Capability (MVAR) | Generation | [6 empty] | Reactive Capability - GEN | MVAR | GENERATION | NETMAXLEAD |  | 1.Net Maximum Leading Operating Capability <=0 | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,MMS
Maximum Lagging Operating Capability (MVAR) | Generation | [6 empty] | Reactive Capability - GEN | MVAR | GENERATION | NETMAXLAG |  | 1.Net Maximum Lagging Operating Capability >=0 2. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,MMS
Manufacturer's Capability Curve submitted? | Generation | [6 empty] | Reactive Capability - GEN | Y/N | GENERATION | MFR_CAPABILITY_CURVE_FLG |  | Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0
Reactive Capability - CC | CC | [6 empty] | Reactive Capability - CC |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type selected is 'Combined Cycle '. Required for each configuration. All the fields in this tab should be filled. | C |  |  |  | EMS,MMS,NMMS
GENERATOR DETAILS | CC | [6 empty] | Reactive Capability - CC |  | Not in table | Not in table
Unit Name | CC | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Reactive Capability - CC | List | CCUNIT | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
SITE_CODE | CC | [5 empty] | ADD 02/2012 | Reactive Capability - CC | Automatic | CCUNIT | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
Resource Name (Unit Code/Mnemonic) | CC | [5 empty] | ADD 02/2012 | Reactive Capability - CC | Automatic | CCUNIT | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
REACTIVE CAPABILITY CURVES DETAILS | CC | [6 empty] | Reactive Capability - CC |  | Not in table | Not in table |  | 4. Can not exceed 13 characters for split gen resources
Reactive Capability Data Provided is Gross/Net Values? | CC | [5 empty] | ADD 04/2012 | Reactive Capability - CC | List | CCUNIT | REACT_CAPB_DATA_GROSS_NET_VAL |  | Select from the list: Y or N |  | Dropdown List
Reactive Capability Data Provided is from NDCRC Test Data? | CC | [5 empty] | ADD 04/2012 | Reactive Capability - CC | Y/N | CCUNIT | REACT_CAPB_NDCRC_TEST_DATA |  | Select from the list: Y or N |  | Dropdown List
If Reactive Capability Data Provided Is From NDCRC test Data Then Enter The Date On Which The Test Was Performed. | CC | [5 empty] | ADD 04/2012 | Reactive Capability - CC | mm/dd/yyyy | CCUNIT | REACT_CAPB_NDCRC_TEST_DATA_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date
Mw1 | CC | [6 empty] | Reactive Capability - CC | MW | CCUNIT | MW1_GEN |  | 1. MW1 >=0 .1 2.MW1<MW2. 3. X(1) <= WMN(Unit Minimal output) where X(1) represents MW1( Generate a Warning Only when Business Rule#2 fails) | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS
Lagging MVAR Limit Associated With Mw1 Output | CC | [6 empty] | Reactive Capability - CC | MVAR | CCUNIT | MVAR1LAG_GEN |  | 1. Lagging MVAR limit associated with MW1 output >=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS
Leading MVAR Limit Associated With Mw1 Output | CC | [6 empty] | Reactive Capability - CC | MVAR | CCUNIT | MVAR1LEAD_GEN |  | 1. Leading MVAR limit associated with MW1 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS
Mw2 | CC | [6 empty] | Reactive Capability - CC | MW | CCUNIT | MW2_GEN |  | 1. MW2>0 2.MW2<MW3 | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS
Lagging MVAR Limit Associated With Mw2 Output | CC | [6 empty] | Reactive Capability - CC | MVAR | CCUNIT | MVAR2LAG_GEN |  | 1. Lagging MVAR limit associated with MW2 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS
Leading MVAR Limit Associated With Mw2 Output | CC | [6 empty] | Reactive Capability - CC | MVAR | CCUNIT | MVAR2LEAD_GEN |  | 1. Leading MVAR limit associated with MW2 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS
Mw3 | CC | [6 empty] | Reactive Capability - CC | MW | CCUNIT | MW3_GEN |  | 1.MW3 >0 2.MW3<MW4 | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS
Lagging MVAR Limit Associated With Mw3 Output | CC | [6 empty] | Reactive Capability - CC | MVAR | CCUNIT | MVAR3LAG_GEN |  | 1. Lagging MVAR limit associated with MW3 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS
Leading MVAR Limit Associated With Mw3 Output | CC | [6 empty] | Reactive Capability - CC | MVAR | CCUNIT | MVAR3LEAD_GEN |  | 1. Leading MVAR limit associated with MW3 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS
Mw4 | CC | [6 empty] | Reactive Capability - CC | MW | CCUNIT | MW4_GEN |  | 1. MW4> 0 2.MW4<MW5 3. X(n) > = WMX (Unit Max output) where n is the last MW value in the curve. If the curve has 4 points, X(n) is X(4) [ Generate a Warning Only When Business Rule#2 Fails] | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS
Lagging MVAR Limit Associated With Mw4 Output | CC | [6 empty] | Reactive Capability - CC | MVAR | CCUNIT | MVAR4LAG_GEN |  | 1. Lagging MVAR limit associated with MW4 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS
Leading MVAR Limit Associated With Mw4 Output | CC | [6 empty] | Reactive Capability - CC | MVAR | CCUNIT | MVAR4LEAD_GEN |  | 1.MVAR limit associated with MW4 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS
Mw5 - Unity Power Factor | CC | [6 empty] | Reactive Capability - CC | MW | CCUNIT | MW5UNITYPF_GEN |  | 1. MW5 >0 2.MW5>MW4 | R | Numeric | B,DVB | Lin Xu | MMS,NMMS
If Hydrogen Cooled, Indicate Hydrogen Pressure (PSI) Associated With Your Reactive Curve Submitted For ERCOT Studies | CC | [6 empty] | Reactive Capability - CC | PSI | CCUNIT | HYDROCOOLED |  | Data type is Numeric | O | Numeric | B | Angela Moy/RARF Guide Version 4.0
Maximum Lagging Operating Capability | CC | [6 empty] | Reactive Capability - CC | MVAR | CCUNIT | NETMAXLEAD_GEN |  | 1. Net Maximum Leading Operating Capability <=0 | R | Numeric | B,DVB | Lin Xu | MMS
Maximum Leading Operating Capability | CC | [6 empty] | Reactive Capability - CC | MVAR | CCUNIT | NETMAXLAG_GEN |  | 1.Net Maximum Lagging Operating Capability >=0 2. Lagging MVAR must always be greater than the Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB | Lin Xu | MMS
Manufacturer's Capability Curve Submitted? | CC | [6 empty] | Reactive Capability - CC | Y/N | CCUNIT | MFR_CAPABILITY_CURVE_FLG |  | Select from Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0
Reactive Capability - WIND | Wind | [6 empty] | Reactive Capability - Wind |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type selected is 'WIND '. If the Unit Info-Wind tab shows multiple groups of turbines in a Unit, then the Reactive Curve tab must show the values for multiple groups, Produce an error if the corresponding data is missing in the Reactive Capability-Wind Tab. | C |  | B,DVB | Angela Moy | EMS,MMS,NMMS
GENERATOR DETAILS | Wind | [6 empty] | Reactive Capability - Wind |  | Not in table | Not in table
Reactive Standard? | Wind | [5 empty] | REMOVE | Reactive Capability - Wind |  | REACT_CAP_WIND |  |  | Select from the list: Y ,N, Capacitors Installed REMOVED | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 | EMS,NMMS
Unit Name | Wind | Removed From Wind Form |  |  |  |  | ADD 02/2012 | Reactive Capability - Wind | List | WIND | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Wind | [5 empty] | ADD 02/2012 | Reactive Capability - Wind | Automatic | REACT_CAP_WIND | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB
REACTIVE CAPABILITY CURVES DETAILS | Wind | [6 empty] | Reactive Capability - Wind |  | Not in table | Not in table
Reactive Capability Data Provided Below Is Gross/net Values? | Wind | Corrected List value Gross or Net 03/05/2012 |  |  |  |  | ADD 04/2012 | Reactive Capability - Wind | List | REACT_CAP_WIND | REACT_CAPB_DATA_GROSS_NET_VAL |  | Select from the list: Gross, Net |  | Dropdown List
Reactive Capability Data Provided Below Is From Ndcrc Test Data? | Wind | Corrected Label 03/05/2012 |  |  |  |  | ADD 04/2012 | Reactive Capability - Wind | Y/N | REACT_CAP_WIND | REACT_CAPB_NDCRC_TEST_DATA |  | Select from the list: Y or N |  | Dropdown List
If Reactive Capability Data Provided Below Is From Ndcrc Test Data Then Enter The Date On Which The Test Was Performed. | Wind | Corrected Label 03/05/2012 |  |  |  |  | ADD 04/2012 | Reactive Capability - Wind | mm/dd/yyyy | REACT_CAP_WIND | REACT_CAPB_NDCRC_TEST_DATA_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date
MW1 | Wind | Corrected Label 03/05/2012 | [5 empty] | Reactive Capability - Wind | MW | REACT_CAP_WIND | MW1 |  | 1. MW1 >=0.1 2.MW1<MW2. 3. X(1) <= WMN(Unit Minimal output or LRL) where X(1) represents MW1( Generate a Warning Only when this rule fails). This is a WARNING ONLY | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS
Lagging MVAR limit associated with MW1 output | Wind | Corrected Label 03/05/2012 | [5 empty] | Reactive Capability - Wind | MVAR | REACT_CAP_WIND | MVAR1LAG |  | 1. Lagging MVAR limit associated with MW1 output >=0. Generate a Warning only if LAG value is negative 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3) Generate a Warning only if LAG value is negative 4) Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS
Leading MVAR limit associated with MW1 output | Wind | Corrected Label 03/05/2012 | [5 empty] | Reactive Capability - Wind | MVAR | REACT_CAP_WIND | MVAR1LEAD |  | 1. Leading MVAR limit associated with MW1 output <=0 .Generate a Warning only if LEAD value is positive 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3) Generate a Warning only if LEAD value is positive | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS
MW2 | Wind | Corrected Label 03/05/2012 | [5 empty] | Reactive Capability - Wind | MW | REACT_CAP_WIND | MW2 |  | 1. MW2 >0 2. MW2<MW3 | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS
Lagging MVAR limit associated with MW2 output | Wind | Corrected Label 03/05/2012 | [5 empty] | Reactive Capability - Wind | MVAR | REACT_CAP_WIND | MVAR2LAG |  | 1. Lagging MVAR limit associated with MW2 output >=0 . Generate a Warning only if LAG value is negative 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Generate a Warning only if LAG value is negative 4. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS
Leading MVAR limit associated with MW2 output | Wind | Corrected Label 03/05/2012 | [5 empty] | Reactive Capability - Wind | MVAR | REACT_CAP_WIND | MVAR2LEAD |  | 1.Leading MVAR limit associated with MW2 output <=0 .Generate a Warning only if LEAD value is positive 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Generate a Warning only if LEAD value is positive | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS
MW3 | Wind | Corrected Label 03/05/2012 | [5 empty] | Reactive Capability - Wind | MW | REACT_CAP_WIND | MW3 |  | 1. MW3 >0 2.MW3<MW4 | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS
Lagging MVAR limit associated with MW3 output | Wind | Corrected Label 03/05/2012 | [5 empty] | Reactive Capability - Wind | MVAR | REACT_CAP_WIND | MVAR3LAG |  | 1Lagging MVAR limit associated with MW3 output >=0 .Generate a Warning only if LAG value is negative 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Generate a Warning only if LAG value is negative 4.Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS
Leading MVAR limit associated with MW3 output | Wind | Corrected Label 03/05/2012 | [5 empty] | Reactive Capability - Wind | MVAR | REACT_CAP_WIND | MVAR3LEAD |  | 1. Leading MVAR limit associated with MW3 output <=0 .Generate a Warning only if LEAD value is positive 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Generate a Warning only if LEAD value is positive | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS
MW4 | Wind | Corrected Label 03/05/2012 | [5 empty] | Reactive Capability - Wind | MW | REACT_CAP_WIND | MW4 |  | 1. MW4<MW5 2. X(n) > = WMX (Unit Max output or HRL), where n is the last MW value in the curve. If the curve has 4 points, X(n) is X(4) [ Generate an Error When this rule fails. 3)For wind units that have multiple groups of turbines, Produce a Warning Only when the rule#2 fails (MW4 should be >= HRL) . For Units that have single group of turbine, produce an Error when the rule fails (MW4 should be >= HRL) | R | Numeric | B,DVB | Lin Xu/WeiHui | EMS,NMMS
Lagging MVAR limit associated with MW4 output | Wind | Corrected Label 03/05/2012 | [5 empty] | Reactive Capability - Wind | MVAR | REACT_CAP_WIND | MVAR4LAG |  | 1. Lagging MVAR limit associated with MW4 output >=0.Generate a Warning only if LAG value is negative 2. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS
Leading MVAR limit associated with MW4 output | Wind | Corrected Label 03/05/2012 | [5 empty] | Reactive Capability - Wind | MVAR | REACT_CAP_WIND | MVAR4LEAD |  | Leading MVAR limit associated with MW3 output <=0 .Generate a Warning only if LEAD value is positive | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS
MW5 - Unity Power Factor | Wind | [5 empty] | REMOVE | Reactive Capability - Wind | MVAR | REACT_CAP_WIND | MW5UNITYPF |  | 1. MW5>0 - REMOVED 2. MW5>MW4. REMOVED | R | Numeric | B | Lin Xu | MMS,NMMS
Maximum Leading Operating Capability | Wind | [6 empty] | Reactive Capability - Wind | MVAR | REACT_CAP_WIND | NETMAXLEAD |  | Net Maximum Leading Operating Capability <=0 | R | Numeric | B,DVB | Lin Xu | MMS
Maximum Lagging Operating Capability | Wind | [6 empty] | Reactive Capability - Wind | MVAR | REACT_CAP_WIND | NETMAXLAG |  | Net Maximum Lagging Operating Capability >=0 | R | Numeric | B,DVB | Lin Xu | MMS
Manufacturer's Capability Curve submitted? | Wind | [6 empty] | Reactive Capability - Wind | Y/N | REACT_CAP_WIND | MFR_CAP_CURVE |  | Select from Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0
CC Configurations | CC | [6 empty] | CC Config |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type selected is 'CC'. Can register up to 3 trains at one site. Register Operationally Unique Configurations. | C |  |  |  | NMMS
GENERATOR DETAILS | CC | [6 empty] | CC Config |  | Not in table | Not in table
TRAIN CODE | CC | Corrected 02/23/2012 |  |  |  |  | ADD 02/2012 | CC Config | List | CCUNIT_Configuration TRAIN | TRAIN_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources
SITE CODE | CC | [5 empty] | ADD 02/2012 | CC Config | Automatic | CCUNIT_Configuration | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
Resource Name (Unit Code/Mnemonic) | CC | [5 empty] | ADD 02/2012 | CC Config | List | CCUNIT_Configuration | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0/Jamil Daouk | NMMS
CONFIGURATION DETAILS | CC | [6 empty] | CC Config |  | Not in table | Not in table
Configuration # | CC | [7 empty] | # | Not in table | Not in table
Configuration Code | CC | [5 empty] | ADD 02/2012 | CC Config | Automatic | CCUNIT_Configuration | CONFIG_CODE |  | Concantanate SITE_CODE, TRAIN_CODE and CONFIG_NUM
Configuration Type | CC | [5 empty] | ADD 02/2012 | CC Config | List | CCUNIT_Configuration | CONFIG_TYPE |  | There is no limit to the no. of configurations that can be registered but they should be Operationally Unique and should Increase in number of units and MWs from left to right | R | Integer | B,DVB | RARF Guide Version 4.0/ Lin Xu | NMMS
CC2 Config | CC | [5 empty] | REMOVE | CC2 Config |  |  |  |  | This tab is conditional. Required if the Generation Type selected is 'CC'. Can register up to 3 trains at one site. Register Operationally Unique Configurations. | C
Resource Name(Unit Code) | CC | [5 empty] | REMOVE | CC2 Config |  |  |  |  | Not null. Data type: Character. Should match unit Mnemonic for CC Unit | C | Character | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0/Jamil Daouk
Unit Type | CC | [5 empty] | REMOVE | CC2 Config |  |  |  |  | Not null. Data type: Character. Should match physical unit type from unit info CC | C | Character | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0/Jamil Daouk
Operational Configurations ( | CC | [5 empty] | REMOVE | CC2 Config |  |  |  |  | There is no limit to the no. of configurations that can be registered but they should be Operationally Unique and should Increase in number of units and MWs from left to right | C | Integer | B,DVB | Lin Xu/RARF Guide Version 4.0
CC3 Config | CC | [5 empty] | REMOVE | CC3 Config |  |  |  |  | This tab is conditional. Required if the Generation Type selected is 'CC'. Can register up to 3 trains at one site. Register Operationally Unique Configurations. | C
Resource Name(Unit Code) | CC | [5 empty] | REMOVE | CC3 Config |  |  |  |  | Not null. Data type: Character. Should match unit Mnemonic for CC Unit | C | Character | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0/Jamil Daouk
Unit Type | CC | [5 empty] | REMOVE | CC3 Config |  |  |  |  | Not null. Data type: Character. Should match physical unit type from unit info CC | C | Character | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0/Jamil Daouk
Operational Configurations | CC | [5 empty] | REMOVE | CC3 Config |  |  |  |  | There is no limit to the no. of configurations that can be registered but they should be Operationally Unique and should Increase in number of units and MWs from left to right | C | Integer | B,DVB | RARF Guide Version 4.0/ Lin Xu
CC Transitions | CC | [6 empty] | CC Transitions |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type selected is 'CC'. Should be populated (should match it) from CC configuration | C |  |  | Jamil Daouk | EMS,MMS,NMMS
GENERATOR DETAILS | CC | [6 empty] | CC Transitions |  | Not in table | Not in table
SiteCode | CC | [5 empty] | ADD 02/2012 | CC Transitions | List | TRANSITIONS | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
Mnemonic for Combine Cyle Train | CC | [5 empty] | ADD 02/2012 | CC Transitions | List | TRANSITIONS | TRAIN_CODE |  | CONCANTENATE SITE_CODE and TRAIN_NAME
Configuration Code From | CC | [5 empty] | UPDATE 02/2012 | CC Transitions | List | TRANSITIONS | CONFIGCODE_TO |  | 1.Each configuration in Transitions including Offline can be reached. Each configuration in CC1 Transitions including Offline can reach at least one of the other configurations including Offline . 2.Values allowed are X for Main Transition , A for Alternate Transition ,Null for Non Transition 3. 1.If a RARF is submitted that does not have the first Transition from OFFLINE, Generate an ERROR. 4. Generate a Warning if the Transitions skip. For instance the transitions table has ‘Offline’ to ‘CC1_2’ and so it skips CC1_1. This is an acceptable possibility, but the resource needs to be notified of it because they would not be in RUC until the CC1_2 configuration, in this case would only be in RUC with both units available, not just the single unit associated to CC1_1. 5) Generate a Warning if the Transition is missing for a Configuration
Configuration Code To | CC | [5 empty] | UPDATE 02/2012 | CC Transitions | List | TRANSITIONS | CONFIGCODE_FROM |  | 1.Each configuration in CC2 Transitions except Offline needs to be defined in CC2 Config. 2.Each configuration in CC2 Transitions including Offline can be reached. Each configuration in CC2 Transitions including Offline can reach at least one of the other configurations including Offline 3. 1.If a RARF is submitted that does not have the first Transition from OFFLINE, Generate an ERROR. 4. Generate a Warning if the Transitions skip. For instance the transitions table has ‘Offline’ to ‘CC1_2’ and so it skips CC1_1. This is an acceptable possibility, but the resource needs to be notified of it because they would not be in RUC until the CC1_2 configuration, in this case would only be in RUC with both units available, not just the single unit associated to CC1_1. 5. Generate a Warning if the Transition is missing for a Configuration
Operational Configurations (Test_CC1_X to Test_CC1_X) | CC | [5 empty] | REMOVE | CC1 Transitions |  |  |  |  | 1.If CC1 Transitions to CC2 , CC2 should be registered as a Configuration. 2.Each configuration in CC1 Transitions including Offline can be reached. Each configuration in CC1 Transitions including Offline can reach at least one of the other configurations including Offline . 3.Values allowed are X for Main Transition , A for Alternate Transition ,Null for Non Transition 4. 1.If a RARF is submitted that does not have the first Transition from OFFLINE, Generate an ERROR. 5. Generate a Warning if the Transitions skip. For instance the transitions table has ‘Offline’ to ‘CC1_2’ and so it skips CC1_1. This is an acceptable possibility, but the resource needs to be notified of it because they would not be in RUC until the CC1_2 configuration, in this case would only be in RUC with both units available, not just the single unit associated to CC1_1. 6) Generate a Warning if the Transition is missing for a Configuration | R | Character | B,DVB | Lin Xu/ Jamil Daouk | EMS,MMS,NMMS
CC2 Transitions | CC | [5 empty] | REMOVE | CC2 Transitions |  | Not in table | Not in table |  | CC2 Transitions tab is conditional. Required for only Combined Cycle Generation Resources | C |  |  | RARF Guide Version 4.0 | EMS,MMS
Operating Transitions From offline 1-30 to offline 1-30 | CC | [5 empty] | REMOVE | CC2 Transitions |  |  |  |  | 1.Each configuration in CC2 Transitions except Offline needs to be defined in CC2 Config. 2.Each configuration in CC2 Transitions including Offline can be reached. Each configuration in CC2 Transitions including Offline can reach at least one of the other configurations including Offline 3. 1.If a RARF is submitted that does not have the first Transition from OFFLINE, Generate an ERROR. 4. Generate a Warning if the Transitions skip. For instance the transitions table has ‘Offline’ to ‘CC1_2’ and so it skips CC1_1. This is an acceptable possibility, but the resource needs to be notified of it because they would not be in RUC until the CC1_2 configuration, in this case would only be in RUC with both units available, not just the single unit associated to CC1_1. 5. Generate a Warning if the Transition is missing for a Configuration | C |  | B,DVB | Lin Xu | EMS,MMS
CC3 Transitions | CC | [5 empty] | REMOVE | CC3 Transitions |  | Not in table | Not in table |  | CC3 Transitions tab is conditional. Required for only Combined Cycle Generation Resources | C |  |  | RARF Guide Version 4.0
Operating Transitions From offline 1-30 to offline 1-30 | CC | [5 empty] | REMOVE | CC3 Transitions |  |  |  |  | 1.Each configuration in CC3 Transitions except Offline needs to be defined in CC1 Config. 2.Each configuration in CC3 Transitions including Offline can be reached. Each configuration in CC3 Transitions including Offline can reach at least one of the other configurations including Offline 3. 1.If a RARF is submitted that does not have the first Transition from OFFLINE, Generate an ERROR. 4. Generate a Warning if the Transitions skip. For instance the transitions table has ‘Offline’ to ‘CC1_2’ and so it skips CC1_1. This is an acceptable possibility, but the resource needs to be notified of it because they would not be in RUC until the CC1_2 configuration, in this case would only be in RUC with both units available, not just the single unit associated to CC1_1. 5. Generate a Warning if the Transition is missing for a Configuration | C |  | B,DVB | Lin Xu | EMS,MMS
Planning - GEN | Generation | [6 empty] | Planning - GEN |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type Selected is 'GEN' where GEN is non-CC non-wind Generation Resources. This tab is unit specific and required for all non-cc non-wind units. All the fields in this section should be complete. For all the UNITS in the Unit info-GEN tab , there should be corresponding data in Planning-GEN Tab | C |  |  | RARF Guide Version 4.0 | MMS,NMMS
Generator Details | Generation | [6 empty] | Planning - GEN |  | Not in table | Not in table
Unit Name | Generation | Do not show Message on Audit or Delta |  | Passed/DCSES |  |  | ADD 02/2012 | Planning - GEN | List | GENERATION | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Generation |  |  | Passed/DCSES |  |  | ADD 02/2012 | Planning - GEN | Automatic | GENERATION | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
PLANNING DETAILS | Generation | [6 empty] | Planning - GEN |  | Not in table | Not in table
What is the MVA base that the following data is based on? | Generation | [6 empty] | Planning - GEN | MVA | GENERATION | MVABASE |  | 1) This field is required 2) Value must be Float 3) Generate a Warning if MVABASE > 2500 4)[ If MVABASE value is within +/- 25% range of Unit Name Plate Rating] OR [MVABASE value = 100, then it is OK.If MVABASE value is outside the +/- 25% range of Unit Name Plate Rating, then Generate a Warning that the MVABSE is outside the typical +/- 25% variation of unit name plate rating | R | Float | B | Planning Team
What is the kV base that the following data is based on? | Generation | [6 empty] | Planning - GEN | KV | GENERATION | KVBASE |  | 1) This field is required 2) Value must be >0 and <1000 3) Generate a Warning if KVBASE > 40 4) If KVBASE value is within +/- 25% range of Unit KV value in the unit-information tab then it is OK.If If KVBASE value is outside the typical +/- 25% variation of Unit KV value in the unit-information tab then Generate a Warning that the KVBASE is outside the typical +/- 25% variation of Unit KV value | R | Float | B,DVB | Planning Team
Direct Axis Sub transient reactance, X"di (unsaturated) | Generation | [6 empty] | Planning - GEN | p.u. | GENERATION | DIRECT_AXIS_SUBSTNT_REACTANCE |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B | Planning Team
Direct Axis Transient reactance, X'di (unsaturated) | Generation | [6 empty] | Planning - GEN | p.u. | GENERATION | DIRECT_AXIS_TRANSNT_REACTANCE |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B | Planning Team
Positive Sequence Z (unsaturated) | Generation | [6 empty] | Planning - GEN | R in p.u. | GENERATION | POSITIVE_SEQ_Z_R_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 |  |  |  | Planning Team
Positive Sequence Z (unsaturated) | Generation | [6 empty] | Planning - GEN | X in p.u. | GENERATION | POSITIVE_SEQ_Z_X_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) |  |  |  | Planning Team
Negative Sequence Z (unsaturated) | Generation | [6 empty] | Planning - GEN | R in p.u. | GENERATION | NEGATIVE_SEQ_Z_R_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 |  |  |  | Planning Team
Negative Sequence Z (unsaturated) | Generation | [6 empty] | Planning - GEN | X in p.u. | GENERATION | NEGATIVE_SEQ_Z_X_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] |  |  |  | Planning Team
Does Zero Sequence Z exist? | Generation | [6 empty] | Planning - GEN | Y/N | Generation | DOES_ZERO_SEQ_EXIST |  | Drop down list select Y/N | R | Dropdown List |  | Planning Team
Zero Sequence Z (unsaturated) | Generation | [6 empty] | Planning - GEN | R in p.u. | GENERATION | ZERO_SEQ_Z_R_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U |  |  |  | Planning Team
Zero Sequence Z (unsaturated) | Generation | [6 empty] | Planning - GEN | X in p.u. | GENERATION | ZERO_SEQ_Z_X_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] |  |  |  | Planning Team
Direct Axis Sub transient reactance, X"dv (saturated) | Generation | [5 empty] | ADD 04/2012 | Planning - GEN | p.u. | GENERATION | DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value.(* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team
Direct Axis Transient reactance, X'dv (saturated) | Generation | [5 empty] | ADD 04/2012 | Planning - GEN | p.u. | GENERATION | DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team
Positive Sequence Z (saturated) - (R in p.u) | Generation | [5 empty] | ADD 04/2012 | Planning - GEN | R in p.u. | GENERATION | POSITIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B | Planning Team | NMMS
Positive Sequence Z (saturated) - ( X in p.u) | Generation | [5 empty] | ADD 04/2012 | Planning - GEN | X in p.u. | GENERATION | POSITIVE_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B | Planning Team | NMMS
Negative Sequence Z (saturated) - ( R in p.u) | Generation | [5 empty] | ADD 04/2012 | Planning - GEN | R in p.u. | GENERATION | NEGATIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B | Planning Team
Negative Sequence Z (saturated) - ( X in p.u) | Generation | [5 empty] | ADD 04/2012 | Planning - GEN | X in p.u. | GENERATION | NEGATIVE_SEQ_Z_X-SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team
Zero Sequence Z (saturated) - (R in p.u) | Generation | [5 empty] | ADD 04/2012 | Planning - GEN | R in p.u. | GENERATION | ZERO_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U | R | Float | B | Planning Team | NMMS
Zero Sequence Z (saturated) - (X in p.u) | Generation | [5 empty] | ADD 04/2012 | Planning - GEN | X in p.u. | GENERATION | ZERO_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team | NMMS
Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Generation | [5 empty] | ADD 04/2012 | Planning - GEN | p.u. | GENERATION | ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Generation | [5 empty] | ADD 04/2012 | Planning - GEN | p.u. | GENERATION | ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Zero Sequence Resistance In P.u. (100 Mva Base) | Generation | [5 empty] | ADD 04/2012 | Planning - GEN | p.u. | GENERATION | ZERO_SEQ_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Zero Sequence Reactance In P.u. (100 Mva Base) | Generation | [5 empty] | ADD 04/2012 | Planning - GEN | p.u. | GENERATION | ZERO_SEQ_Reactance_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Generator Auxiliary Load | Generation | [6 empty] | Planning - GEN |  | Not in table | Not in table
Average Amount of Auxiliary Real Power | Generation | [6 empty] | Planning - GEN | MW | GENERATION | AUX_MWTOTAL |  | 1) This field is optional 2) Data type is float 3) Value must be < Parameters - GEN - High Reasonability Limit 4) Warn if value > (High Reasonability Limit) * .75 5) Error if value > (High Reasonability Limit) * .66 | R | Float | B | Planning Team
Average Amount of Auxiliary Reactive Power | Generation | [6 empty] | Planning - GEN | MVAR | GENERATION | AUX_MVARTOTAL |  | 1) This field is optional 2) Data type is Float 3) Value must be < Reactive Capability - GEN - Maximum Lagging Operating Capability (MVAR) 4) Warn if value > ( Maximum Lagging Operating Capability) * .75 5) Error if value > ( Maximum Lagging Operating Capability) * .66 | R | Float | B | Planning Team
Auxilary Load Power Factor | Generation | [5 empty] | ADD 04/2012 | Planning - GEN |  | GENERATION | AUX_LOAD_PWR_FACT |  | Between .8 and 1.0 |  |  |  | Planning Team
Generation Auxiliary Load Characteristics for MW Load | Generation | [6 empty] | Planning - GEN |  | Not in table | Not in table
Generation Auxiliary Load Characteristics for MW Load - Large Motor, percent of total MW load | Generation | [6 empty] | Planning - GEN | Percent | GENERATION | AUXMW_LARGEMTR_PCT |  | 1) This field is optional 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | R | Percent | B,DVB | Model Adminstration/Planning Team | MMS
Generation Auxiliary Load Characteristics for MW Load - Small Motor, percent of total MW load | Generation | [6 empty] | Planning - GEN | Percent | GENERATION | AUXMW_SMALLMTR_PCT |  | 1) This field is optional 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | R | Percent | B,DVB | Model Adminstration/Planning Team | MMS
Generation Auxiliary Load Characteristics for MW Load - Resistive (Heating) Load, percent of total MW load | Generation | [6 empty] | Planning - GEN | Percent | GENERATION | AUXMW_RESISTIVE_PCT |  | 1) This field is optional 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | R | Percent | B,DVB | Model Adminstration/Planning Team | MMS
Generation Auxiliary Load Characteristics for MW Load - Discharge Lighting, percent of total MW load | Generation | [6 empty] | Planning - GEN | Percent | GENERATION | AUXMW_DISCHARGE_PCT |  | 1) This field is optional 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | R | Percent | B,DVB | Model Adminstration/Planning Team | MMS
Generation Auxiliary Load Characteristics for MW Load - Other, percent of total MW load | Generation | [6 empty] | Planning - GEN | Percent | GENERATION | AUXMW_OTHER_PCT |  | 1) This field is optional 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | R | Percent | B,DVB | Model Adminstration/Planning Team | MMS
Generation Auxiliary Load Characteristics for MVAR Load | Generation | [6 empty] | Planning - GEN |  | Not in table | Not in table
Generation Auxiliary Load Characteristics for MVAR Load - Large Motor, percent of total MVAR load | Generation | [6 empty] | Planning - GEN | Percent | GENERATION | AUXMVAR_LARGEMTR_PCT |  | 1) This field is optional 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | R | Percent | B,DVB | Model Adminstration/Planning Team | MMS
Generation Auxiliary Load Characteristics for MVAR Load - Small Motor, percent of total MVAR load | Generation | [6 empty] | Planning - GEN | Percent | GENERATION | AUXMVAR_SMALLMTR_PCT |  | 1) This field is optional 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | R | Percent | B,DVB | Model Adminstration/Planning Team | MMS
Generation Auxiliary Load Characteristics for MVAR Load - Discharge Lighting, percent of total MVAR load | Generation | [6 empty] | Planning - GEN | Percent | GENERATION | AUXMVAR_DISCHARGE_PCT |  | 1) This field is optional 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | R | Percent | B,DVB | Model Adminstration/Planning Team | MMS
Generation Auxiliary Load Characteristics for MVAR Load - Other, percent of total MVAR load | Generation | [6 empty] | Planning - GEN | Percent | GENERATION | AUXMVAR_OTHER_PCT |  | 1) This field is optional 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | R | Percent | B,DVB | Model Adminstration/Planning Team | MMS
PSSE MODEL : THE FOLLOWING LIST OF FILES ARE REQUIRED TO BE SUBMITTED IF THIS IS AN INITIAL REGISTRATION OR IF THERE ARE CHANGES MODIFYING PREVIOUSLY SUBMITTED PSSE FILES. PLEASE INCLUDE ALL PSSE FILES IN A ZIP OR COMPRESSED FOLDER FILE ALONG WITH YOUR RARF SUBMITTAL IN THE SAME SERVICE REQUEST. | Generation | [6 empty] | Planning - GEN |  | Not in table | Not in table
Generator Form | Generation | [6 empty] | Planning - GEN |  | Not in table | Not in table
Turbine-governor Form | Generation | [6 empty] | Planning - GEN |  | Not in table | Not in table
Excitation Form | Generation | [6 empty] | Planning - GEN |  | Not in table | Not in table
Power System Stabilizer Form (required If There Is A Power System Stabilizer) | Generation | [6 empty] | Planning - GEN |  | Not in table | Not in table
Compensator Form (required If There Is A Compensator) | Generation | [6 empty] | Planning - GEN |  | Not in table | Not in table
Over Excitation Limiter Form (required If There Is An Over Excitation Limiter) | Generation | [6 empty] | Planning - GEN |  | Not in table | Not in table
Under Excitation Limiter Form (required If There Is An Under Excitation Limiter) | Generation | [6 empty] | Planning - GEN |  | Not in table | Not in table
Planning - CC | CC | [6 empty] | Planning - CC |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type selected is 'CC'.This tab is unit specific and is required for all CC units. All the fields in this tab are required. Can register up to 3 trains at one site. This information is required for each unit of the train. For all the CCUNITS in the unit info-cc tab , there should be corresponding data in planning-cc Tab | C |  |  | RARF Glossary Version 4.0 | MMS
GENERATOR DETAILS | CC | [6 empty] | Planning - CC |  | Not in table | Not in table
Unit Name | CC | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Planning - CC | List | CCUNIT | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
SITE_CODE | CC | [5 empty] | ADD 02/2012 | Planning - CC | Automatic | CCUNIT | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
Resource Name (Unit Code/mnemonic) | CC | [5 empty] | ADD 02/2012 | Planning - CC | Automatic | CCUNIT | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
PLANNING DETAILS | CC | [6 empty] | Planning - CC |  | Not in table | Not in table
What Is The Mva Base That The Following Data Is Based On? | CC | [6 empty] | Planning - CC | MVA | CCUNIT | MVABASE |  | 1) This field is required 2) Value must be Float 3) Generate a Warning if MVABASE > 2500 4)[ If MVABASE value is within +/- 25% range of Unit Name Plate Rating] OR [MVABASE value = 100, then it is OK.If MVABASE value is outside the +/- 25% range of Unit Name Plate Rating, then Generate a Warning that the MVABSE is outside the typical +/- 25% variation of unit name plate rating | R | Float | B | Planning Team
What Is The Kv Base That The Following Data Is Based On? | CC | [6 empty] | Planning - CC | kV | CCUNIT | KVBASE |  | 1) This field is required 2) Value must be >0 and <1000 3) Generate a Warning if KVBASE > 40 4) If KVBASE value is within +/- 25% range of Unit KV value in the unit-information tab then it is OK.If If KVBASE value is outside the typical +/- 25% variation of Unit KV value in the unit-information tab then Generate a Warning that the KVBASE is outside the typical +/- 25% variation of Unit KV value | R | Float | B,DVB | Planning Team
Direct Axis Subtransient Reactance, X"di (unsaturated) | CC | [6 empty] | Planning - CC | p.u. | CCUNIT | DIRECT_AXIS_SUBSTNT_REACTANCE |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B | Planning Team
Direct Axis Transient Reactance, X'di (unsaturated) | CC | [6 empty] | Planning - CC | p.u. | CCUNIT | DIRECT_AXIS_TRANSNT_REACTANCE |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B | Planning Team
Positive Sequence Z (unsaturated) | CC | [6 empty] | Planning - CC | R in p.u. | CCUNIT | POSITIVE_SEQ_Z_R__PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 |  |  |  | Planning Team
Positive Sequence Z (unsaturated) | CC | [6 empty] | Planning - CC | X in p.u. | CCUNIT | POSITIVE_SEQ_Z_X__PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] |  |  |  | Planning Team
Negative Sequence Z (unsaturated) | CC | [6 empty] | Planning - CC | R in p.u. | CCUNIT | NEGATIVE_SEQ_Z_R__PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning when value is > 1.0 P.U |  |  |  | Planning Team
Negative Sequence Z (unsaturated) | CC | [6 empty] | Planning - CC | X in p.u. | CCUNIT | NEGATIVE_SEQ_Z_X-_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] |  |  |  | Planning Team
Does Zero Sequence Z exist? | CC | [5 empty] | ADD 04/2012 | Planning - CC | Y/N | CCUNIT | DOES_ZERO_SEQ_EXIST |  | Drop down list select Y/N | R | Dropdown List |  | Planning Team
Zero Sequence Z (unsaturated) | CC | [6 empty] | Planning - CC | R in p.u. | CCUNIT | ZERO_SEQ_Z_R__PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U |  |  |  | Planning Team
Zero Sequence Z (unsaturated) | CC | [6 empty] | Planning - CC | X in p.u. | CCUNIT | ZERO_SEQ_Z_X__PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] |  |  |  | Planning Team
Direct Axis Subtransient Reactance, X"dv (saturated) | CC | Corrected |  |  |  |  | ADD 04/2012 | Planning - CC | p.u. | CCUNIT | DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value.(* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team
Direct Axis Transient Reactance, X'dv (saturated) | CC | [5 empty] | ADD 04/2012 | Planning - CC | p.u. | CCUNIT | DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team
Positive Sequence Z (saturated) | CC | [5 empty] | ADD 04/2012 | Planning - CC | R in p.u. | CCUNIT | POSITIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B | Planning Team | NMMS
Positive Sequence Z (saturated) | CC | [5 empty] | ADD 04/2012 | Planning - CC | X in p.u. | CCUNIT | POSITIVE_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B | Planning Team | NMMS
Negative Sequence Z (saturated) | CC | [5 empty] | ADD 04/2012 | Planning - CC | R in p.u. | CCUNIT | NEGATIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B | Planning Team
Negative Sequence Z (saturated) | CC | [5 empty] | ADD 04/2012 | Planning - CC | X in p.u. | CCUNIT | NEGATIVE_SEQ_Z_X-SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team
Zero Sequence Z (saturated) | CC | [5 empty] | ADD 04/2012 | Planning - CC | R in p.u. | CCUNIT | ZERO_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U | R | Float | B | Planning Team | NMMS
Zero Sequence Z (saturated) | CC | [5 empty] | ADD 04/2012 | Planning - CC | X in p.u. | CCUNIT | ZERO_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team | NMMS
Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | CC | [5 empty] | ADD 04/2012 | Planning - CC | p.u. | CCUNIT | ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | CC | [5 empty] | ADD 04/2012 | Planning - CC | p.u. | CCUNIT | ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Zero Sequence Resistance In P.u. (100 Mva Base) | CC | [5 empty] | ADD 04/2012 | Planning - CC | p.u. | CCUNIT | ZERO_SEQ_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Zero Sequence Reactance In P.u. (100 Mva Base) | CC | [5 empty] | ADD 04/2012 | Planning - CC | p.u. | CCUNIT | ZERO_SEQ_Reactance_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
GENERATOR AUXILIARY LOAD | CC | [6 empty] | Planning - CC |  | Not in table | Not in table
Average Amount of Auxiliary Real Power | CC | [6 empty] | Planning - CC | MW | CCUNIT | AUX_MWTOTAL |  | 1) This field is required. 2) Data type is float 3) Value must be < Parameters - GEN - High Reasonability Limit 4) Warn if value > (High Reasonability Limit) * .75 5) Error if value > (High Reasonability Limit) * .66 | R | Float | B | Planning Team
Average Amount of Auxiliary Reactive Power | CC | [6 empty] | Planning - CC | MVAR | CCUNIT | AUX_MVARTOTAL |  | 1) This field is required 2) Data type is Float 3) Value must be < Reactive Capability - GEN - Maximum Lagging Operating Capability (MVAR) 4) Warn if value > ( Maximum Lagging Operating Capability) * .75 5) Error if value > ( Maximum Lagging Operating Capability) * .66 | R | Float | B | Planning Team
Auxiliary Load Power Factor | CC | [5 empty] | ADD 04/2012 | Planning - CC |  | CCUNIT | AUX_LOAD_PWR_FACT |  | Between .8 and 1.0 |  |  |  | Planning Team
Generation Auxiliary Load Characteristics For Mw Load | CC | [6 empty] | Planning - CC |  | Not in table | Not in table
Large Motor, Percent Of Total Mw Load | CC | [6 empty] | Planning - CC | Percent | CCUNIT | AUXMW_LARGEMTR_PCT |  | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | R | Percent | B,DVB | Planning Team | MMS
Small Motor, Percent Of Total Mw Load | CC | [6 empty] | Planning - CC | Percent | CCUNIT | AUXMW_SMALLMTR_PCT |  | This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | R | Percent | B,DVB | Planning Team | MMS
Resistive (heating) Load, Percent Of Total Mw Load | CC | [6 empty] | Planning - CC | Percent | CCUNIT | AUXMW_RESISTIVE_PCT |  | This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | R | Percent | B,DVB | Planning Team | MMS
Discharge Lighting, Percent Of Total Mw Load | CC | [6 empty] | Planning - CC | Percent | CCUNIT | AUXMW_DISCHARGE_PCT |  | This field is CONDITIONAL (Not required when Average Amount Of Real Power value is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | R | Percent | B,DVB | Planning Team | MMS
Other, Percent Of Total Mw Load | CC | [6 empty] | Planning - CC | Percent | CCUNIT | AUXMW_OTHER_PCT |  | This field is CONDITIONAL (Not required when Average Amount Of Real Power value zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | R | Percent | B,DVB | Planning Team | MMS
Generation Auxiliary Load Characteristics for MVAR Load | CC | [6 empty] | Planning - CC |  | Not in table | Not in table
Large Motor, Percent Of Total Mvar Load | CC | [6 empty] | Planning - CC | Percent | CCUNIT | AUXMVAR_LARGEMTR_PCT |  | 1) This field is CONDITIONAL (Not required when Average Amount Of Reactive Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | R | Percent | B,DVB | Planning Team | MMS
Small Motor, Percent Of Total Mvar Load | CC | [6 empty] | Planning - CC | Percent | CCUNIT | AUXMVAR_LARGEMTR_PCT |  | This field is CONDITIONAL (Not required when Average Amount Of Reactive Power Value is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | R | Percent | B,DVB | Planning Team | MMS
Discharge Lighting, Percent Of Total Mvar Load | CC | [6 empty] | Planning - CC | Percent | CCUNIT | AUXMVAR_DISCHARGE_PCT |  | This field is CONDITIONAL (Not required when Average Amount Of Reactive Power value is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | R | Percent | B,DVB | Planning Team | MMS
Other, Percent Of Total Mvar Load | CC | [6 empty] | Planning - CC | Percent | CCUNIT | AUXMVAR_OTHER_PCT |  | This field is CONDITIONAL (Not required when Average Amount Of Reactive Power value is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | R | Percent | B,DVB | Planning Team | MMS
PSSE MODEL : THE FOLLOWING LIST OF FILES ARE REQUIRED TO BE SUBMITTED IF THIS IS AN INITIAL REGISTRATION OR IF THERE ARE CHANGES MODIFYING PREVIOUSLY SUBMITTED PSSE FILES. PLEASE INCLUDE ALL PSSE FILES IN A ZIP OR COMPRESSED FOLDER FILE ALONG WITH YOUR RARF SUBMITTAL IN THE SAME SERVICE REQUEST. | CC | [6 empty] | Planning - CC |  | Not in table | Not in table
Generator Form | CC | [6 empty] | Planning - CC |  | Not in table | Not in table
Turbine-governor Form | CC | [6 empty] | Planning - CC |  | Not in table | Not in table
Excitation Form | CC | [6 empty] | Planning - CC |  | Not in table | Not in table
Power System Stabilizer Form (required If There Is A Power System Stabilizer) | CC | [6 empty] | Planning - CC |  | Not in table | Not in table
Compensator Form (required If There Is A Compensator) | CC | [6 empty] | Planning - CC |  | Not in table | Not in table
Over Excitation Limiter Form (required If There Is An Over Excitation Limiter) | CC | [6 empty] | Planning - CC |  | Not in table | Not in table
Under Excitation Limiter Form (required If There Is An Under Excitation Limiter) | CC | [6 empty] | Planning - CC |  | Not in table | Not in table
Planning - WIND | Wind | [6 empty] | Planning - Wind |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type selected is 'WIND '.This tab is unit specific and is required for all wind units. All the fields in this tab should be required. For all the UNITS in the Unit info-WIND tab , there should be corresponding data in Planning-WIND Tab | C |  |  | RARF Guide Version 4.0 | MMS
GENERATOR DETAILS | Wind | [6 empty] | Planning - Wind |  | Not in table | Not in table
Unit Name | Wind | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Planning - Wind | List | WIND | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Wind | [5 empty] | ADD 02/2012 | Planning - Wind | Automatic | WIND | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
Type of Turbine | Wind | Corrected DB_FIELD 03/01/2012 |  |  |  |  | ADD 02/2012 | Planning - Wind | List | WIND | TURBINE_TYPE TUR_TYPE |  | Dropdown list | R | Dropdown list
PLANNING DETAILS | Wind | [6 empty] | Planning - Wind |  | Not in table | Not in table
What is the MVA base that the following data is based on? | Wind | [6 empty] | Planning - Wind | MVA | WIND | MVABASE |  | 1) This field is required 2) Value must be Float 3) Generate a Warning if MVABASE > 2500 4)[ If MVABASE value is within +/- 25% range of Unit Name Plate Rating] OR [MVABASE value = 100, then it is OK.If MVABASE value is outside the +/- 25% range of Unit Name Plate Rating, then Generate a Warning that the MVABSE is outside the typical +/- 25% variation of unit name plate rating | R | Float | B | Planning Team
What is the kV base that the following data is based on? | Wind | [6 empty] | Planning - Wind | KV | WIND | KVBASE |  | 1) This field is required 2) Value must be >0 and <1000 3) Generate a Warning if KVBASE>40 4) If KVBASE value is within +/- 25% range of Unit KV value in the unit-information tab then it is OK.If If KVBASE value is outside the typical +/- 25% variation of Unit KV value in the unit-information tab then Generate a Warning that the KVBASE is outside the typical +/- 25% variation of Unit KV value | R | Float | B,DVB | Planning Team
Direct Axis Subtransient Reactance, X"di (unsaturated) | Wind | [6 empty] | Planning - Wind | p.u. | WIND | DIRECT_AXIS_SUBSTNT_REACTANCE |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B | Planning Team
Direct Axis Transient Reactance, X'di (unsaturated) | Wind | [6 empty] | Planning - Wind | p.u. | WIND | DIRECT_AXIS_TRANSNT_REACTANCE |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B | Planning Team
Positive Sequence Z (unsaturated) | Wind | [6 empty] | Planning - Wind | R in p.u. | WIND | POSITIVE_SEQ_Z_R_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 |  |  |  | Planning Team
Positive Sequence Z (unsaturated) | Wind | [6 empty] | Planning - Wind | X in p.u. | WIND | POSITIVE_SEQ_Z_X_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) |  |  |  | Planning Team
Negative Sequence Z (unsaturated) | Wind | [6 empty] | Planning - Wind | R in p.u. | WIND | NEGATIVE_SEQ_Z_R_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 |  |  |  | Planning Team
Negative Sequence Z (unsaturated) | Wind | [6 empty] | Planning - Wind | X in p.u. | WIND | NEGATIVE_SEQ_Z_X_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) |  |  |  | Planning Team
Does Zero Sequence Z exist? | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | Y/N | Wind | DOES_ZERO_SEQ_EXIST |  | Drop down list select Y/N | R | Dropdown List |  | Planning Team
Zero Sequence Z (unsaturated) | Wind | [6 empty] | Planning - Wind | R in p.u. | WIND | ZERO_SEQ_Z_R_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 . Generate a Warning when value is > 1.0 P.U |  |  |  | Planning Team
Zero Sequence Z (unsaturated) | Wind | [6 empty] | Planning - Wind | X in p.u. | WIND | ZERO_SEQ_Z_X_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) |  |  |  | Planning Team
Direct Axis Sub transient reactance, X"dv (saturated)- (R in p.u) | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | p.u. | WIND | DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B | Planning Team
Direct Axis Transient reactance, X'dv (saturated) - (X in p.u) | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | p.u. | WIND | DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B | Planning Team
Positive Sequence Z (saturated) - (R in p.u) | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | R in p.u. | WIND | POSITIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B | Planning Team | NMMS
Positive Sequence Z (saturated) - ( X in p.u) | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | X in p.u. | WIND | POSITIVE_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B | Planning Team | NMMS
Negative Sequence Z (saturated) - ( R in p.u) | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | R in p.u. | WIND | NEGATIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B | Planning Team
Negative Sequence Z (saturated) - ( X in p.u) | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | X in p.u. | WIND | NEGATIVE_SEQ_Z_X-SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team
Zero Sequence Z (saturated) - (R in p.u) | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | R in p.u. | WIND | ZERO_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U | R | Float | B | Planning Team | NMMS
Zero Sequence Z (saturated) - (X in p.u) | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | X in p.u. | WIND | ZERO_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B | Planning Team | NMMS
Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | p.u. | WIND | ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | p.u. | WIND | ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Zero Sequence Resistance In P.u. (100 Mva Base) | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | p.u. | WIND | ZERO_SEQ_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Zero Sequence Reactance In P.u. (100 Mva Base) | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | p.u. | WIND | ZERO_SEQ_Reactance_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Generator Auxiliary Load | Wind | [6 empty] | Planning - Wind |  | Not in table | Not in table
Average Amount Of Auxiliary Real Power | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | MW | WIND | AUX_MWTOTAL |  | 1) This field is optional 2) Data type is float 3) Value must be < Parameters - GEN - High Reasonability Limit 4) Warn if value > (High Reasonability Limit) * .75 5) Error if value > (High Reasonability Limit) * .66 | R | Float | B | Planning Team
Average Amount Of Auxiliary Reactive Power | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | MWAR | WIND | AUX_MVARTOTAL |  | 1) This field is optional 2) Data type is Float 3) Value must be < Reactive Capability - GEN - Maximum Lagging Operating Capability (MVAR) 4) Warn if value > ( Maximum Lagging Operating Capability) * .75 5) Error if value > ( Maximum Lagging Operating Capability) * .66 | R | Float | B | Planning Team
Auxilary Load Power Factor | Wind | [5 empty] | ADD 04/2012 | Planning - Wind |  | WIND | AUX_LOAD_PWR_FACT |  | Between .8 and 1.0 |  |  |  | Planning Team
Generation Auxiliary Load Characteristics for MW Load | Wind | [6 empty] | Planning - Wind |  | Not in table | Not in table
Large Motor, Percent Of Total Mw Load | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | Percent | WIND | LRG_MTR_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Planning Team
Small Motor, Percent Of Total Mw Load | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | Percent | WIND | SML_MTR_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Planning Team
Resistive (heating) Load, Percent Of Total Mw Load | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | Percent | WIND | RESISTIVE_LOAD_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Planning Team
Discharge Lighting, Percent Of Total Mw Load | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | Percent | WIND | DISCHARGE LIGHT_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Planning Team
Other, Percent Of Total Mw Load | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | Percent | WIND | OTH_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Planning Team
Generation Auxiliary Load Characteristics for MVAR Load | Wind | [6 empty] | Planning - Wind |  | Not in table | Not in table
Large Motor, Percent Of Total Mvar Load | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | Percent | WIND | LRG_MTR_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Planning Team
Small Motor, Percent Of Total Mvar Load | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | Percent | WIND | SML_MTR_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | R | Numeric | B,DVB | Planning Team
Discharge Lighting, Percent Of Total Mvar Load | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | Percent | WIND | DISCHARGE LIGHT_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Planning Team
Other, Percent Of Total Mvar Load | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | Percent | WIND | OTH_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Planning Team
TURBINE STEP-UP TRANSFORMER DATA | Wind | [6 empty] | Planning - Wind |  | Not in table | Not in table
High Side Voltage Level (nominal) | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | Kv | WIND | HIGH_SIDE_VT_LEVL |  | 1) This field is required 2) Data type must be real 3) Generate an Error if not between 345 and 69 | R | Real | B,DVB | Planning Team/Model Adminstration
Low Side Voltage Level (nominal) | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | KV | WIND | LOW_SIDE_VT_LEVL |  | 1) This field is required 2) Data type must be real 3) Generate an Error if not < 69 | R | Real | B,DVB | Planning Team/Model Adminstration
High Side Voltage Connection - Wye / Wye - Grounded / Delta | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | List | WIND | HIGH_SIDE_VT_CONNT |  | 1) This field is required 2) Data type must be from list 3) Generate an Error if blank | R | Real | B,DVB | Planning Team/Model Adminstration
Low Side Voltage Connection - Wye / Wye - Grounded / Delta | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | List | WIND | LOW_SIDE_VT_CONNT |  | 1) This field is required 2) Data type must be from list 3) Generate an Error if blank | R | Real | B,DVB | Planning Team/Model Adminstration
Impedance Z | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | p.u. | WIND | IMPEDANCE_Z |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0 | R | Real | B,DVB | Planning Team/Model Adminstration
X/r Ratio | Wind | [5 empty] | ADD 04/2012 | Planning - Wind |  | WIND | X_R_RATIO |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 1 | R | Real | B,DVB | Planning Team/Model Adminstration
Zero Sequence Z | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | p.u. | WIND | ZERO_SEQ_Z |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0 | R | Real | B,DVB | Planning Team/Model Adminstration
Zero Sequence X/r Ratio | Wind | [5 empty] | ADD 04/2012 | Planning - Wind |  | WIND | ZERO_SEQ_X_R_RATIO |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 1 | R | Real | B,DVB | Planning Team/Model Adminstration
Base Mva For Transformer Data | Wind | [5 empty] | ADD 04/2012 | Planning - Wind | MVA | WIND | BASE_MVA_TRANSFORMER_DATA |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank, Generate Warning if > 2000 | R | Real | B,DVB | Planning Team/Model Adminstration
PSSE MODELS : THE FOLLOWING FILES ARE REQUIRED TO BE SUBMITTED IF NOT LISTED IN THE WIND TURBINE DYNAMIC MODELS AVAILABLE AT ERCOT OR IF ADDITIONAL EQUIPMENT HAS BEEN ADDED TO THE SITE REQUIRING MODEL UPDATES. PLEASE INCLUDE ALL PSSE FILES IN A ZIP OR COMPRESSED FOLDER ALONG WITH YOUR RARF SUBMITTAL SERVICE REQUEST. | Wind | [6 empty] | Planning - Wind |  | Not in table | Not in table
PSSE Compatible Wind Generator Models | Wind | [6 empty] | Planning - Wind |  | Not in table | Not in table
Dynamic Reactive Device Form | Wind | [6 empty] | Planning - Wind |  | Not in table | Not in table
Private Network - Site - GEN | Generation | [6 empty] | Private Network - Site - GEN |  | Not in table | Not in table
Private Network? | Generation | [6 empty] | Private Network - Site - GEN | Y/N | SITECODES | PRIVATE_NTWK_SITE_FLG |  | Select from Y or N. Private Network Flag is not null | R | Dropdown List | B,DVB | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms/Kittiepong | EMS
SITE DETAILS | Generation | [6 empty] | Private Network - Site - GEN |  | Not in table | Not in table
Unit Name | Generation | Do not show Message on Audit or Delta |  | Removed Field from RARF form after sheet was split |  |  | ADD 02/2012 | Private Network - Site - GEN | List | GENERATION | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Site Code | Generation | Corrected and removed from Form |  | Passed/DCSES |  |  | ADD 02/2012 | Private Network - Site - GEN | Automatic | SITECODES | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
Private Network- Site Information | Generation | [6 empty] | Private Network - Site - GEN |  | Not in table | Not in table |  | This tab is conditional : Required for all Private Use Networks |  |  |  | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
Average Amount of Self-Serve private load | Generation | [6 empty] | Private Network - Site - GEN | MW | GENERATION | AVG_LD_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms | EMS
Average Amount of Self-Serve private reactive load | Generation | [6 empty] | Private Network - Site - GEN | MVAR | GENERATION | AVG_LD_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
Expected Typical Private Network Net Interchange | Generation | [6 empty] | Private Network - Site - GEN | MW | GENERATION | NET_INTERCHNG_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms | EMS
Expected Typical Private Network Net Reactive Interchange | Generation | [6 empty] | Private Network - Site - GEN | MVAR | GENERATION | NET_INTERCHNG_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
Private Network Gross Unit Capability | Generation | [6 empty] | Private Network - Site - GEN | MW | GENERATION | GROSS_CAPBLTY_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
Private Network Gross Unit Reactive Capability | Generation | [6 empty] | Private Network - Site - GEN | MVAR | GENERATION | GROSS_CAPBLTY_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
Load Characteristics for MW Load | Generation | [6 empty] | Private Network - Site - GEN |  | Not in table | Not in table |  | This tab is conditional : Required for all Private Use Networks |  |  |  | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
Large Motor, percent of total MW load | Generation | [6 empty] | Private Network - Site - GEN | % | SITECODES | PUN_MW_LARGEMTR_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Small Motor, percent of total MW load | Generation | [6 empty] | Private Network - Site - GEN | % | SITECODES | PUN_MW_SMALLMTR_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Resistive (Heating) Load, percent of total MW load | Generation | [6 empty] | Private Network - Site - GEN | % | SITECODES | PUN_MW_RESISTIVE_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Discharge Lighting, percent of total MW load | Generation | [6 empty] | Private Network - Site - GEN | % | SITECODES | PUN_MW_DISCHARGE_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Other, percent of total MW load | Generation | [6 empty] | Private Network - Site - GEN | % | SITECODES | PUN_MW_OTHER_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Load Characteristics for MVAR Load | Generation | [6 empty] | Private Network - Site - GEN |  | Not in table | Not in table |  | This tab is conditional : Required for all Private Use Networks
Large Motor, percent of total MVAR load | Generation | [6 empty] | Private Network - Site - GEN | % | SITECODES | PUN_MVAR_LARGEMTR_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Small Motor, percent of total MVAR load | Generation | [6 empty] | Private Network - Site - GEN | % | SITECODES | PUN_MVAR_SMALLMTR_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | R | Numeric | B,DVB | Lin Xu | MMS
Discharge Lighting, percent of total MVAR load | Generation | [6 empty] | Private Network - Site - GEN | % | SITECODES | PUN_MVAR_DISCHARGE_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Other, percent of total MVAR load | Generation | [6 empty] | Private Network - Site - GEN | % | SITECODES | PUN_MVAR_OTHER_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Private Network - Unit - GEN | Generation | [6 empty] | Private Network - Unit - GEN |  | Not in table | Not in table
GENERATOR DETAILS | Generation | [6 empty] | Private Network - Unit - GEN
Unit Name | Generation | Do not show Message on Audit or Delta |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 02/2012 | Private Network - Unit - GEN | List | GENERATION | UNIT_NAME |  | 1. This field is not null. Data type: Character. | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
SITE_CODE | Generation |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 02/2012 | Private Network - Unit - GEN |  | GENERATION | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
Resource Name (Unit Code/Mnemonic) | Generation |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 02/2012 | Private Network - Unit - GEN | Automatic | SITECODES | UNIT_CODE | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
Private Network - Unit Information | Generation | [6 empty] | Private Network - Unit - GEN |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Resource Type selected is non-cc non-wind Generation Resources | C |  |  | RARF Guide Version 4.0
Average Amount of Self-Serve private load | Generation | [6 empty] | Private Network - Unit - GEN | MW | GENERATION | AVG_LD_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS
Average Amount of Self-Serve private reactive load | Generation | [6 empty] | Private Network - Unit - GEN | MVAR | GENERATION | AVG_LD_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0
Expected Typical Private Network Net Interchange | Generation | [6 empty] | Private Network - Unit - GEN | MW | GENERATION | NET_INTERCHNG_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS
Expected Typical Private Network Net Reactive Interchange | Generation | [6 empty] | Private Network - Unit - GEN | MVAR | GENERATION | NET_INTERCHNG_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0
Private Network Gross Unit Capability | Generation | [6 empty] | Private Network - Unit - GEN | MW | GENERATION | GROSS_CAPBLTY_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS
Private Network Gross Unit Reactive Capability | Generation | [6 empty] | Private Network - Unit - GEN | MVAR | GENERATION | GROSS_CAPBLTY_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0
If Unit trips, does Load trip? | Generation | [6 empty] | Private Network - Unit - GEN | Y/N | GENERATION | LOAD_TRIP_FLG |  | Select from Y or N. | C | Dropdown List | B,DVB | RARF Glossary Version 4.0/RARF Guide Version 4.0
If yes, approximate percentage of Load that will trip? | Generation | [6 empty] | Private Network - Unit - GEN | % | GENERATION | LOAD_TRIP_PCT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0
Private Network - Site - CC | CC | [6 empty] | Private Network - Site - CC |  | Not in table | Not in table
SITE DETAILS | CC | [6 empty] | Private Network - Site - CC |  | Not in table | Not in table
Private Network? | CC | [6 empty] | Private Network - Site - CC | Y/N | SITECODES | PRIVATE_NTWK_SITE_FLG |  | Select from Y or N. Private Network Flag is not null | R | Dropdown List | B,DVB | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms/Kittiepong | EMS
SITE CODE | CC | REMOVED FROM CC FORM |  |  |  |  | ADD 02/2012 | Private Network - Site - CC | Automatic | CCUNIT | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
PRIVATE NETWORK - SITE INFORMATION | CC | [6 empty] | Private Network - Site - CC |  | Not in table | Not in table |  | This tab is conditional : Required for all Private Use Networks |  |  |  | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
Average Amount of Self-Serve private load | CC | [6 empty] | Private Network - Site - CC | MW | CCUNIT | AVG_LD_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms | EMS
Average Amount of Self-Serve private reactive load | CC | [6 empty] | Private Network - Site - CC | MVAR | CCUNIT | AVG_LD_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
Expected Typical Private Network Net Interchange | CC | [6 empty] | Private Network - Site - CC | MW | CCUNIT | NET_INTERCHNG_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms | EMS
Expected Typical Private Network Net Reactive Interchange | CC | [6 empty] | Private Network - Site - CC | MVAR | CCUNIT | NET_INTERCHNG_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
Private Network Gross Unit Capability | CC | [6 empty] | Private Network - Site - CC | MW | SITECODES | GROSS_CAPBLTY_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
Private Network Gross Unit Reactive Capability | CC | [6 empty] | Private Network - Site - CC | MVAR | SITECODES | GROSS_CAPBLTY_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
Load Characteristics for MW Load | CC | [6 empty] | Private Network - Site - CC |  | Not in table | Not in table |  | This tab is conditional : Required for all Private Use Networks |  |  |  | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
Large Motor, Percent Of Total | CC | [6 empty] | Private Network - Site - CC | % | SITECODES | PUN_MW_LARGEMTR_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Small Motor, Percent Of Total | CC | [6 empty] | Private Network - Site - CC | % | SITECODES | PUN_MW_SMALLMTR_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Resistive (heating) Load, Percent Of Total MW Load | CC | [6 empty] | Private Network - Site - CC | % | SITECODES | PUN_MW_RESISTIVE_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Discharge Lighting, Percent Of Total | CC | [6 empty] | Private Network - Site - CC | % | SITECODES | PUN_MW_DISCHARGE_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Other, Percent Of Total MW Load | CC | [6 empty] | Private Network - Site - CC | % | SITECODES | PUN_MW_OTHER_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Load Characteristics for MVAR Load | CC | [6 empty] | Private Network - Site - CC |  | Not in table | Not in table |  | This tab is conditional : Required for all Private Use Networks
Large Motor, Percent Of Total MVAR Load | CC | [6 empty] | Private Network - Site - CC | % | SITECODES | PUN_MVAR_LARGEMTR_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Small Motor, Percent Of Total MVAR Load | CC | [6 empty] | Private Network - Site - CC | % | SITECODES | PUN_MVAR_SMALLMTR_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | R | Numeric | B,DVB | Lin Xu | MMS
Discharge Lighting, Percent Of Total MVAR Load | CC | [6 empty] | Private Network - Site - CC | % | SITECODES | PUN_MVAR_DISCHARGE_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Other, Percent Of Total MVAR Load | CC | [6 empty] | Private Network - Site - CC | % | SITECODES | PUN_MVAR_OTHER_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Private Network - Unit - CC | CC | [6 empty] | Private Network - Unit - CC |  | Not in table | Not in table
GENERATOR DETAILS | CC | [6 empty] | Private Network - Unit - CC |  | Not in table | Not in table
Unit Name | CC | Do not show Message on Audit or Delta | [5 empty] | Private Network - Unit - CC | List | CCUNIT | UNIT_NAME |  | 1. This field is not null. Data type: Character.
SITE CODE | CC | [5 empty] | ADD 02/2012 | Private Network - Unit - CC | Automatic | CCUNIT | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
Resource Name (Unit Code/Mnemonic) | CC | [5 empty] | ADD 02/2012 | Private Network - Unit - CC | Automatic | CCUNIT | UNIT_CODE | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
PRIVATE NETWORK - UNIT INFORMATION | CC | [6 empty] | Private Network - Unit - CC |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Resource Type selected is non-cc non-wind Generation Resources | C |  |  | RARF Guide Version 4.0
Average Amount of Self-Serve private load | CC | [6 empty] | Private Network - Unit - CC | MW | CCUNIT | AVG_LD_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS
Average Amount of Self-Serve private reactive load | CC | [6 empty] | Private Network - Unit - CC | MVAR | CCUNIT | AVG_LD_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0
Expected Typical Private Network Net Interchange | CC | [6 empty] | Private Network - Unit - CC | MW | CCUNIT | NET_INTERCHNG_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS
Expected Typical Private Network Net Reactive Interchange | CC | [6 empty] | Private Network - Unit - CC | MVAR | CCUNIT | NET_INTERCHNG_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0
Private Network Gross Unit Capability | CC | [6 empty] | Private Network - Unit - CC | MW | CCUNIT | GROSS_CAPBLTY_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS
Private Network Gross Unit Reactive Capability | CC | [6 empty] | Private Network - Unit - CC | MVAR | CCUNIT | GROSS_CAPBLTY_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0
If Unit Trips, Does Load Trip? | CC | [6 empty] | Private Network - Unit - CC | Y/N | CCUNIT | LOAD_TRIP_FLG |  | Select from Y or N. | C | Dropdown List | B,DVB | RARF Glossary Version 4.0/RARF Guide Version 4.0
If Yes, Approximate Percentage Of Load That Will Trip? | CC | [6 empty] | Private Network - Unit - CC | % | CCUNIT | LOAD_TRIP_PCT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0
Private Network - Site - Wind | Wind | [6 empty] | Private Network - Site - Wind |  | Not in table | Not in table
Private Network? | Wind | [6 empty] | Private Network - Site - Wind | Y/N | SITECODES | PRIVATE_NTWK_SITE_FLG |  | Select from Y or N. Private Network Flag is not null | R | Dropdown List | B,DVB | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms/Kittiepong | EMS
SITE DETAILS | Wind | [6 empty] | Private Network - Site - Wind |  | Not in table | Not in table
Unit Name | Wind | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Private Network - Site - Wind | List | WIND | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Site Code | Wind | Corrected and removed from Form |  |  |  |  | ADD 02/2012 | Private Network - Site - Wind | Automatic | SITECODES | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
Private Network- Site Information | Wind | [6 empty] | Private Network - Site - Wind |  | Not in table | Not in table |  | This tab is conditional : Required for all Private Use Networks |  |  |  | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
Average Amount of Self-Serve private load | Wind | [6 empty] | Private Network - Site - Wind | MW | WIND | AVG_LD_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms | EMS
Average Amount of Self-Serve private reactive load | Wind | [6 empty] | Private Network - Site - Wind | MVAR | WIND | AVG_LD_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
Expected Typical Private Network Net Interchange | Wind | [6 empty] | Private Network - Site - Wind | MW | WIND | NET_INTERCHNG_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms | EMS
Expected Typical Private Network Net Reactive Interchange | Wind | [6 empty] | Private Network - Site - Wind | MVAR | WIND | NET_INTERCHNG_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
Private Network Gross Unit Capability | Wind | [6 empty] | Private Network - Site - Wind | MW | WIND | GROSS_CAPBLTY_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
Private Network Gross Unit Reactive Capability | Wind | [6 empty] | Private Network - Site - Wind | MVAR | WIND | GROSS_CAPBLTY_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
Load Characteristics for MW Load | Wind | [6 empty] | Private Network - Site - Wind |  | Not in table | Not in table |  | This tab is conditional : Required for all Private Use Networks |  |  |  | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
Large Motor, percent of total MW load | Wind | [6 empty] | Private Network - Site - Wind | % | SITECODES | PUN_MW_LARGEMTR_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Small Motor, percent of total MW load | Wind | [6 empty] | Private Network - Site - Wind | % | SITECODES | PUN_MW_SMALLMTR_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Resistive (Heating) Load, percent of total MW load | Wind | [6 empty] | Private Network - Site - Wind | % | SITECODES | PUN_MW_RESISTIVE_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Discharge Lighting, percent of total MW load | Wind | [6 empty] | Private Network - Site - Wind | % | SITECODES | PUN_MW_DISCHARGE_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Other, percent of total MW load | Wind | [6 empty] | Private Network - Site - Wind | % | SITECODES | PUN_MW_OTHER_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Load Characteristics for MVAR Load | Wind | [6 empty] | Private Network - Site - Wind |  | Not in table | Not in table |  | This tab is conditional : Required for all Private Use Networks
Large Motor, percent of total MVAR load | Wind | [6 empty] | Private Network - Site - Wind | % | SITECODES | PUN_MVAR_LARGEMTR_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Small Motor, percent of total MVAR load | Wind | [6 empty] | Private Network - Site - Wind | % | SITECODES | PUN_MVAR_SMALLMTR_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | R | Numeric | B,DVB | Lin Xu | MMS
Discharge Lighting, percent of total MVAR load | Wind | [6 empty] | Private Network - Site - Wind | % | SITECODES | PUN_MVAR_DISCHARGE_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Other, percent of total MVAR load | Wind | [6 empty] | Private Network - Site - Wind | % | SITECODES | PUN_MVAR_OTHER_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | B,DVB | Lin Xu | MMS
Private Network - Unit - Wind | Wind | [6 empty] | Private Network - Unit - Wind |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Resource Type selected is non-cc non-wind Generation Resources | C |  |  | RARF Guide Version 4.0
UNIT DETAILS | Wind | [6 empty] | Private Network - Unit - Wind |  | Not in table | Not in table
Unit Name | Wind | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Private Network - Unit - Wind | List | WIND | UNIT_NAME | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | 1. This field is not null. Data type: Character. | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
SITE_CODE | Wind | [5 empty] | ADD 02/2012 | Private Network - Unit - Wind | Automatic | WIND | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
Resource Name (Unit Code/Mnemonic) | Wind | [5 empty] | ADD 02/2012 | Private Network - Unit - Wind | Automatic | WIND | UNIT_CODE | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
Private Network - Unit Information | Wind | [6 empty] | Private Network - Unit - Wind |  | Not in table | Not in table | This tab is conditional. Required if the Generation Resource Type selected is non-cc non-wind Generation Resources | 3. Should not allow spaces |  |  | RARF Guide Version 4.0
Average Amount of Self-Serve private load | Wind | [6 empty] | Private Network - Unit - Wind | MW | WIND | AVG_LD_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS
Average Amount of Self-Serve private reactive load | Wind | [6 empty] | Private Network - Unit - Wind | MVAR | WIND | AVG_LD_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0
Expected Typical Private Network Net Interchange | Wind | [6 empty] | Private Network - Unit - Wind | MW | WIND | NET_INTERCHNG_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS
Expected Typical Private Network Net Reactive Interchange | Wind | [6 empty] | Private Network - Unit - Wind | MVAR | WIND | NET_INTERCHNG_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0
Private Network Gross Unit Capability | Wind | [6 empty] | Private Network - Unit - Wind | MW | WIND | GROSS_CAPBLTY_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0 | EMS
Private Network Gross Unit Reactive Capability | Wind | [6 empty] | Private Network - Unit - Wind | MVAR | WIND | GROSS_CAPBLTY_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0
If Unit trips, does Load trip? | Wind | [6 empty] | Private Network - Unit - Wind | Y/N | WIND | LOAD_TRIP_FLG |  | Select from Y or N. | C | Dropdown List | B,DVB | RARF Glossary Version 4.0/RARF Guide Version 4.0
If yes, approximate percentage of Load that will trip? | Wind | [6 empty] | Private Network - Unit - Wind | % | WIND | LOAD_TRIP_PCT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric | B | RARF Glossary Version 4.0/RARF Guide Version 4.0
General Information - ALL (LAAR FORM) | LAAR | [6 empty] | General Information - LAAR |  | Not in table | Not in table |  | This tab is conditional. Required if the Resource Type is selected as ' Load ' | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0 | EMS,MMS,NMMS
This submittal is for: | LAAR | 03/09/2012 Already in form added to mapping document | [5 empty] | General Information - LAAR |  | LOAD_RESOURCES | SUBMIR_REASON |  | Not null. Select from the list: New Resource Entity, Revision, Additions or Deletions | R | Dropdown List | B,DVB
Date Form Completed: | LAAR |  | NO DATA |  |  |  |  | General Information - LAAR |  | LOAD_RESOURCES | FORM_COMP_DT |  | Optional | O | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Resource Entity Submitting Form: | LAAR | 03/09/2012 Updated Validation | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | General Information - LAAR |  | RE_RARF | RE_NAME |  | 1. Not null 2. Name must match ERCOT records (SIEBEL) 1.This field is not null. 2. All should be capital letters 3.No Special characters except spaces and dashes. | R | Character | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
Resource Entity DUNS #: | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | General Information - LAAR |  | RE_RARF | RE_DUNS |  | 2. Name must match ERCOT records (SIEBEL) | R | Character | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk
Printed Name: | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | General Information - LAAR |  | LOAD_RESOURCES | NAME_AR |  | Not null | R | Character | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
Title: | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | General Information - LAAR |  | LOAD_RESOURCES | TITLE_AR |  | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Phone Number: | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | General Information - LAAR |  | LOAD_RESOURCES | PHONE_AR |  | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
E-mail Address: | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | General Information - LAAR |  | LOAD_RESOURCES | EMAIL_AR |  | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Fax Number: | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | General Information - LAAR |  | LOAD_RESOURCES | FAX_AR |  | Optional | O | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
Load Resource Information | LAAR | [6 empty] | Load Resource Information |  | Not in table | Not in table
UNIT DETAILS | LAAR | [6 empty] | Load Resource Information |  | Not in table | Not in table
Name of End Use Customer | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information |  | LOAD_RESOURCES | END_USE_CUSTOMER |  | This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
Common Name for Load Resource | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information |  | LOAD_RESOURCES | COMMON_NAME_LOAD_RSRC |  | This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
Dispatch Asset Code | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Parameters |  | LOAD_RESOURCES | DISPATCH_ASSET_CODE
Physical Street Address for point of Delivery (POD) | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information |  | LOAD_RESOURCES | STREET_ADD_POD |  | This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
Name of City for Point of Delivery (POD) | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information |  | LOAD_RESOURCES | CITY_POD |  | This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
Is Load Netted From Generation at ERCOT Read Gensite? | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information | Y/N | LOAD_RESOURCES | LOAD_NET_FROM_GENSITE_FLG |  | This field is not null. Select from the list :Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0
Is Load Behind a NOIE Settlement Meter Point? | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information | Y/N | LOAD_RESOURCES | LOAD_BEHIND_NOIE_FLG |  | This field is not null. Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0
Load Resource Type (CLR/UFR/Interruptible) | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information |  | LOAD_RESOURCES | LOAD_RESOURCE_TYPE |  | Select from the list: CLR,UFR or Interruptible. Load Resource Type is not null | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0 | EMS
If CLR, will CLR be Dynamically Scheduling? | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information | Y/N | LOAD_RESOURCES | CLR_DYNAMIC_SCHED_FLG |  | Select from the list Y or N. This field is optional. This field is required for CLR and optional for other types | C/O | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0
Load Resource Effective Date | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information | Y/N | LOAD_RESOURCES | LOAD_RESOURCE_EFF_DATE |  | This field is not null. Date format should be MM/DD/YYYY | R | Date time | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
Load Resource Expiration Date | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information | MM/DD/YYYY | LOAD_RESOURCES | LOAD_RESOURCE_EXP_DATE |  | This field is optional. Date format should be MM/DD/YYYY. NA is not valid, Leave it blank if not applicable | O | Date time | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
Substation Name for POD | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information | (all caps) | LOAD_RESOURCES | SUBSTATION_NAME_POD |  | This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
Substation Code for POD | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information | (all caps) | LOAD_RESOURCES | SUBSTATION_CODE_POD |  | This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
Unit Name | LAAR | [5 empty] | REMOVE | Load Resource Information |  | LOAD_RESOURCES |  |  | This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
ESIID Station Name | LAAR | [5 empty] | REMOVE | Load Resource Information |  | LOAD_RESOURCES |  |  | REMOVE 11/11/2011 This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
ESIID Station Code | LAAR | [5 empty] | REMOVE | Load Resource Information |  | LOAD_RESOURCES |  |  | REMOVE 11/11/2011 This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
Transmission Bus POD (PTI Bus No) | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information |  | LOAD_RESOURCES | TRANSMISSION_BUS_POD |  | 1.This field is not null and should be a number 2.ERCOT needs to associate each load resource to one and only one load in the network model used by State Estimator. For lack of a better source of information; the static network model load connected at this PTI bus number is what this load resource will be mapped to. Therefore there MUST be a static network model load at this PTI bus number (CIM). | R | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
Transmission Station Voltage | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information | KV | LOAD_RESOURCES | VOLTAGE_LVL_TLMTRD_LOAD |  | This field is not null and should be a number | R | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
Transmission Station Load Name in Network Operations Model | LAAR |  | ADD 04/2012 |  |  |  | ADD 04/2012 | Load Resource Information | (all caps) | LOAD_RESOURCES | TRANS_STAT_LOAD_NAM_NOM |  | ALL CAPS
Meter Reading Entity (TDSP) | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information |  | LOAD_RESOURCES | MTR_RDG_ENTITY_TDSP |  | This field is not null. | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
Meter Reading Entity Duns Number | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information |  | LOAD_RESOURCES | MTR_RDG_ENTITY_DUNS |  | This field is not null. This is either 9 or 13 digit number. Validate with the existing record in ERCOT?? | R | Integer | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
QSE Name | LAAR | [5 empty] | REMOVE | Load Resource Information |  | LOAD_RESOURCES |  |  | REMOVE 11/11/2011 | R | Character | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 | NMMS
QSE Duns Number | LAAR | [5 empty] | REMOVE | Load Resource Information |  | LOAD_RESOURCES |  |  | REMOVE 11/11/2011 | R | Integer | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 | NMMS
ESI-ID assigned to meter | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information |  | LOAD_RESOURCES | ESIID_ASSIGNED |  | This field is not null and should be a number. Data type is character | R | Character | B | Angela Moy/RARF Glossary Version 4.0 /RARF Guide version 4.0
Wholesale Delivery Point? | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information | Y/N | LOAD_RESOURCES | WHOLESALE_DLVRY_PT |  | This field is not null. Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0
High Set Under-frequency Relay (UFR) Setting | LAAR | [5 empty] | REMOVE | Load Resource Information |  | LOAD_RESOURCES |  |  | REMOVE 11/11/2011 This field is not null. This field is conditional: Required for UFR Load Resource Type and CLR Load Resource Type where the flag is checked stating that the Resource can operate as UFR. In that case the value should not be less than 59.7 Hz. (An Interruptible Load Resource Type would not enter a value, nor would a Load Resource that was just a CLR.) | C | Numeric | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
Load Resource Control Device | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 | POD | TOTAL | LOAD |  | Load Resource Information |  | LOAD_RESOURCES | LOAD_RES_CTRL_DEVICE |  | This field is not null | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0 /RARF Guide version 4.0
If CLR, ability to operate as a UFR type Resource? | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information | Y/N | LOAD_RESOURCES | CLR_OPERATE_AS_UFR_FLG |  | This field is not null. Select from Y or N. If 'Y' , must fill all the fields for both resource types. If 'N', Need to fill fields specific to CLR only | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0
ERCOT Load Zone | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information |  | LOAD_RESOURCES | ERCOT_LOAD_ZONE |  | This field is a required and data type is character | R | Character | B,DVB | RARF Glossary Version 4.0 /Angela Moy
Maximum POD Total Load | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 | POD | TOTAL | LOAD |  | Load Resource Information | MW | LOAD_RESOURCES | MAX_POD_TOTAL_LOAD |  | Maximum POD Total Load >= Summer Interruptible MW.This field is not null and should be a Number | R | Numeric | B,DVB | Lin Xu | MMS
Maximum Interruptible Load MW | LAAR |  | Field needs to be added to RARF Audit and Delta |  |  |  | ADD 02/2012 | Load Resource Information | MW | LOAD_RESOURCES | MAX_INT_LOAD_MW |  | Maximum POD Total Load >= Summer Interruptible MW.This field is not null and should be a Number
Summer Interruptible MW | LAAR |  | Created defect 20114 to remove field on Load Resource Table |  |  |  | REMOVE | Load Resource Information |  | LOAD_RESOURCES |  |  | REMOVE 11/11/2011 Maximum POD Total Load >= Summer Interruptible MW.This field is not null and should be a Number | R | Numeric | B,DVB | Lin Xu | MMS
Winter Interruptible MW | LAAR |  | Created defect 20114 to remove field on Load Resource Table |  |  |  | REMOVE | Load Resource Information |  | LOAD_RESOURCES |  |  | REMOVE 11/11/2011 Maximum POD Total Load >= Winter Interruptible MW. This field is not null and should be a Number | R | Numeric | B,DVB | Lin Xu | MMS
High Reasonability Limit | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information | MW | LOAD_RESOURCES | HIGH_REAS_LIMIT |  | 1. HRL >=0 . 2. High Reasonability Limit >=HSL or MPC.This field is not null and should be a Number 3. Value must be >= LRL 4. HRL >= Both Summer Interruptible MW and Winter Interruptible MW Rating | R | Numeric | B,DVB | RARF Workshop for Load Resources/ RARF Glossary Version 4.0 /RARF Guide version 4.0/Steve Krein | EMS
Low Reasonability Limit | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information | MW | LOAD_RESOURCES | LOW_REAS_LIMIT |  | 1. LRL should be <= HRL. LRL must be >= 0 2. Low Reasonability Limit <= LSL or LPC. This field is not null and should be a Number Note in most cases the LRL = LSL = LPC = 0 | R | Numeric | B,DVB | Angela Moy/RARF Workshop for Load Resources/ RARF Glossary Version 4.0 /RARF Guide version 4.0/Steve Krein | EMS
CLR High Reasonability Ramp Rate Limit | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information | MW/min | LOAD_RESOURCES | HIGH_REAS_RAMPRATE_LIMIT |  | 1. CLR High Reasonability Ramp Rate Limit >= Low Reasonability Ramp Rate Limit. This field is conditional: Required only if Load Resource type selected is 'CLR'. Must be a positive number. This field can not be null if Load Resource type selected is 'CLR'. | C | Numeric | B,DVB | Lin Xu/kiittipong/Jamil Daouk | MMS
CLR Low Reasonability Ramp Rate Limit | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information | MW/min | LOAD_RESOURCES | LOW_REAS_RAMPRATE_LIMIT |  | 1. CLR LowReasonableRampRateLimit <= Emergency Downward ramp rate <= CLR HighReasonableRampRateLimit. This field is conditional: Required only if Load Resource type selected is 'CLR'. Must be a positive number. This field can not be null if Load Resource type selected is 'CLR'. | C | Numeric | B,DVB | Lin Xu/kiittipong/Jamil Daouk | MMS
Private Use Network? | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Information | Y/N | LOAD_RESOURCES | PRIVATE_USE_NETWRK_FLG |  | Select from the list: Y or N. This field is Not null | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0
Load Resource Parameters | LAAR | [6 empty] | Load Resource Parameters |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type selected is ' Load ' | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0 | MMS,NMMS
Non-CLR Resource Parameters | LAAR | [6 empty] | Load Resource Parameters |  | Not in table | Not in table |  | This Section is conditional: Required {if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C |  | B,DVB | Scott Middleton | NMMS
Dispatch Asset Code | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Parameters |  | LD_RES_RAMPRATE_NRRC | DISPATCH_ASSET_CODE
Non-CLR Resource Parameters | LAAR | [6 empty] | Load Resource Parameters |  | Not in table | Not in table
Minimum Interruption Time | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Parameters | hours | LOAD_RESOURCES | MIN_INTERUPT_TIME |  | 1. Minimum Interruption Time <= Maximum Interruption Time. 2.Minimum Interruption Time >=0. This field should not be null 3.Unit of measure is hour - This number should be rounded up to the nearest whole number (can't dispatch for partial hours). Data type is Integer. 4.This Field is conditional: Required {if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Integer | B,DVB | Lin Xu/kiittipong/Jamil Daouk/Scott Middleton | MMS,NMMS
Minimum Restoration Time | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Parameters | hours | LOAD_RESOURCES | MIN_RESTOR_TIME |  | 1.Minimum Restoration Time >=0. This field should not be null. 2.Unit of measure is hour - This number should be rounded up to the nearest whole number (can't dispatch for partial hours). Data type is Integer 3.This Field is conditional: Required {if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Integer | B,DVB | Lin Xu/kiittipong/Jamil Daouk/Scott Middleton | MMS,NMMS
Max WEEKLY Deployments | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Parameters |  | LOAD_RESOURCES | MAX_WKLY_DEPLOYS |  | 1.Max WEEKLY Deployments > =0. This field should not be null and It is an Integer. 2.This Field is conditional: Required {if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Integer | B,DVB | Lin Xu/kiittipong/Scott Middleton | MMS,NMMS
Max Interruption Time | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Parameters |  | LOAD_RESOURCES | MAX_INTERUPT_TIME |  | 1.Max Interruption Time > 0. 2.Unit of measure is hours, with only 1 digit after decimal point 3.This Field is conditional: Required {if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Numeric | B,DVB | Lin Xu/kiittipong/Jamil Daouk/Scott Middleton | MMS,NMMS
Max DAILY Deployments | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Parameters |  | LOAD_RESOURCES | MAX_DAILY_DEPLOYS |  | 1.Max WEEKLY Deployments > Max DAILY Deployments. 2.Maximum Daily Deployment is not null and it is an Integer 3.This Field is conditional: {Required if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Integer | B,DVB | Lin Xu/kiittipong/Scott Middleton | MMS,NMMS
Max Weekly Energy | LAAR |  | PASSED/EXXON-001213214 and THE DOW COMPANY - 0013815811000 |  |  |  |  | Load Resource Parameters | MWh | LOAD_RESOURCES | MAX_WKLY_ENERGY |  | 1.Max Weekly Energy > =0. 2.This Field is conditional: Required {if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Numeric | B,DVB | Lin Xu/kiittipong/Scott Middleton | MMS,NMMS
Minimum Notice Time | LAAR |  | PASSED/EXXON-001213214 |  |  |  |  | Load Resource Parameters | minutes | LOAD_RESOURCES | MIN_NOTICE_TIME |  | 1.Minimum Notice Time > =0 2.Unit of measure is hour - This number should be rounded up to the nearest whole number (can't dispatch for partial hours). Data type is Integer 3.This Field is conditional: Required {if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Integer | B,DVB | Lin Xu/kiittipong/Jamil Daouk/Scott Middleton | MMS,NMMS
CLR Resource Parameters | LAAR | [6 empty] | Load Resource Parameters |  | Not in table | Not in table |  | This section is conditional: Required ONLY if the Load Resource Type is CLR | C
CLR Resource Parameters | LAAR | [6 empty] | Load Resource Parameters |  | Not in table | Not in table
Max Deployment Time | LAAR |  | PASSED/APD |  |  |  |  | Load Resource Parameters | hours | LOAD_RESOURCES | MAX_DEPLOY_TIME_CLR |  | 1.Max Deployment Time > 0 2.Unit of measure is hour - This number should be rounded down to the nearest whole number (can't dispatch for partial hours). Data type is Integer | C | Integer | B,DVB | Lin Xu/kiittipong/Jamil Daouk | MMS
Max Weekly Energy | LAAR |  | PASSED/APD |  |  |  |  | Load Resource Parameters | MWh | LOAD_RESOURCES | MAX_WKLY_ENERGY_CLR |  | Max Weekly Energy > =0 | C | Numeric | B,DVB | Lin Xu/kiittipong | MMS
CLR - Normal Ramp Rate Curve | LAAR | [6 empty] | Load Resource Parameters |  | Not in table | Not in table |  | This section is conditional: Required ONLY if the Load Resource Type is CLR | C |  |  | Lin Xu | MMS
CLR - Normal Ramp Rate Curve | LAAR | [6 empty] | Load Resource Parameters |  | Not in table | Not in table
MW1 to 10 | LAAR |  | PASSED/APD |  |  |  |  | Load Resource Parameters | MW | LD_RES_RAMPRATE_NRRC | MW_NUMBER_NRRC |  | 1. MW1 to MW10 are increasing MW Values. 2.MW1 can't be null, and must have value for both ramp up and ramp down | C | Numeric | B,DVB | RARF Guide Version 4.0/ Jamil Daouk | NMMS
Upward RampRate1 to 10 | LAAR |  | PASSED/APD |  |  |  |  | Load Resource Parameters | MW/min | LD_RES_RAMPRATE_NRRC | UPWARD_RAMPRATE_NRRC |  | 1. CLR Normal Upward Ramp Rate <= CLR Emergency Upward Ramp Rate. Zero or negative ramp rate values are not allowed. Normal Up ramp rate > 0 if breakpoint is given. 2. If Load Resource Type is 'CLR/UFR' then verify thatLowReasonableRampRateLimit <= Normal Up ramp rate <= HighReasonableRampRateLimit | C | Numeric | B,DVB | Lin Xu/kiittipong | MMS,NMMS
Downward RampRate1 to 10 | LAAR |  | PASSED/APD |  |  |  |  | Load Resource Parameters | MW/min | LD_RES_RAMPRATE_NRRC | DOWNWARD_RAMPRATE_NRRC |  | 1.Zero or negative ramp rate values are not allowed. CLR Normal Downward Ramp Rate <= Emergency Downward Ramp Rate. Normal Dn ramp rate > 0 if breakpoint is given 2. If Load Resource Type is 'CLR/UFR' then verify that LowReasonableRampRateLimit <= Normal Dn ramp rate <= HighReasonableRampRateLimit | C | Numeric | B,DVB | Lin Xu/kiittipong | MMS,NMMS
CLR - Emergency Ramp Rate Curve | LAAR | [6 empty] | Load Resource Parameters |  | Not in table | Not in table |  | This section is conditional: Required ONLY if the Load Resource Type is CLR | C |  |  | Lin Xu | MMS,NMMS
CLR - Emergency Ramp Rate Curve | LAAR | [6 empty] | Load Resource Parameters |  | Not in table | Not in table
MW1 to 10 | LAAR |  | PASSED/APD |  |  |  |  | Load Resource Parameters | MW | LD_RES_RAMPRATES_ERRC | MW_NUMBER_ERRC |  | 1. MW1 to MW10 are increasing MW Values. 2.MW1 can't be null, and must have value for both ramp up and ramp down | C | Numeric | B,DVB | Lin Xu/ Jamil Daouk | MMS,NMMS
Upward RampRate1 to 10 | LAAR |  | PASSED/APD |  |  |  |  | Load Resource Parameters | MW/min | LD_RES_RAMPRATES_ERRC | UPWARD_RAMPRATE_ERRC |  | CLR Normal Upward Ramp Rate <= CLR Emergency Upward Ramp Rate. Zero or negative ramp rate values are not allowed. No null values are allowed, required for each CLR. LowReasonableRampRateLimit <= Emergency Up ramp rate <= HighReasonableRampRateLimit | C | Numeric | B,DVB | Lin Xu/kiittipong | MMS,NMMS
Downward RampRate1 to 10 | LAAR |  | PASSED/APD |  |  |  |  | Load Resource Parameters | MW/min | LD_RES_RAMPRATES_ERRC | DOWNWARD_RAMPRATE_ERRC |  | Zero or negative ramp rate values are not allowed. If Load Resource Type is 'CLR/UFR' then verify that LowReasonableRampRateLimit <= Emergency Dn ramp rate <= HighReasonableRampRateLimit | C | Numeric | B,DVB | Lin Xu/kiittipong | MMS,NMMS
Protection - GEN | Generation | [6 empty] | Protection - GEN |  | Not in table | Not in table |  | Not all the fields need to be complete. Only the fields that have Data.
GENERATOR DETAILS | Generation | [6 empty] | Protection - GEN |  | Not in table | Not in table
Unit Name | Generation | Do not show Message on Audit or Delta |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 02/2012 | Protection - GEN | List | GENERATION | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Generation |  |  | This field already existed in RARF HUB, was just added to RARF FORM/Passed |  |  | ADD 02/2012 | Protection - GEN | Automatic | GENERATION | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Breaker Interruption Time | Generation | [6 empty] | Protection - GEN |  | Not in table | Not in table
Breaker Interruption Time | Generation | [6 empty] | Protection - GEN | cycles | GENERATION | BREAKER_INTERRUP |  | 1) this field is required 2) Data type must be Integer | R | Integer | B | Planning Team
PLANT VOLTAGE PROTECTION | Generation | [6 empty] | Protection - GEN |  | Not in table | Not in table
Instantaneous Under voltage Trip | Generation | [6 empty] | Protection - GEN | p.u. | GENERATION | UVOLT_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | O | Float | B | Planning Team
Instantaneous Under voltage Trip - Time 1 Time 2 Time 3 Time 4 | Generation | [6 empty] | Protection - GEN | sec | GENERATION | UVOLT_TRIP_TIME1 UVOLT_TRIP_TIME2 UVOLT_TRIP_TIME3 UVOLT_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | C | Float |  | Planning Team
Instantaneous Under voltage Trip - Under voltage 1 Under voltage 2 Under voltage 3 Under voltage 4 | Generation | [6 empty] | Protection - GEN | p.u. | GENERATION | UVOLT_TRIP_VOLT1 UVOLT_TRIP_VOLT2 UVOLT_TRIP_VOLT3 UVOLT_TRIP_VOLT4 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Under voltage 1 is required, Under voltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | R | Float | B | Planning Team
Instantaneous Overvoltage Trip | Generation | [6 empty] | Protection - GEN | p.u. | GENERATION | OVOLT_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | O | Float | B | Planning Team
Instantaneous Overvoltage Trip Time 1 Time 2 Time 3 Time 4 | Generation | [6 empty] | Protection - GEN | sec | GENERATION | OVOLT_TRIP_TIME1 OVOLT_TRIP_TIME2 OVOLT_TRIP_TIME3 OVOLT_TRIP_TIME4 |  | 11) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | R | Float | B | Planning Team
Instantaneous Overvoltage Trip - Overvoltage 1 Overvoltage 2 Overvoltage 3 Overvoltage 4 | Generation | [6 empty] | Protection - GEN | p.u. | GENERATION | OVOLT_TRIP_VOLT1 OVOLT_TRIP_VOLT2 OVOLT_TRIP_VOLT3 OVOLT_TRIP_VOLT4 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Under voltage 1 is required, Under voltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | O | Float | B | Planning Team
Plant Frequency Protection | Generation | [6 empty] | Protection - GEN |  | Not in table | Not in table
Instantaneous Under frequency Trip | Generation | [6 empty] | Protection - GEN | Hz | GENERATION | UFREQ_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float | O | Float | B | Planning Team
Instantaneous Under frequency Trip Time 1 Time 2 Time 3 Time 4 | Generation | [6 empty] | Protection - GEN | sec | GENERATION | UFREQ_TRIP_TIME1 UFREQ_TRIP_TIME2 UFREQ_TRIP_TIME3 UFREQ_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R | Float | B | Planning Team
Instantaneous Under frequency Trip - Under frequency 1 Under frequency 2 Under frequency 3 Under frequency 4 | Generation | [6 empty] | Protection - GEN | Hz | GENERATION | UFREQ_TRIP_HZ1 UFREQ_TRIP_HZ2 UFREQ_TRIP_HZ3 UFREQ_TRIP_HZ4 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Under frequency 1 is required, Under frequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | R | Float | B | Planning Team
Instantaneous Over frequency Trip | Generation | [6 empty] | Protection - GEN | Hz | GENERATION | OFREQ_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float | O | Float | B | Planning Team
Instantaneous Over frequency Trip Time 1 Time 2 Time 3 Time 4 | Generation | [6 empty] | Protection - GEN | sec | GENERATION | OFREQ_TRIP_TIME1 OFREQ_TRIP_TIME2 OFREQ_TRIP_TIME3 OFREQ_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R | Float | B | Planning Team
Instantaneous Over frequency Trip - Over frequency 1 Over frequency 2 Over frequency 3 Over frequency 4 | Generation | [6 empty] | Protection - GEN | Hz | GENERATION | OFREQ_TRIP_HZ1 OFREQ_TRIP_HZ2 OFREQ_TRIP_HZ3 OFREQ_TRIP_HZ4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Over frequency 1 is required, Over frequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | R | Float | B | Planning Team
Protection - CC | Generation | [6 empty] | Protection - CC |  | Not in table | Not in table |  | Not all the fields need to be complete. Only the fields that have Data. Upto 3 trains per site can be registered |  |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
GENERATOR DETAILS | Generation | [6 empty] | Protection - CC |  | Not in table | Not in table
Unit Name | Generation | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Protection - CC | List | CCUNIT | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
SITE_CODE | Generation | [5 empty] | ADD 02/2012 | Protection - CC | Automatic | CCUNIT | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
Resource Name (Unit Code/mnemonic) | Generation | [5 empty] | ADD 02/2012 | Protection - CC | Automatic | CCUNIT | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
PLANT VOLTAGE PROTECTION | CC | [6 empty] | Protection - CC |  | Not in table | Not in table
Breaker Interruption Time | CC | [6 empty] | Protection - CC | cycles | CCUNIT | BREAKER_INTERRUP |  | 1) this field is required 2) Data type must be Integer | R | Integer | B | Planning Team
Instantaneous Undervoltage Trip | CC | [6 empty] | Protection - CC | p.u. | CCUNIT | UVOLT_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
nstantaneous Under voltage Trip - Time 1 Time 2 Time 3 Time 4 | CC | [6 empty] | Protection - CC | sec | CCUNIT | UVOLT_TRIP_TIME1 UVOLT_TRIP_TIME2 UVOLT_TRIP_TIME3 UVOLT_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6) Time settings should exist if time delayed under/voltage SETTINGS defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab
Instantaneous Under voltage Trip - Undervoltage 1 Undervoltage 2 Undervoltage 3 Undervoltage 4 | CC | [6 empty] | Protection - CC | p.u. | CCUNIT | UVOLT_TRIP_VOLT1 UVOLT_TRIP_VOLT2 UVOLT_TRIP_VOLT3 UVOLT_TRIP_VOLT4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Over Voltage 1 is required, OverVoltage2,3,4 are optional 4)This should be expressed in p.u values 5)Voltage settings should exist if time settings are defined 6)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Instantaneous Overvoltage Trip | CC | [6 empty] | Protection - CC | p.u. | CCUNIT | OVOLT_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | O | Float | B | Planning Team
Instantaneous Overvoltage Trip Time 1 Time 2 Time 3 Time 4 | CC | [6 empty] | Protection - CC | sec | CCUNIT | OVOLT_TRIP_TIME1 OVOLT_TRIP_TIME2 OVOLT_TRIP_TIME3 OVOLT_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6) Time settings should exist if time delayed under/voltage SETTINGS defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab | C | Float | B | Planning Team
Instantaneous Overvoltage Trip - Overvoltage 1 Overvoltage 2 Overvoltage 3 Overvoltage 4 | CC | [6 empty] | Protection - CC | p.u. | CCUNIT | OVOLT_TRIP_VOLT1 OVOLT_TRIP_VOLT2 OVOLT_TRIP_VOLT3 OVOLT_TRIP_VOLT4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Over Voltage 1 is required, OverVoltage2,3,4 are optional 4)This should be expressed in p.u values 5)Voltage settings should exist if time settings are defined 6)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | R | Float | B | Planning Team
PLANT FREQUENCY PROTECTION | CC | [6 empty] | Protection - CC |  | Not in table | Not in table
Instantaneous Underfrequency Trip | CC | [6 empty] | Protection - CC | Hz | CCUNIT | UFREQ_TRIP_INSTANT |  | 1) This field is OPTIONAL 2) Data type must be Float | O | Float | B | Planning Team
Instantaneous Under frequency Trip Time 1 Time 2 Time 3 Time 4 | CC | [6 empty] | Protection - CC | sec | CCUNIT | UFREQ_TRIP_TIME1 UFREQ_TRIP_TIME2 UFREQ_TRIP_TIME3 UFREQ_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | C | Float | B | Planning Team
Instantaneous Under frequency Trip - Underfrequency 1 Underfrequency 2 Underfrequency 3 Underfrequency 4 | CC | [6 empty] | Protection - CC | Hz | CCUNIT | UFREQ_TRIP_HZ1 UFREQ_TRIP_HZ2 UFREQ_TRIP_HZ3 UFREQ_TRIP_HZ4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Under frequency 1 is required, Under frequency 2,3,4 are optional 8) Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | R | Float | B | Planning Team
Instantaneous Overfrequency Trip | CC | [6 empty] | Protection - CC | Hz | CCUNIT | OFREQ_TRIP_INSTANT |  | 1) This field is OPTIONAL 2) Data type must be Float | O | Float | B | Planning Team
Instantaneous Over frequency Trip Time 1 Time 2 Time 3 Time 4 | CC | [6 empty] | Protection - CC | sec | CCUNIT | OFREQ_TRIP_TIME1 OFREQ_TRIP_TIME2 OFREQ_TRIP_TIME3 OFREQ_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | C | Float | B | Planning Team
nstantaneous Over frequency Trip - Overfrequency 1 Overfrequency 2 Overfrequency 3 Overfrequency 4 | CC | [6 empty] | Protection - CC | Hz | CCUNIT | OFREQ_TRIP_HZ1 OFREQ_TRIP_HZ2 OFREQ_TRIP_HZ3 OFREQ_TRIP_HZ4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Over frequency 1 is required, Over frequency 2,3,4 are optional 5)Frequency settings should exist if time settings are defined’ Plant Frequency Protection tab | R | Float | B | Planning Team
Protection - Wind | Wind | [6 empty] | Protection - Wind |  | Not in table | Not in table |  | Not all the fields need to be complete. Only the fields that have Data.
GENERATOR DETAILS | Wind | [6 empty] | Protection - Wind |  | Not in table | Not in table
Unit Name | Wind | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Protection - Wind | List | WIND | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
SITE_CODE | Wind | [5 empty] | ADD 02/2012 | Protection - Wind | Automatic | WIND | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk
Resource Name (Unit Code/Mnemonic) | Wind | [5 empty] | ADD 02/2012 | Protection - Wind | Automatic | WIND | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
Breaker Interruption Time | Wind | [6 empty] | Protection - Wind |  | Not in table | Not in table
Breaker Interruption Time | Wind | [6 empty] | Protection - Wind | cycles | WIND | BREAKER_INTERRUP |  | 1) this field is required 2) Data type must be Integer | R | Integer | B | Planning Team
PLANT VOLTAGE PROTECTION | Wind | [6 empty] | Protection - Wind |  | Not in table | Not in table
Instantaneous Under voltage Trip | Wind | [6 empty] | Protection - Wind | p.u. | Wind | UVOLT_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | O | Float | B | Planning Team
Instantaneous Under voltage Trip - Time 1 Time 2 Time 3 Time 4 | Wind | [6 empty] | Protection - Wind | sec | Wind | UVOLT_TRIP_TIME1 UVOLT_TRIP_TIME2 UVOLT_TRIP_TIME3 UVOLT_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage SETTINGS defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | R | Float |  | Planning Team
Instantaneous Under voltage Trip - Under voltage 1 Under voltage 2 Under voltage 3 | Wind | [6 empty] | Protection - Wind | p.u. | Wind | UVOLT_TRIP_VOLT1 UVOLT_TRIP_VOLT2 UVOLT_TRIP_VOLT3 UVOLT_TRIP_VOLT4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Under voltage 1 is required, Under voltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | R | Float | B | Planning Team
Instantaneous Overvoltage Trip | Wind | [6 empty] | Protection - Wind | p.u. | Wind | OVOLT_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values 4)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | O | Float | B | Planning Team
Instantaneous Overvoltage Trip Time 1 Time 2 Time 3 Time 4 | Wind | [6 empty] | Protection - Wind | sec | Wind | OVOLT_TRIP_TIME1 OVOLT_TRIP_TIME2 OVOLT_TRIP_TIME3 OVOLT_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage SETTINGS defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | R | Float | B | Planning Team
Instantaneous Overvoltage Trip - Overvoltage 1 Overvoltage 2 Overvoltage 3 Overvoltage 4 | Wind | [6 empty] | Protection - Wind | p.u. | Wind | OVOLT_TRIP_VOLT1 OVOLT_TRIP_VOLT2 OVOLT_TRIP_VOLT3 OVOLT_TRIP_VOLT4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Overvoltage 1 is required, Overvoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | R | Float | B | Planning Team
Plant Frequency Protection | Wind | [6 empty] | Protection - Wind |  | Not in table | Not in table
Instantaneous Under frequency Trip | Wind | [6 empty] | Protection - Wind | Hz | Wind | UFREQ_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float | O | Float | B | Planning Team
Instantaneous Under frequency Trip Time 1 Time 2 Time 3 Time 4 | Wind | [6 empty] | Protection - Wind | sec | Wind | UFREQ_TRIP_TIME1 UFREQ_TRIP_TIME2 UFREQ_TRIP_TIME3 UFREQ_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R | Float | B | Planning Team
Instantaneous Under frequency Trip - Under frequency 1 Under frequency 2 Under frequency 3 Under frequency 4 | Wind | [6 empty] | Protection - Wind | Hz | Wind | UFREQ_TRIP_HZ1 UFREQ_TRIP_HZ2 UFREQ_TRIP_HZ3 UFREQ_TRIP_HZ4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR . Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Under frequency 1 is required, Under frequency 2,3,4 are optional 5)Frequency settings should exist if time settings are defined – Plant Frequency Protection tab | R | Float | B | Planning Team
Instantaneous Over frequency Trip | Wind | [6 empty] | Protection - Wind | Hz | Wind | OFREQ_TRIP_INSTANT |  | 1) This field is OPTIONAL 2) Data type must be Float | O | Float | B | Planning Team
Instantaneous Over frequency Trip Time 1 Time 2 Time 3 Time 4 | Wind | [6 empty] | Protection - Wind | sec | Wind | OFREQ_TRIP_TIME1 OFREQ_TRIP_TIME2 OFREQ_TRIP_TIME3 OFREQ_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R | Float | B | Planning Team
Instantaneous Over frequency Trip - Over frequency 1 Over frequency 2 Over frequency 3 Over frequency 4 | Wind | [6 empty] | Protection - Wind | Hz | Wind | OFREQ_TRIP_HZ1 OFREQ_TRIP_HZ2 OFREQ_TRIP_HZ3 OFREQ_TRIP_HZ4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Over frequency 1 is required, Over frequency 2,3,4 are optional 5)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | R | Float | B | Planning Team
Provide Manufacturer's Technical Document / Simulation Results / Test Result, Etc. Describing The Turbine Technology & Vrt Options Purchased With Turbine, If Any | Wind | [6 empty] | Protection - Wind |  | Not in table | Not in table
Do Personnel (onsite Operator/engineer Etc.) Have Control To Enable/disable Or Change The Settings For Voltage Ride-through | Wind | [6 empty] | Protection - Wind |  | Not in table | Not in table |  | Select from the list: Y or N | R | Dropdown List
Does The Resource Use Dynamic Reactive Devices (svc/statcom, Etc.) At The Wind Farm? - (note: Capacitor Banks Used For Conventional Reactive Support Cannot Be Considered As Dynamic Reactive Devices) - If Yes, Please Provide Supporting Documentation. (manufacturer's Technical Document, Pss/e Model Etc.) | Wind | [6 empty] | Protection - Wind |  | Not in table | Not in table |  | 1) This field is required 2) Data type must 'Y' or 'N' 3) Generate an Warning if blank, if 'Y', test results must be attached | C | Dropdown List | B,DVB
Does the Resource Have the Turbine Voltage & Frequency Protection Settings As Per Manufacturer - Technical Document And/or Spec Sheet | Wind | [6 empty] | Protection - Wind |  | Not in table | Not in table |  | 1) This field is required 2) Data type must 'Y' or 'N' 3) Generate an Warning if blank, if 'Y', test results must be attached | C | Dropdown List | B,DVB
Does The Resource Have Plant Voltage Protection? If Yes, Please Provide Supporting Documentation. | Wind | [6 empty] | Protection - Wind |  | Not in table | Not in table |  | Select from the list: Y or N |  | Dropdown List
Does The Resource Have Feeder Voltage Protection? If Yes, Please Provide Supporting Documentation. | Wind | [6 empty] | Protection - Wind |  | Not in table | Not in table |  | Select from the list: Y or N |  | Dropdown List
Collector System - Wind | Wind | 03/13/2012 Updated | [5 empty] | Collector System - Wind |  | Not in table | Not in table
COLLECTION SYSTEM DETAILED MODEL | Wind | 03/13/2012 Updated | [5 empty] | Collector System - Wind |  | Not in table | Not in table
Cable Type | Wind | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System - Wind |  | COLLECTOR_SYS | CABLE_TYPE |  | 1) This field is required 2) Data type must string 3) Generate an Warning if blank | R | String | B,DVB
Voltage Level kV | Wind | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System - Wind | kv | COLLECTOR_SYS | VT_LEVEL_KV |  | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | T | Float | B/DVE
POSITIVE SEQUENCE DATA | Wind | 03/13/2012 Updated | [5 empty] | Collector System - Wind |  | Not in table | Not in table
R/kft | Wind | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System - Wind | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_R_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank | R | Float | B,DVB
X/kft | Wind | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System - Wind | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_X_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank | R | String | B,DVB
Charging Bc/kft | Wind | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System - Wind | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_CHRG_BC_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank | R | Float | B,DVB
Zero Sequence Data | Wind | 03/13/2012 Updated | [5 empty] | Collector System - Wind |  | Not in table | Not in table
R0/kft | Wind | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System - Wind | (p.u. on 100 MVA base) | COLLECTOR_SYS | ZERO_R0_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank | R | Float | B,DVB
X0/kft | Wind | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System - Wind | (p.u. on 100 MVA base) | COLLECTOR_SYS | ZERO_X0_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank | R | Float | B,DVB
Collector System-Wind Seg Data | Wind | 03/13/2012 Updated | [5 empty] | Collector System-Wind Seg Data |  | Not in table | Not in table
Cable Type | Wind | 03/13/2012 Updated | [5 empty] | Collector System-Wind Seg Data |  | Not in table | Not in table
Cable Type | Wind | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System-Wind Seg Data | List | CABLE_SEG_DATA | CABLE_TYPE |  | 1) This field is required 2) Data type must string 3) Generate an Warning if blank | R | String | B,DVB
Wind Segament Detail | Wind | 03/13/2012 Updated | [5 empty] | Collector System-Wind Seg Data |  | Not in table | Not in table
From | Wind | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System-Wind Seg Data | Integer | CABLE_SEG_DATA | CABLE_SEG_DATA_FROM |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank | R | Integer | B,DVB
To | Wind | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System-Wind Seg Data | Integer | CABLE_SEG_DATA | CABLE_SEG_DATA_TO |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank | R | Integer | B,DVB
Circuit Number | Wind | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System-Wind Seg Data | Integer | CABLE_SEG_DATA | CIRCT_NUM |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank | R | Integer | B,DVB
Voltage Level | Wind | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System-Wind Seg Data | kV | CABLE_SEG_DATA | VT_LEVL |  | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0. | T | Float | B/DVE
Cable Segment Length | Wind | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System-Wind Seg Data | in kft | CABLE_SEG_DATA | CABLE_SEG_LENTH |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank | R | Float | B,DVB
Number of Turbines on cable segment | Wind | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System-Wind Seg Data | Integer | CABLE_SEG_DATA | NUM_TURBIN_ON_CABLE_SEG |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank | R | Integer | B,DVB
Line Data | Transmission | [6 empty] | Line Data | Not in table | Not in table | Not in table
Description of Change | Transmission | [6 empty] | Line Data |  | LINE | CHANGE_DESCRIPTION |  | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Alpha | B | Joel Koepke
LINE (any length) Details | Transmission | [6 empty] | Line Data |  | Not in table | Not in table
Line Name | Transmission | [6 empty] | Line Data | enter all caps | LINE | ERCOT_LINE_NAME |  | 1) This field is required 2) This field may not have any special characters, except an underscore "_" and a dash "-" 3) Warn if > 14 characters. Warning! ERCOT Line Name () should not be > 14 characters long or the name will be truncated in the model which requires uniqueness. 4) Line Name can not be duplicated in a Station | T | Alpha | B | Joel Koepke
Line Voltage Level | Transmission | [6 empty] | Line Data | kV | LINE | LINE_VOLT_LVL |  | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value must be < 345 4) The value must be > 1 | T | Float | B/DVE | Joel Koepke
Resistance in P.U. (100 MVA Base) | Transmission | [6 empty] | Line Data | p.u. | LINE | RESISTANCE |  | 1) Field is required If value is < 0.0001 and Internal Line = 'Y' then Warning! Resistance should be less than 0.0001 If value is < 0.0001 and Internal Line = 'N' then Warning! Resistance should be less than 0.0001 3) If Line Data - Line Voltage Level = 69kV, value must be <= 1.5 If Line Data - Line Voltage Level = 138kV or 345kV, value must be <= 0.5 WARN if value is outside of these conditions 4) If the Zero Impedance Lines are contained within a single substation, then they should be removed from the Line tab and the updated connections should be shown in the Breaker/Switch tab. "ERROR! Internal zero impedance lines should be modeled on the breaker/switch tab" If Zero Impedance Lines are between two substations, produce a warning if line ratings are entered as 9999. "ERROR! Invalid MVA Rating between substations" | T | Float | B | Joel Koepke
Reactance in P.U. (100 MVA Base) | Transmission | [6 empty] | Line Data | p.u. | LINE | REACTANCE |  | 1) Field is required If value is < 0.0001 and Internal Line = 'Y' then Warning! Reactance should be less than 0.0001 If value is < 0.0001 and Internal Line = 'N' then Warning! Reactance should be less than 0.0001 If Line Data - Line Voltage Level = 69kV, value must be <=1.0 If Line Data - Line Voltage Level = 138kV, value must be <=0.1 If Line Data - Line Voltage Level = 345kV, value must be <=.05 WARN if value is outside of these conditions 3)Error if Reactance value is > 1. Error! Reactance (value) > 1.0. Reactance should be expressed in terms of per unit (e.g. not percentage). 4) If the Zero Impedance Lines are contained within a single substation, then they should be removed from the Line tab and the updated connections should be shown in the Breaker/Switch tab. "ERROR! Internal zero impedance lines should be modeled on the breaker/switch tab" | T | Float | B | Joel Koepke
Charging Susceptance in PU (100 MVA Base) | Transmission | [6 empty] | Line Data | p.u. | LINE | CHARGING_SUSC |  | 1) Field is required 2) Value must be >= 0 If Line Data - Line Voltage Level = 69kV, value must be >=.00001<=0.3 If Line Data - Line Voltage Level = 138kV, value must be >=.00001<=0.5 If Line Data - Line Voltage Level = 345kV, value must be >=.00001<=2.2. Generate a Warning if Rule fails 3) If the Zero Impedance Lines are contained within a single substation, then they should be removed from the Line tab and the updated connections should be shown in the Breaker/Switch tab. ERROR! Internal zero impedance lines should be modeled on the breaker/switch tab. | T | Float | B | Joel Koepke
Zero Sequence Line Resistance In P.u. (100mva Base) | Transmission | [5 empty] | ADD 04/2012 | Line Data | p.u. | LINE | ZERO_SEQ_LINE_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R
Zero Sequence Line Reactance In P.u. (100mva Base) | Transmission | 03/08/2012 Removed Validation #3 per plaaning group. |  |  |  |  | ADD 04/2012 | Line Data | p.u. | LINE | ZERO_SEQ_LINE_REACTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R
Zero Sequence Charging Susceptance In P.u. (100mva Base) | Transmission | 03/08/2012 Removed Validation #3 per plaaning group. |  |  |  |  | ADD 04/2012 | Line Data | p.u. | LINE | ZERO_ SEQ_ CHRG_ SUSECPTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R
Type (overhead / underground) | Transmission | [6 empty] | Line Data | List | LINE | TYPE |  | 1) Field is required 2) Value must be at from the following list: OVERHEAD, UNDERGROUND, BOTH | T | Alpha | B | Joel Koepke
Segment Length | Transmission | [6 empty] | Line Data | miles | LINE | SEGMENT_LENGTH |  | 1) Field is required 2) Value must > 0 3) Formula on Line Data - Segment Length: The formula to determine the length of a line based on the Reactance (X) and the Charging Susceptance (Chg) is 486 * SQRT(X_pu * Chg_pu). Generate a Warning when Segment length is not within the 25% variation of the calculated value. 4) Update the Warning message to include the text " This is applicable for Overhead lines only" | T | Float | B | Joel Koepke
To Station | Transmission | [6 empty] | Line Data |  | Not in table | Not in table
EROCT STATION TO - Station Code Mnemonic | Transmission | [6 empty] | Line Data | enter all caps | LINE | ERCOT_CODE_TO |  | 1) This field is Optional 2) Warn if left blank 3) This field must match ERCOT records (unless new) .Substation Code invalid message should be warning only if the PUN flag is 'yes'. 4.If the Internal Line Flag is 'Y', then the TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic can be same. If the internal Line Flag is 'N', TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic should be distinct . Error message should be "'Error! TO and FROM Station Code ( ) should not be duplicated if Internal Line Flag = "N". 5) If the internal Line Flag is 'N', ,FROM Station Code Mnemonic cannot be listed as a TO Station Code Mnemonic on any other lines. The Warning would occur on the secondary side (eg: they had DIESEL on the FROM station on the first line, and DIESEL on the TO Station on the second line then the TO station would produce the Warning) or (eg: DIESEL is on the TO station on the 3rd line and DIESEL on the FROM station on the 4th line then the FROM station would produce the Warning). | T | Alpha | B/DVE | Joel Koepke
Internal Line | Transmission | [6 empty] | Line Data | Y/N | LINE | INTERNAL_LINE_TO_FLG |  | 1) This field is required 2) Value must be of the following: 'Y', 'N' | T | Alpha | B
TSP Name | Transmission | [6 empty] | Line Data | List | LINE | TSPNAME_TO |  | 1) This field is conditionally required if TO STATION - Internal Line - 'N' 2) This field must match ERCOT records (drop down in RARF) | T | Alpha | B/DVE | Joel Koepke
Connected Device 1 thru 10 | Transmission | [6 empty] | Line Data | enter all caps | LINE_DEVICES | DEVICE_NAME |  | 1) This field is required 2) May not be >= than 17 characters. Warning! Device Name () should not be > 17 characters long or the name will be truncated in the model which requires uniqueness. 3) May not have duplicates within the TO or FROM Station 4) May not contain special characters except for an underscore "_" and a dash "-" | T | Alpha | B/DVE | Joel Koepke
Bus Number (PTI Bus Number) | Transmission | [6 empty] | Line Data | # | LINE | BUS_NUM_TO |  | 1) This field is optional 2) This field must be between 1 - 99,999 | T | Integer | B/DVE | Joel Koepke
Weather Zone / Weather Station (used for Dynamic Ratings) | Transmission | [6 empty] | Line Data | List | LINE | WEATHERZONE_TO |  | 1) This field is conditionally required if "Line Rating (Static or Dynamic)" = 'DYNAMIC' 2) Value must be from the following list: COAST, EAST, FAR_WEST, NORTH, NORTH_C, SOUTH_C, SOUTHERN, WEST, KABI, KAUS, KBRO, KCRP, KDFW, KGLS, KIAH, KJCT, KLRD, KLFK, KMAF, KMWL, KSJT, KSAT, KTYR, KVCT, KACT, KSPS, KINK, KPRX | T | Alpha | B/DVE | Joel Koepke
From Station | Transmission | [6 empty] | Line Data |  | Not in table | Not in table
ERCOT FROM Station Code Mnemonic | Transmission | [6 empty] | Line Data | enter all caps | LINE | ERCOT_CODE_FROM |  | 1) This field is required 2) Must match ERCOT records (unless new) 3) Value must be <= 8 characters .Warning! Station Code () should not be > 8 characters long or the name will be truncated in the model which requires uniqueness. 4. If the Internal Line Flag is 'Y', then the TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic can be same. If the internal Line Flag is 'N', TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic should be distinct. Error message should be "'Error! TO and FROM Station Code ( ) should not be duplicated if Internal Line Flag = "N". 5) If the internal Line Flag is 'N', ,FROM Station Code Mnemonic cannot be listed as a TO Station Code Mnemonic on any other lines. The Warning would occur on the secondary side (eg: they had DIESEL on the FROM station on the first line, and DIESEL on the TO Station on the second line then the TO station would produce the Warning) or (eg: DIESEL is on the TO station on the 3rd line and DIESEL on the FROM station on the 4th line then the FROM station would produce the Warning). | T | Alpha | B/DVE
Connected Device 1 thru 10 | Transmission | [6 empty] | Line Data | enter all caps | LINE_DEVICES | DEVICE_NAME |  | 1) This field is required 2) May not have duplicates within the TO or FROM Station 3) May not contain special characters except for an underscore "_" and a dash "-" 4) May not be > than 17 characters. Warning! Device Name () should not be > 17 characters long or the name will be truncated in the model which requires uniqueness. | T | Alpha | B/DVE | Joel Koepke
Bus Number (PTI Bus Number) | Transmission | [6 empty] | Line Data | (integer) | LINE | BUSNUMBR_FROM |  | 1) This field is optional 2) This field must be between 1 - 99,999 3) Warn if left blank | T | Integer | B/DVE | Joel Koepke
Weather Zone / Weather Station (used for Dynamic Ratings) | Transmission | [6 empty] | Line Data | # | LINE | WEATHERZONE_FROM |  | 1) This field is conditionally required if "Line Rating (Static or Dynamic)" = 'DYNAMIC' 2) Value must be from the following list: COAST, EAST, FAR_WEST, NORTH, NORTH_C, SOUTH_C, SOUTHERN, WEST, KABI, KAUS, KBRO, KCRP, KDFW, KGLS, KIAH, KJCT, KLRD, KLFK, KMAF, KMWL, KSJT, KSAT, KTYR, KVCT, KACT, KSPS, KINK, KPRX | T | Alpha | B/DVE | Joel Koepke
Line Code | Transmission | [5 empty] | ADD 02/2012 | Line Data | List | LINE | LINE_CODE |  | Concantenate (Site Code_Substation Code_ERCOT_LINE_NAME) | R
Comments | Transmission | [6 empty] | Line Data |  | LINE | COMMENTS_LINE
Date Effective | Transmission | [6 empty] | Line Data | mm/dd/yyyy | LINE | EFF_DATE |  | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T | Date | B/DVB | Scott/Woody/Angie
Line Temperture | Transmission | [6 empty] | Line Temperture |  | Not in table | Not in table
Line Name | Transmission | [5 empty] | ADD 02/2012 | Line Temperture | Automatic | LINE_TEMP | ERCOT_LINE_NAME |  | 1) This field is required 2) This field may not have any special characters, except an underscore "_" and a dash "-" 3) Warn if > 14 characters. Warning! ERCOT Line Name () should not be > 14 characters long or the name will be truncated in the model which requires uniqueness. 4) Line Name can not be duplicated in a Station
Line Code | Transmission | [5 empty] | ADD 02/2012 | Line Temperture | Automatic | LINE_TEMP | LINE_CODE |  | Concantenate (Site Code_Substation Code_ERCOT_LINE_NAME)
Line Rating | Transmission | [5 empty] | ADD 02/2012 | Line Temperture | (Static or Dynamic) | LINE_TEMP | LINE_RATING |  | 1) Field is required 2) Field must be from the following list: STATIC, DYNAMIC | T | Alpha | B | Joel Koepke
Nominal | Transmission | [6 empty] | Line Temperture |  | Not in table | Not in table
Nominal (Static and Dynamic) - Continuous Rating | Transmission | [6 empty] | Line Data | MVA | LINE | CONTINUOUS_RTG |  | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be <= Nominal (Static) - 2-hr Emergency Rating 3) Value must be <= Nominal (Static) - 15-min Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - Continuous Rating AND value must be >= 115 °F Continuous Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Integer | B/DVE | Joel Koepke
Nominal (Static and Dynamic) - 2-hr Emergency Rating | Transmission | [6 empty] | Line Data | MVA | LINE | EMGCY_RTG_2HR |  | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be >= Nominal (Static) - Continuous Rating 3) Value must be <= Nominal (Static) - 15-min Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 2-hr Emergency Rating AND value must be >= 115 °F 2-hr Emergency Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Integer | B/DVE | Joel Koepke
Nominal (Static and Dynamic) - 15-min Rating | Transmission | [6 empty] | Line Data | MVA | LINE | RTG_15MIN |  | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be >= Nominal (Static) - Continuous Rating 3) Value must be >= Nominal (Static) - 2-hr Emergency Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 15-min Rating AND value must be >= 115 °F 15-min Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Integer | B/DVE | Joel Koepke
Line Temperture | Transmission | [6 empty] | Line Temperture |  | LINE_TEMP | LINE_TEMP |  | Degree of Temperature
20 °F - Continuous Rating - 115 °F Continuous Rating | Transmission | [6 empty] | Line Temperture | MVA | LINE_TEMP | CONTINUOUS_RTG |  | 1) These field are conditionally required. If Line Rating (Static or Dynamic) = Dynamic this field is required 2) Line Rating (Static or Dynamic) = Static, this field must be blank 3) If required, these values must be <= the subsequent dynamic rating. For example: 20 °F - Continuous Rating >= 25 °F - Continuous Rating 25 °F - Continuous Rating >= 30 °F - Continuous Rating 4) If required, within each temp rating, the following must apply Continuous Rating <= 2-hr Emergency Rating <= 15-min rating | T | Integer | B/DVE | Joel Koepke
20 °F - 2-hr Emergency Rating - 115 °F 2-hr Emergency Rating | Transmission | [6 empty] | Line Temperture | MVA | LINE_TEMP | EMGCY_RTG_2HR |  | 1) These field are conditionally required. If Line Rating (Static or Dynamic) = Dynamic this field is required 2) Line Rating (Static or Dynamic) = Static, this field must be blank 3) If required, these values must be >= the subsequent dynamic rating. For example: 20 °F - 2-hr Emergency Rating >= 25 °F - 2-hr Emergency Rating 25 °F - 2-hr Emergency Rating >= 30 °F - 2-hr Emergency Rating 4) If required, within each temp rating, the following must apply Continuous Rating <= 2-hr Emergency Rating <= 15-min rating | T | Integer | B/DVE | Joel Koepke
20 °F - 15-min Rating - 115 °F 15-min Rating | Transmission | [6 empty] | Line Temperture | MVA | LINE_TEMP | RTG_15MIN |  | 1) These field are conditionally required. If Line Rating (Static or Dynamic) = Dynamic this field is required 2) Line Rating (Static or Dynamic) = Static, this field must be blank 3) If required, these values must be >= the subsequent dynamic rating. For example: 20 °F - 2-hr 15-min Rating >= 25 °F - 15-min Rating 25 °F - 2-hr 15-min Rating >= 30 °F - 15-min Rating 4) If required, within each temp rating, the following must apply Continuous Rating <= 2-hr Emergency Rating <= 15-min rating | T | Integer | B/DVE | Joel Koepke
Planning Rate C | Transmission | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Line Temperture | MVA | LINE_TEMP | PLANNING_RATE_C |  | This field is required Numeric value Must be >= Emergency Rating (2HR Rating) | R | Float |  | Model Adminstration
Breaker Swirch Data | Transmission | [6 empty] | Breaker Switch Data |  | Not in table | Not in table
Description of Change | Transmission | [6 empty] | Breaker Switch Data | List | BREAKER_SWITCH | CHANGE_DESCRIPTION | CHANGE_DESCRIPTION | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Alpha | B | Joel Koepke
Breaker/Switch | Transmission | [6 empty] | Breaker Switch Data |  | Not in table | Not in table
Switch Name | Transmission | [6 empty] | Breaker Switch Data | enter all caps | BREAKER_SWITCH | SWITCH_NAME |  | 1) This field is required 2) Value may contain no special characters except an underscore "_" and a dash "-" 3) Must be <=14 characters. Warning! Switch Name () should not be >14 characters long or the name will be truncated in the model which requires uniqueness. 4) Switch Name can not be duplicated in a station | T | Alpha | B | Joel Koepke
ERCOT Station Code Mnemonic | Transmission | [6 empty] | Breaker Switch Data | enter all caps | BREAKER_SWITCH | SUBSTATION_CODE | SWITCH_NAME | 1) This field is required 2) Must match ERCOT records (unless new). Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters. Warning! Station Code () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) substation code should be in Upper case letters. Generate an error if the rule fails | T | Alpha | B | Joel Koepke
Switch Code | Transmission | [5 empty] | UPDATE 02/2012 | Breaker Switch Data | Automatic | BREAKER_SWITCH | BREAKER_CODE | SUBSTATION_CODE | Concantenate (Site Code_Substation Code_Switch Name)
Is this a Fault Isolating Device (e.g. Circuit Breaker) | Transmission | [6 empty] | Breaker Switch Data | Y/N | BREAKER_SWITCH | FAULT_ISO_DEV_FLG | FAULT_ISO_DEV_FLG | 1) This is a required field 2) Values must from the following list: 'Y', 'N' | T | Alpha | B | Joel Koepke
Normal Operating Status (when in-service) | Transmission | [6 empty] | Breaker Switch Data | Oper/Closed | BREAKER_SWITCH | NORM_OP_STATUS | NORM_OP_STATUS | 1) This field is required 2) Value must be from the following list: 'OPEN', 'CLOSED' 3) Generate a warning when the Normal Operating Status is 'OPEN' | T | Alpha | B | Joel Koepke
Voltage Level | Transmission | [6 empty] | Breaker Switch Data | kV | BREAKER_SWITCH | VOLT_LVL | VOLT_LVL | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | T | Float | B/DVE | Joel Koepke
Static Ratings for Planning | Transmission | [6 empty] | Breaker Switch Data |  | Not in table | Not in table
Continuous Ratings | Transmission | [5 empty] | ADD 04/2012 | Breaker Switch Data | MVA | BREAKER_SWITCH | CONTINUOUS_RTG |  | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be <= Nominal (Static) - 2-hr Emergency Rating 3) Value must be <= Nominal (Static) - 15-min Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - Continuous Rating AND value must be >= 115 °F Continuous Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Integer | B/DVE | Model Adminstration
2HR Rating Emergency Rating | Transmission | [5 empty] | ADD 04/2012 | Breaker Switch Data | MVA | BREAKER_SWITCH | EMGCY_RTG_2HR |  | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be >= Nominal (Static) - Continuous Rating 3) Value must be <= Nominal (Static) - 15-min Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 2-hr Emergency Rating AND value must be >= 115 °F 2-hr Emergency Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Integer | B/DVE | Model Adminstration
15 Min Rating | Transmission | [5 empty] | ADD 04/2012 | Breaker Switch Data | MVA | BREAKER_SWITCH | RTG_15MIN |  | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be >= Nominal (Static) - Continuous Rating 3) Value must be >= Nominal (Static) - 2-hr Emergency Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 15-min Rating AND value must be >= 115 °F 15-min Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Integer | B/DVE | Model Adminstration
Side 1 / Side 2 - Directly connected device name(s) | Transmission | [6 empty] | Breaker Switch Data | enter all caps | BREAKER_SWITCH_SIDE | DEVICE_NAME |  | 1) This field is required 2) Value may contain no special characters except an underscore "_" and a dash "-" 3) Must be <=17 characters. Must be <=17 characters. Warning! Device Names () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. 4) At least one connected device is required on each side of the Breaker/Switch. Generate an error if at least one connected device is missing on both sides Generate a Warning when at least one connected device is missing on any one side. | T | Alpha | B | Joel Koepke
Comments | Transmission | [8 empty] | BREAKER_SWITCH | COMMENTS_BRKSWITCH
Date Effective | Transmission | [7 empty] | mm/dd/yyyy | BREAKER_SWITCH | EFF_DATE |  | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T | Date | Scott/Woody/Angie
Capacitor or Reactor Data | Transmission | [6 empty] | Capacitor and Reactor Data |  | Not in table | Not in table
Description of Change | Transmission | [6 empty] | Capacitor and Reactor Data | List | CAPREACT | CHANGE_DESCRIPTION |  | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Alpha | B | Joel Koepke
Capacitor or Reactor | Transmission | [6 empty] | Capacitor and Reactor Data |  | Not in table | Not in table |  | 1) This field is required 2) Value must be from the following list: 'C', 'R' | T | Alpha | B | Joel Koepke
Device Name | Transmission | [6 empty] | Capacitor and Reactor Data | enter all caps | CAPREACT | DEVICE_NAME |  | 1) This field is required 2) Value may contain no special characters except an underscore "_" and a dash "-" 3) Must be <=14 characters. Warning! Device Name () should not be >14 characters long or the name will be truncated in the model which requires uniqueness. 4) Device Name can not be duplicated in a Station | T | Alpha | B | Joel Koepke
ERCOT Station Code Mnemonic | Transmission | [5 empty] | UPDATE 02/2012 | Capacitor and Reactor Data | enter all caps | CAPREACT | SUBSTATION_CODE |  | 1) This field is required 2) Must match ERCOT records (unless new).Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3)This field may not have any special characters, except an underscore "_" and a dash "-" 4) Value must be <= 8 characters. Warning! Station Code () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) substation code should be in Upper case letters. Generate an error if the rule fails | T | Alpha | B | Joel Koepke
Device Code | Transmission | [5 empty] | UPDATE 02/2012 | Capacitor and Reactor Data | Automatic | CAPREACT | DEVICE_CODE |  | Concantenate (Site Code_Substation Code_Device Code)
Capacitor or Reactor | Transmission | [6 empty] | Capacitor and Reactor Data | List | CAPREACT | CAPACITOR_REACTOR_FLG |  | 1) This field is required 2) Value must be from the following list: 'C', 'R' | T | Alpha | B | Joel Koepke
Nominal MVAR | Transmission | [6 empty] | Capacitor and Reactor Data | MVAR | CAPREACT | NOMINAL_MVAR |  | 1) This field is required 2) If the Capacitor or Reactor field is 'C' , the value should be > 0 , if it is 'R', value should be < 0 | T | Float | B | Joel Koepke
Voltage Level kV | Transmission | [6 empty] | Capacitor and Reactor Data | kV | CAPREACT | VOLT_LVL_KV |  | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | T | Float | B/DVE | Joel Koepke
Bus Number (PTI Bus Number) | Transmission | [6 empty] | Capacitor and Reactor Data | # | CAPREACT | PTI_BUSNUM |  | 1) This field is optional 2) This field must be between 1 - 99,999 | T | Float | B | Joel Koepke
Automatic Voltage Regulation | Transmission | [6 empty] | Capacitor and Reactor Data | Y/N | CAPREACT | AUTO_VOLT_FLG |  | 1) This field is required 2) Value must be from the following list: 'Y', 'N' | T | Alpha | B | Joel Koepke
Voltage Level of Bus bar being regulated | Transmission | [6 empty] | Capacitor and Reactor Data | kV | CAPREACT | BUSBAR_VOLT |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | T | Float | B/DVE | Joel Koepke
Desired Regulating voltage | Transmission | [6 empty] | Capacitor and Reactor Data | kV | CAPREACT | DES_REG_VOLT |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) The value may not exceed 345. (REMOVED) 3) The value must be > 0 4) The value must >= Minimum Regulating Voltage 5) The value must <=Maximum Regulating Voltage 6) Value should be within the range of 10% of the base kV..anything beyond should be a Warning. | T | Float | B/DVE | Joel Koepke
Minimum Regulating Voltage | Transmission | [6 empty] | Capacitor and Reactor Data | kv | CAPREACT | MIN_REG_VOLT |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) The value may not exceed 345(REMOVED) 3) The value must be > 0 4) The value must be <= Maximum Regulating Voltage 5) Warning if value exceeds 50% from Maximum Regulating Voltage 6) Value should be within the range of 10% of the base kV..anything beyond should be a Warning. | T | Float | B/DVE | Joel Koepke
Maximum Regulating Voltage | Transmission | [6 empty] | Capacitor and Reactor Data | kv | CAPREACT | MAX_REG_VOLT |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 3) The value must be > 0 4) The value must be >= Minimum Regulating Voltage 5) Warning if value exceeds 50% from Minimum Regulating Voltage 6) Value should be within the range of 10% of the base kV..anything beyond should be a Warning. | T | Float | B/DVE | Joel Koepke
Zero Sequence Reactance Increment In P.u. | Transmission | 03/08/2012 Removed Validation #3 per plaaning group. |  |  |  |  | ADD 04/2012 | Capacitor and Reactor Data | p.u. | CAPREACT | ZERO_SEQ_REACTANCE_INCRMENT_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Model Adminstration
Device Name(s) - that this reactive device is directly connected to | Transmission | [6 empty] | Capacitor and Reactor Data | enter all caps | CAPREACT_DEVICE | CONNECTED_DEVICE_NAME |  | 1) This field is optional 2) May not contain special characters except for an underscore "_" and a dash "-" 3) ) May not be > than 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. 4)This field should be unique. Every Device entry needs to have a unique “Device Name(s) – that this reactive device is directly connected to". No two capacitors should have the same controlling breaker or switch. 5) 'Connected Device in Capacitor Reactor should have a Controlling Breaker/Switch in Breaker/switch Tab. Audit report should generate an error if the rule fails. For all other equipment that is not a Capacitor/Reactor, they can have connectivity references to transformers, lines, etc. However, for the Capacitor/Reactors, the EMS needs to have a controlling switch modeled, else they would always be "On | T | Alpha | B/DVE | Joel Koepke
Comments | Transmission | [8 empty] | CAPREACT | COMMENTS_CAPREACT
Date Effective | Transmission | [7 empty] | mm/dd/yyyy | CAPREACT | EFF_DATE |  | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T | Date | B/DVB | Scott/Woody/Angie
Static Var Compensator Data | Transmission | [6 empty] | Static Var Compensator Data |  | Not in table | Not in table
Description of Change | Transmission | [6 empty] | Static Var Compensator Data |  | STATIC_VAR_COMP | CHANGE_DESCRIPTION |  | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Alpha | B | Joel Koepke
Static Var Compensator | Transmission | [6 empty] | Static Var Compensator Data |  | Not in table | Not in table
SVC Name | Transmission | [6 empty] | Static Var Compensator Data | enter all caps | STATIC_VAR_COMP | SVC_NAME |  | 1) This field is required 2) May not be > than 14 characters..Warning! SVC Name () should not be >14 characters long or the name will be truncated in the model which requires uniqueness. 3) May not contain special characters except for an underscore "_" and a dash "-" 4) Device Name can not be duplicated in a Station | T | Alpha | B | Joel Koepke
ERCOT Station Name (Station Code or Station Mnemonic) | Transmission | [6 empty] | Static Var Compensator Data | enter all caps | STATIC_VAR_COMP | SUBSTATION_CODE |  | 1) This field is required 2) Must match ERCOT records (unless new).Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) Must be <= 8 characters. Warning! Station Name () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. | T | Alpha | B/DVE | Joel Koepke
SVC CODE | Transmission | [5 empty] | UPDATE 02/2012 | Static Var Compensator Data | Automatic | STATIC_VAR_COMP | SVC_CODE |  | Concantenate (Site Code_Substation Code_SVC Name)
SVC Base Voltage Level | Transmission | [6 empty] | Static Var Compensator Data | kV | STATIC_VAR_COMP | SVC_BASE_VOLT |  | 1) This field is required 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | T | Float | B/DVE | Joel Koepke
Fixed MVAR (VAR injection at nominal voltage) | Transmission | [5 empty] | UPDATE 02/2012 | Static Var Compensator Data | MVAR | STATIC_VAR_COMP | FIXED_MVAR |  | 1) This field is required | T | Float | B/DVE | Joel Koepke/Planning 11/08/11
Minimum Admittance Limits (100 MVA Base) | Transmission | [5 empty] | UPDATE 02/2012 | Static Var Compensator Data | p.u. | STATIC_VAR_COMP | MIN_ADM_LIMIT |  | 1) This field is required 2) Value must be <= Maximum Admittance | T | Float | B/DVE | Joel Koepke/Planning 11/08/11
Maximum Admittance Limits (100 MVA Base) | Transmission | [5 empty] | UPDATE 02/2012 | Static Var Compensator Data | p.u. | STATIC_VAR_COMP | MAX_ADM_LIMIT |  | 1) This field is required 2) Value must be >= Minimum Admittance | T | Float | B/DVE | Joel Koepke/Planning 11/08/11
Minimum Steady State Reactive Power Limits | Transmission | [6 empty] | Static Var Compensator Data | MVAR | STATIC_VAR_COMP | MIN_STD_STATE_REACT |  | 1) This field is required 2) Value must be >= Maximum Steady State Reactive Power Limits | T | Float | B/DVE | Joel Koepke
Maximum Steady State Reactive Power Limits | Transmission | [6 empty] | Static Var Compensator Data | MVAR | STATIC_VAR_COMP | MAX_STD_STATE_REACT |  | 1) This field is required 2) Value must be >= Minimum Steady State Reactive Power Limits | T | Float | B/DVE | Joel Koepke
Minimum Threshold (post contingency) Reactive Power Limits | Transmission | [6 empty] | Static Var Compensator Data | MVAR | STATIC_VAR_COMP | MIN_THRESH_REACT |  | 1) This field is required 2) Value must be <= Maximum Threshold (post contingency) Reactive Power Limits | T | Float | B/DVE | Joel Koepke
Maximum Threshold (post contingency) Reactive Power Limits | Transmission | [5 empty] | UPDATE 02/2012 | Static Var Compensator Data | MVAR | STATIC_VAR_COMP | MAX_THRESH_REACT |  | 1) This field is required 2) Value must be <= Maximum Steady State Reactive Power Limits | T | Float | B/DVE | Joel Koepke/Planning 11/08/11
Minimum Voltage Threshold | Transmission | [5 empty] | UPDATE 02/2012 | Static Var Compensator Data | kV | STATIC_VAR_COMP | MIN_VOLT_THRESH |  | 1) This field is required 2) Value must be <= Maximum Voltage Threshold (100 MVA Base) 3) The value may not exceed 370 3) The value must be > 0 4) Warn if Max / Min exceed 50% of one another | T | Float | B/DVE | Joel Koepke/Planning 11/08/11
Maximum Voltage Threshold | Transmission | [5 empty] | UPDATE 02/2012 | Static Var Compensator Data | kV | STATIC_VAR_COMP | MAX_VOLT_THRESH |  | 1) This field is required 2) Value must be >= Minimum Voltage Threshold (100 MVA Base) 3) The value may not exceed 370 4) The value must be > 0 5) Warn if Max / Min exceed 50% of one another | T | Float | B/DVE | Joel Koepke/Planning 11/08/11
Device Name(s) - that this reactive device is directly connected to | Transmission | [6 empty] | Static Var Compensator Data | enter all caps | STATIC_VAR_COMP_DEVICES | SWITCH_DEVICE_NAME |  | 1) This field is optional 2) May not contain special characters except for an underscore "_" and a dash "-" 3) May not be > than 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. | T | Alpha | B | Joel Koepke
Comments | Transmission | [6 empty] | Static Var Compensator Data |  | STATIC_VAR_COMP | COMMENTS_STATIC VAR_COMP
Date Effective | Transmission | [6 empty] | Static Var Compensator Data | mm/dd/yyyy | STATIC_VAR_COMP | EFF_DATE |  | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T | Date | B/DVB | Scott/Woody/Angie
Series Device Data | Transmission | [6 empty] | Load Data |  | Not in table | Not in table
Description of Change | Transmission | [6 empty] | Series Device Data | List | SERIES_DEVICE_DATA | CHANGE_DESCRIPTION |  | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Alpha | B | Joel Koepke
Series Device Data | Transmission | [6 empty] | Series Device Data |  | Not in table | Not in table
Series Device Name | Transmission | [6 empty] | Series Device Data | enter all caps | SERIES_DEVICE_DATA | SD_NAME |  | 1) This field is required 2) No special characters except and underscore 3) Warn if >= 14 characters. First 14 characters must be unique. Warning! Series Device Name() should not be >= 14 characters long or the name will be truncated in the model which requires uniqueness. 4) Device Name can not be duplicated in a Station | T | Alpha | B | Joel Koepke
ERCOT Station Name (Station Code or Station Mnemonic) | Transmission | [6 empty] | Series Device Data | enter all caps | SERIES_DEVICE_DATA | SUBSTATION_CODE |  | 1) This field is required 2) Must match ERCOT records (unless new).Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters. Warning! Station Code () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. | T | Alpha | B | Joel Koepke
SD CODE | Transmission | [5 empty] | UPDATE 02/2012 | Series Device Data | Automatic |  |  |  | Concantenate (Site Code_Substation Code_SD Name)
Voltage Level | Transmission | [6 empty] | Series Device Data | kV | SERIES_DEVICE_DATA | VOLATGE |  | 1) This field is required 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | T | Float | B/DVE | Joel Koepke
Resistance | Transmission | [6 empty] | Series Device Data | p.u. | SERIES_DEVICE_DATA | RESISTANCE |  | 1) This value is required 2) Value must be > 0 | T | Float | B | Joel Koepke
Reactance | Transmission | [6 empty] | Series Device Data | p.u. | SERIES_DEVICE_DATA | REACTANCE |  | 1) This value is required 2) Value may be negative. Allow negative Reactance (to represent Series Capacitors) 3)Error if Reactance value is > 1. Error! Reactance (value) > 1.0. Reactance should be expressed in terms of per unit (e.g. not percentage). | T | Float | B | Joel Koepke
Continuous Rating | Transmission | [6 empty] | Series Device Data | MVA | SERIES_DEVICE_DATA | CONTINUOUS_RTG |  | 1) This field is required 2) Value must be <= 2-hr Emergency Rating 3) Value must be <= 15-min Rating | T | Float | B/DVE | Joel Koepke
2-hr Emergency Rating | Transmission | [6 empty] | Series Device Data | MVA | SERIES_DEVICE_DATA | EMGCY_RTG_2HR |  | 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be <=15-min Rating | T | Float | B/DVE | Joel Koepke
15-min Rating | Transmission | [6 empty] | Series Device Data | MVA | SERIES_DEVICE_DATA | RTG_15MIN |  | 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be >= 2-hr Emergency Rating | T | Float | B/DVE | Joel Koepke
Side 1 | Transmission | [6 empty] | Series Device Data |  | Not in table | Not in table
Side 1 - Connected Switching Device Name(s) | Transmission | [6 empty] | Series Device Data | enter all caps | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME |  | 1) This field is required 2) May not have duplicates within the TO or FROM Station. Warning Only 3) May not contain special characters except for an underscore "_" and a dash "-" 4) May not be > than 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. | T | Alpha | B | Joel Koepke
Side 1 - Bus Number (PTI Bus Number) | Transmission | [6 empty] | Series Device Data | # | SERIES_DEVICE_DATA | SIDE1_PTI_BUS_NUM |  | 1) This field is optional 2) This field must be between 1 - 99,999 | T | Integer | B/DVE | Joel Koepke
Side 2 | Transmission | [6 empty] | Series Device Data |  | Not in table | Not in table
Side 2 - Connected Switching Device Name(s) | Transmission | [6 empty] | Series Device Data | enter all caps | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME |  | 1) This field is required 2) May not have duplicates within the TO or FROM Station 3) May not contain special characters except for an underscore "_" and a dash "-" 4) May not be > than 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. | T | Alpha | B | Joel Koepke
Side 2 - Bus Number (PTI Bus Number) | Transmission | [6 empty] | Series Device Data | # | SERIES_DEVICE_DATA | SIDE2_PTI_BUS_NUM |  | 1) This field is optional 2) This field must be between 1 - 99,999 | T | Integer | B/DVE | Joel Koepke
Comments | Transmission | [6 empty] | Series Device Data |  | SERIES_DEVICE_DATA | SD_COMMENTS
Date Effective | Transmission | [6 empty] | Series Device Data |  | SERIES_DEVICE_DATA | EFF_DATE |  | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T | Date | B/DVB | Scott/Woody/Angie
Transformer Data | Transmission | [6 empty] | Transformer Data |  | Not in table | Not in table
Description of Change | Transmission | [6 empty] | Transformer Data | List | TRANSFORMER | CHANGE_DESCRIPTION |  | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Alpha | B | Joel Koepke
TRANSFORMER DETAILS | Transmission | [6 empty] | Transformer Data |  | Not in table | Not in table
Transformer Name | Transmission | [6 empty] | Transformer Data | enter all caps | TRANSFORMER | TRANSFORMER_NAME |  | 1) This field is required 2) May not contain special characters except for an underscore "_" and a dash "-" 3) Warn if >= 14 characters. First 14 characters must be unique. Warning! Transformer Name () should not be >14 characters long or the name will be truncated in the model which requires uniqueness. 4) l Device name must be unique for each Device code for a substation in a SITE | T | Alpha | B | Joel Koepke
ERCOT Station Name (Station Code or Station Mnemonic) | Transmission | [6 empty] | Transformer Data | enter all caps | TRANSFORMER | SUBSTATION_CODE |  | 1) This field is required 2) Must match ERCOT records. Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters. Warning! Station Name () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) substation code should be in Upper case letters. Generate an error if the rule fails | T | Alpha | B | Joel Koepke
Transformer Code | Transmission | [5 empty] | UPDATE 02/2012 | Transformer Data | Automatic | TRANSFORMER | TRANSFORMER_CODE |  | Concantenate (Site Code_Substation Code_Transformer Name)
Transformer Test Report Attached? | Transmission | [6 empty] | Transformer Data | Y/N | Not in table | Not in table |  | Select from the list: Y or N | R | Dropdown List |  | Model Adminstration
Is this transformer in Master / Follower of Current Balancing configuration? | Transmission | [6 empty] | Transformer Data | Y/N | TRANSFORMER | MASTER_FOLLOW_FLG |  | 1) This field is required 2) Value must be in the following list: 'Y', 'N' | T | Alpha | B
Master Name (can be same as this transformer) | Transmission | [6 empty] | Transformer Data | enter all caps | TRANSFORMER | MASTER_NAME |  | 1) This field is conditionally required if Transformer Data - Is this transformer in Master / Follower of Current Balancing configuration? = 'Y' 2) Warn if >= 14 characters. First 14 characters must be unique. Warning! Master Name () should not be >=14 characters long or the name will be truncated in the model which requires uniqueness. 3) May not contain special characters except for an underscore "_" and a dash "-" 4) Either the Master Name or the Follower Name MUST = Transformer Data - Transformer Name | T | Alpha | B/DVE
Follower Name (can be same as this transformer) | Transmission | [6 empty] | Transformer Data | enter all caps | TRANSFORMER | FOLLOWER_NAME |  | 1) This field is conditionally required if Transformer Data - Is this transformer in Master / Follower of Current Balancing configuration? = 'Y' 2) May not contain special characters except for an underscore "_" and a dash "-" 3) Either the Master Name or the Follower Name MUST = Transformer Data - Transformer Name 4) Warn if >= 14 characters. First 14 characters must be unique. Warning! Follower Name () should not be >=14 characters long or the name will be truncated in the model which requires uniqueness. | T | Alpha | B/DVE
Generation Step-Up Transformer? | Transmission | [6 empty] | Transformer Data | Y/N | TRANSFORMER | GSU_TRANSFORMER_FLG |  | 1) This field is required 2) Value must be in the following list: 'Y', 'N' | T | Alpha | B | Joel Koepke
Zero Sequence Data - Winding Connection Code (1-8) | Transmission | [5 empty] | ADD 04/2012 | Transformer Data | p.u. | TRANSFORMER | ZERO_SEQ_DATA_WINDING_CON_CODE |  | 1) This field is optional 2) Data type must be string | R | real | B,DVB | Model Adminstration
Zero Sequence Grounding Resistance For An Impedance Grounded Transformer In P.u. (100 Mva Base) | Transmission | [5 empty] | ADD 04/2012 | Transformer Data | p.u. | TRANSFORMER | ZERO_SEQ_GRUND_RESISTANCE_IMPEDANCE_GRUND_TRANS_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Model Adminstration
Zero Sequence Grounding Reactance For An Impedance Grounded Transformer In P.u. (100 Mva Base) | Transmission | [5 empty] | ADD 04/2012 | Transformer Data | p.u. | TRANSFORMER | ZERO_SEQ_GRUND_REACTANCE_IMPEDANCE_GRUND_TRANS_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Model Adminstration
Zero Sequence Resistance In P.u. (100 Mva Base) | Transmission | [5 empty] | ADD 04/2012 | Transformer Data | p.u. | TRANSFORMER | ZERO_SEQ_TRANS_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Model Adminstration
Zero Sequence Reactance In P.u. (100 Mva Base) | Transmission | [5 empty] | ADD 04/2012 | Transformer Data | p.u. | TRANSFORMER | ZERO_SEQ_TRANS_REACTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Model Adminstration
Positive Sequence Resistance (100 MVA Base) | Transmission | [5 empty] | UPDATE 02/2012 | Transformer Data | p.u. | TRANSFORMER | SERIES_ RESIST |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Model Adminstration
Positive Sequence Reactance (100 MVA Base) | Transmission | [5 empty] | UPDATE 02/2012 | Transformer Data | p.u. | TRANSFORMER | SERIES_ REACT |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Model Adminstration
Continuous Rating | Transmission | [6 empty] | Transformer Data | MVA | TRANSFORMER | CONTINUOUS_RTG |  | 1) This field is required 2) Value must be <= 2-hr Emergency Rating 3) Value must be <= 15-min Rating 4) Transformer Continuous MVA Rating should be >=HRL or unit will be curtailed down to transformer rating" 5) Continuous must have valid mva rating (eg: will get an ERROR if 9999.00) | T | Integer | B/DVE | Joel Koepke
2-hr Emergency Rating | Transmission | [6 empty] | Transformer Data | MVA | TRANSFORMER | EMGCY_RTG_2HR |  | 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be <= 15-min Rating 4) 2hr-rating must have valid mva rating (9999.00 mva will produce a WARNING) | T | Integer | B/DVE | Joel Koepke
15-min Rating | Transmission | [6 empty] | Transformer Data | MVA | TRANSFORMER | RTG_15MIN |  | 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be >= 2-hr Emergency Rating 4) 15min rating must have valid mva rating(9999.00 mva will produce a WARNING), also if 2hr is 9999.00 then the only valid entry for 15min is 9999.00 or it will give an ERROR. | T | Integer | B/DVE | Joel Koepke
Unit(s) associated with this transformer | Transmission | [6 empty] | Transformer Data | enter all caps | TRANSFORMER_UNITS | TRANSFORMER_UNIT_CODE |  | 1) This field is conditionally required - if Generation Step-up = 'Y', this is required 2) Value(s) must be <=17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. 3) Warn if the unit name is not in the Unit Info - GEN or Unit Info - CC or Unit Info - Wind 4) Generate an ERROR when Non GSU Transformers that have entered associated units. | T | Alpha | B | Joel Koepke
HIGH SIDE VOLTAGE INFORMATION | Transmission | [6 empty] | Transformer Data |  | Not in table | Not in table
High Side Voltage Level (no-load) | Transmission | [6 empty] | Transformer Data | kV | TRANSFORMER | HIGH_NOLOAD |  | 1) This field is required 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 5) The value must be >= Low Voltage Level (no-load) | T | Float | B/DVE | Joel Koepke
High Side Voltage Level (PTI) | Transmission | [6 empty] | Transformer Data | # | TRANSFORMER | HIGH_PTI |  | 1) This field is optional 2) This field must be between 1 - 99,999 | T | Integer | B
High Side Voltage Connection - Wye or Delta | Transmission | [6 empty] | Transformer Data | List | TRANSFORMER | HIGH_CONNECTION |  | 1) This field is required 2) Value must be of the following: 'Wye', 'Delta' | T | Alpha | B
High Side Voltage Connected devices (list on separate lines) | Transmission | [6 empty] | Transformer Data |  | TRANSFORMER_DEVICES | DEVICE_NAME |  | 1) This field is required a) Error: if High Side Voltage >= 60kV and Low Side Voltage >1kV b) Warn: if High Side Voltage < 60kV and Low Side Voltage = 1kV 2) No special characters except an underscore or a dash 3) Warn if >= 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. 4) connected devices listed in transformer tab should exist in the breaker switch tab. Generate an error when the rule fails | T | Alpha | B | Joel Koepke
High Side Manufactured Nominal Voltage | Transmission | [6 empty] | Transformer Data | kV | TRANSFORMER | HIGH_MANU_VOLT |  | 1) This field is required 2) If value > 60kV Accepted if value (using 5%) Deviates < ¦3.45¦ kV from 69 Deviates < ¦6.9¦ kV from 138 Deviates < ¦17.25¦ kV from 345 Warn if value (using >= 5% and <10%) Deviates > = ¦3.45¦ but deviates < ¦6.9¦ from 69 Deviates >= ¦6.9¦ but deviates < 13.8 from 138 Deviates >= ¦17.25¦ but deviates < 34.5 from 345 Error if value (using > =10%) Deviates >= ¦6.9¦ kV from 69 Deviates >= ¦13.8¦kV from 138 Deviates >= ¦34.5¦kV from 345 3) Warn if value > 345 4) The value must be > 0 5) High Side Manufactured Nominal Voltage >= Low Side Manufactured Nominal Voltage 6) High Side Manufactured Nominal Voltage should be > Voltage at Lowest Tap Position and < Voltage at Highest Tap Position 7) Transformer High Side Manufactured Nominal Voltage should equal to Voltage at Highest Tap - Step Size voltage to reach Nominal Tap. | T | Float | B/DVE
LOW SIDE VOLTAGE INFORMATION | Transmission | [6 empty] | Transformer Data |  | Not in table | Not in table
Low Side Voltage Level (no-load) | Transmission | [6 empty] | Transformer Data | kV | TRANSFORMER | LOW_NOLOAD |  | 1) This field is required 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 5) The value must be <= High Voltage Level (no-load) 6) If Generator Step-up Transformer = 'Y' AND Low Side Voltage Level (no-load) > 1kV AND Then the Low Side Voltage Level (no-load) must be equal to Unit Info - GEN / CC / WIND - Unit Generating Voltage | T | Float | B/DVE | Joel Koepke
Low Side Voltage Level (PTI) | Transmission | [6 empty] | Transformer Data | # | TRANSFORMER | LOW_PTI |  | 1) This field is optional 2) This field must be between 1 - 99,999 | T | Integer | B
Low Side Voltage Connection - Wye or Delta | Transmission | [6 empty] | Transformer Data | List | TRANSFORMER | LOW_CONNECTION |  | 1) This field is required 2) Value must be of the following: 'Wye', 'Delta' | T | Alpha | B
Low Side Voltage Connected device(s) (list on separate lines) | Transmission | [6 empty] | Transformer Data |  | TRANSFORMER_DEVICES | DEVICE_NAME |  | 1) This field is required a) Error: if High Side Voltage >= 60kV and Low Side Voltage >1kV b) Warn: if High Side Voltage < 60kV and Low Side Voltage = 1kV 2) Warn if >= 17 characters. 3) No special characters except an underscore "_" or a dash "-" 4) connected devices listed in transformer tab should exist in the breaker switch tab. Generate an error when the rule fails | T | Alpha | B | Joel Koepke
Low Side Manufactured Nominal Voltage | Transmission | [6 empty] | Transformer Data | kV | TRANSFORMER | LOW_MANU_VOLT |  | 1) This field is required 2) If the value >= 69kv: Accepted if value (using 5%) Deviates < ¦3.45¦ kV from 69 Deviates < ¦6.9¦ kV from 138 Deviates < ¦17.25¦ kV from 345 Warn if value (using >= 5% and <10%) Deviates > = ¦3.45¦ but deviates < ¦6.9¦ from 69 Deviates >= ¦6.9¦ but deviates < 13.8 from 138 Deviates >= ¦17.25¦ but deviates < 34.5 from 345 Error if value (using > =10%) Deviates >= ¦6.9¦ kV from 69 Deviates >= ¦13.8¦kV from 138 Deviates >= ¦34.5¦kV from 345 3) Warn if value > 345 4) The value must be > 0 5) High Side Manufactured Nominal Voltage >= Low Side Manufactured Nominal Voltage 6) Low Side Manufactured Nominal Voltage should equal (Voltage at Lowest Tap) + (Step size voltage to reach Nominal tap) | T | Float | B/DVE
Series Resistance (100 MVA Base) | Transmission | [5 empty] | REMOVE/ field being replaced by Zero and Positive Sequance Reactance | Transformer Data |  |  |  |  | 1) This field is required 2) Value must be >=0. Allow negative Resistance only when low side kV is 1kV. 3) Produce an Error if the Transformer Resistance value is less than 3 decimals.(('Error! Resistance (x) may be rounding, it should be accurate to 5th decimal') Produce a Warning if the Transformer Resistance value is greater than 2 decimals and less than 5 decimals('Warning! Resistance(x) may be rounding, it should be accurate to 5th decimal') 4) If “Low kV” <> 1 Then ERROR if R/X > 1 Else “no warning/error” Else if “Low kV” = 1 Then Warning if R/X > 3 Else “no warning/error” (Note: Low KV refers to Low side Voltage Level(no-load)' =1 5) Generates a Warning when R/X ratio is >0.1 | T | Float | B | Joel Koepke
Series Resistance (100 MVA Base) | Transmission | [5 empty] | REMOVE/ field being replaced by Zero and Positive Sequance Resistance | Transformer Data |  |  |  |  | 1) This field is required 2) Error if Reactance value is > 1. Error! Reactance (value) > 1.0. Reactance should be expressed in terms of per unit (e.g. not percentage). Allow negative Reactance only when low side kV is 1kV. 3) Produce an Error if the Transformer Reactance value is less than 3 decimals.(('Error! Reactance (x) may be rounding, it should be accurate to 5th decimal') Produce a Warning if the Transformer Reactance value is greater than 2 decimals and less than 5 decimals('Warning! Reactance(x) may be rounding, it should be accurate to 5th decimal') 4) If “Low kV” <> 1 Then ERROR if R/X > 1 Else “no warning/error” Else if “Low kV” = 1 Then Warning if R/X > 3 Else “no warning/error” (Note: Low KV refers to Low side Voltage Level(no-load)' =1 | T | Float | B | Joel Koepke
Voltage Regulation | Transmission | [6 empty] | Transformer Data |  | Not in table | Not in table
Automatic Voltage Regulation | Transmission | [6 empty] | Transformer Data | Y/N | TRANSFORMER | AUTO_VOLT_REG |  | 1) This field is required 2) Value must be from the following list: 'Y', 'N' 3) AVR is expected to be 'Y' when total number of tap positions >=16. Warn if "Automatic Voltage Regulation" = 'N' and Total Number of Tap Positions>=16 | T | Alpha | B/DVE | Joel Koepke
Does Transformer have a Load Tap Changer? | Transmission | [6 empty] | Transformer Data | Y/N | TRANSFORMER | LOADTAP_CHNGR_FLG |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) Value must be from the following list: 'Y', 'N' 3) Load Tap Changer is expected to be 'Y' when total number of tap positions >=16. Warn if "Load Tap Changer" = 'N' and Total Number of Tap Positions>=16 | T | Alpha | B/DVE | Joel Koepke
Location of Tap Changer High or Low | Transmission | [6 empty] | Transformer Data | List | TRANSFORMER | LOCN_TAP_CHNGR |  | 1) This field is conditionally required if 'Does Transformer have a Load Tap Changer ?' = 'Y' 2) Value must be of the following: 'HIGH', 'LOW' 3) Load Tap Changer should be 'Y' when AVR is 'Y'. Generate an error if Load Tap Changer is 'N' and AVR = 'Y'. | T | Alpha | B/DVE
Base kV of Regulated Side | Transmission | [6 empty] | Transformer Data | kV | TRANSFORMER | REG_KV_BASE |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 5) The value must be >= Low Voltage Level (no-load) | T | Float | B | Joel Koepke
Target kV of Regulated Side | Transmission | [6 empty] | Transformer Data | kV | TRANSFORMER | REG_KV_TARGET |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) Value must be > 0 | T | Float | B | Joel Koepke
Acceptable Deviation of Target Voltage in Percent | Transmission | [6 empty] | Transformer Data | % | TRANSFORMER | ACCEPT_DEV_VOLT_TARGET |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) Value must not exceed 50% | T | Percentage | B | Joel Koepke
Comments | Transmission | [6 empty] | Transformer Data |  | TRANSFORMER | COMMENTS_TRANSFORMER
Date Effective | Transmission | [6 empty] | Transformer Data |  | TRANSFORMER | EFF_DATE |  | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T | Date | B/DVB | Scott/Woody/Angie
Transformer Tap Settings | Transmission | [6 empty] | TRANSFORMER TAP SETTINGS |  | Not in table | Not in table | Not in table
Transformer Code | Transmission | [5 empty] | Added to RARF Form for 02/2012 | Transformer Tap Settings | Automatic | TRANSFORMER_TAP_SETTINGS | TRANSFORMER_CODE |  | Concantenate (Site Code_Substation Code_Transformer Name)
High-Low Flag | Transmission | [5 empty] | Added to RARF Form for 02/2012 | Transformer Tap Settings | List | TRANSFORMER_TAP_SETTINGS | LOW_HIGH_FLG |  | 1) This field is conditioally reguired.This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be of the following: High or Low
TAP SETTINGS - ONLY IF TAP EXISTS | Transmission | [6 empty] | TRANSFORMER TAP SETTINGS |  | Not in table | Not in table
Tap position at Manufactured Nominal Voltage | Transmission | [6 empty] | Transformer Tap Settings | # | TRANSFORMER_TAP_SETTINGS | MANU_VOLT_TAP_POS |  | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field must be left blank if Low Voltage Level = 1 2) Note: this value may be negative 3. Value must be between Lowest and Highest Tap position 4)All tap information is required if it exists on either the LTC or Fixed side. | T | Integer | B
Total Number of Tap Positions | Transmission | [6 empty] | Transformer Tap Settings | # | TRANSFORMER_TAP_SETTINGS | TOTAL_NUM |  | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be >= 2 3) Warn if value >= 16 and "Automatic Voltage Regulation" = 'N' Warn if value >=16 and "Load Tap Changer" = 'N' | T | Integer | B | Joel Koepke
Normal Tap Position | Transmission | [6 empty] | Transformer Tap Settings | # | TRANSFORMER_TAP_SETTINGS | NORMAL_POS |  | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out. Note that it is valid for both, Low and High Tap settings to be filled out. Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be >= Low Tap Settings - Lowest Tap Position 3) Value must be <= Low Tap Settings - Highest Tap Position 4) Note: this value may be negative | T | Integer | B | Joel Koepke
Lowest Tap Position | Transmission | [6 empty] | Transformer Tap Settings | # | TRANSFORMER_TAP_SETTINGS | LOWEST_POS |  | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be <= Low Tap Settings - Highest Tap Position 3) Note: this value may be negative | T | Integer | B | Joel Koepke
Voltage at Lowest Tap Position | Transmission | [6 empty] | Transformer Tap Settings | kV | TRANSFORMER_TAP_SETTINGS | LOWEST_VOLT |  | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be <= Low Tap Settings - Voltage at Highest Tap Position 3) Value must be < High Tap Settings - Voltage at Lowest Tap Position 4) Value must be >= 0 | T | Float | B | Joel Koepke
Highest Tap Position | Transmission | [6 empty] | Transformer Tap Settings | # | TRANSFORMER_TAP_SETTINGS | HIGHEST_POS |  | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out. Note that it is valid for both, Low and High Tap settings to be filled out. Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be >= Low Tap Settings - Low Tap Position 3) Note: this value may be negative | T | Integer | B | Joel Koepke
Voltage at Highest Tap Position | Transmission | [6 empty] | Transformer Tap Settings | kV | TRANSFORMER_TAP_SETTINGS | HIGHEST_VOLT |  | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out. Note that it is valid for both, Low and High Tap settings to be filled out. Second Condition: This field may be left blank if Low Voltage Level = 1 2) Value must be >= Low Tap Settings - Voltage at Lowest Tap Position 3) Value must be <= High Tap Settings - Voltage at Highest Tap Position 4) Value must be >= 0 | T | Float | B | Joel Koepke
Size of each Voltage Step | Transmission | [6 empty] | Transformer Tap Settings | kV | TRANSFORMER_TAP_SETTINGS | STEP_VOLT |  | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field may be left blank if Low Voltage Level = 1 2) Value must > 0 3) Warn if < 0.002 * Low Side Voltage Level (no-load) 4) Warn if > 0.05 * Low Side Voltage Level (no-load) | T | Float | B
Load Data | Transmission | [6 empty] | Load Data |  | Not in table | Not in table
Description of Change | Transmission | [6 empty] | Load Data |  | LOADS | CHANGE_DESCRIPTION
ERCOT Station Name (Station Code or Station Mnemonic) | Transmission | [6 empty] | Load Data |  | LOADS | SUBSTATION_CODE |  | 1) This field is required 2) Must match ERCOT records. Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters 5) substation code should be in Upper case letters. Generate an error if the rule fails | L | Alpha | B
Load Name (as it appears in the ERCOT model) | Transmission | [6 empty] | Load Data |  | LOADS | LOAD_NAME |  | 1) This field is required 2) May not contain special characters except for an underscore "_" and a dash "-" 2) Warn if >= 14 characters. First 14 characters must be unique. 3)Warning! ERCOT Load Name() should not be >= 14 characters long or the name will be truncated in the model which requires uniqueness. 4) Load Name can not be duplicated in a Station | L | Alpha | B
Load Code | Transmission | [5 empty] | UPDATE 02/2012 | Load Data |  | LOADS | LOAD_CODE |  | Concantenate (Site Code_Substation Code_Lode Name
Load Voltage Level | Transmission | [6 empty] | Load Data |  | LOADS | VOLATGE |  | 1) This field is required 2) Value must be >= 0 3) If the value >= 69kv it must be 69,138, or 345 | T | Float | B
PTI Bus Number | Transmission | [6 empty] | Load Data |  | LOADS | PTI_BUS_NUM |  | 1) This field is optional 2) This field must be between 1 - 99,999 | T | Integer | B
Average MW Load Under Normal Operations | Transmission | [6 empty] | Load Data | MW | LOADS | AVG_LOAD |  | 1) This field is required 2) It should be >0 and generate a warning if = 0 | T | Float | B
Average MVAR Under Normal Operations | Transmission | [6 empty] | Load Data | MVAR | LOADS | AVG_MVAR |  | 1) This field is required 2) It should be >0 and generate a warning if = 0 | T | Float | B
Connected Devices | Transmission | [6 empty] | Load Data |  | Not in table | Not in table
Device Name(s) - that this load is physically connected to | Transmission | [6 empty] | Load Data |  | LOAD_DEVICES | LOAD_DEVICE_NAME |  | 1) This field is required 2) No special characters except an underscore or a dash 3) Warn if >= 17 characters. First 17 characters must be unique. Warning! ERCOT Device Name() should not be >=17 characters long or the name will be truncated in the model which requires uniqueness. 4) 'Connected Device that this load is directly connected to' Field in Load Data Tab should be defined either in the Breaker/Switch Tab(if the connected device is a switch Name) or in the Transformer Tab(if the connected device is a Transformer Name). Produce an Error when connected device is missing in the Breaker_switch Tab. 'Error! Unique controlling device must also exist in the 'BREAKER_SWITCH Tab' | T | Alpha | B
Comments | Transmission | [6 empty] | Load Data |  | LOADS | LOAD_COMMENTS
Date Effective | Transmission | [6 empty] | Load Data |  | LOADS | EFF_DATE |  | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T | Date | B/DVB | Scott/Woody/Angie
SubSync - Gen | Generation | [6 empty] | SubSync |  | Not in table | Not in table
GENERATOR Details | Generation | [6 empty] | SubSync |  | Not in table | Not in table
Unit Name | Generation | Do not show Message on Audit or Delta | [5 empty] | SubSync | List | GENERATION | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Generation | [6 empty] | SubSync | Automatic | SUBSYNC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
SUBSYNCHRONOUS RESONANCE | Generation | [6 empty] | SubSync |  | Not in table | Not in table
Mass # | Generation | Correction 02/28/2012 |  | APD_LD1_MW1_NRRC |  |  | NOT IN TABLE | SubSync | List | SUBSYNC NOT IN TABLE SUBSYNC | MASS NOT IN TABLE MASS_NUMBER
Mass Code | Generation | Correction |  | APD_LD1_MW1_ERRC |  |  |  | SubSync | Automatic | SUBSYNC | MASS_CODE MASS |  | CONCATENATE Unit_CODE_MASS
Name | Generation | [6 empty] | SubSync |  | SUBSYNC | NAME
Mass Inertia | Generation | [6 empty] | SubSync |  | SUBSYNC | MASS_INERTIA
Inertia Units | Generation | [6 empty] | SubSync |  | SUBSYNC | INERTIA_UNITS
Associated Damping | Generation | [6 empty] | SubSync |  | SUBSYNC | ASST_DMPG
Damping Units | Generation | [6 empty] | SubSync |  | SUBSYNC | DMPG_UNITS
Stiffness Between Masses Previous and Current Masses | Generation | [6 empty] | SubSync |  | SUBSYNC | STFNS_BTWN_MASSES
Stiffness Units | Generation | [6 empty] | SubSync |  | SUBSYNC | STFNS_UNITS
SubSync - CC | CC | [6 empty] | SubSync |  | Not in table | Not in table
GENERATOR Details | CC | [6 empty] | SubSync |  | Not in table | Not in table
Unit Name | CC | Do not show Message on Audit or Delta | [5 empty] | SubSync | List | CCUNIT | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
SITE_CODE | CC | [6 empty] | SubSync | Automatic | CCUNIT | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
Resource Name (Unit Code/mnemonic) | CC | [6 empty] | SubSync | Automatic | SUBSYNC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
SUBSYNCHRONOUS RESONANCE | CC | [6 empty] | SubSync |  | Not in table | Not in table
Mass # | CC | Correction 02/28/2012 |  |  |  |  | NOT IN TABLE | SubSync | List | SUBSYNC NOT IN TABLE SUBSYNC | MASS NOT IN TABLE MASS_NUMBER
Mass Code | CC | Correction | [5 empty] | SubSync | Automatic | SUBSYNC | MASS_CODE MASS |  | CONCATENATE Unit_CODE_MASS
Mass Name | CC | [6 empty] | SubSync |  | SUBSYNC | NAME
Mass Inertia | CC | [6 empty] | SubSync |  | SUBSYNC | MASS_INERTIA
Inertia Units | CC | [6 empty] | SubSync |  | SUBSYNC | INERTIA_UNITS
Associated Damping | CC | [6 empty] | SubSync |  | SUBSYNC | ASST_DMPG
Damping Units | CC | [6 empty] | SubSync |  | SUBSYNC | DMPG_UNITS
Stiffness Between Masses Previous And Current Mass | CC | [6 empty] | SubSync |  | SUBSYNC | STFNS_BTWN_MASSES
Stiffness Units | CC | [6 empty] | SubSync |  | SUBSYNC | STFNS_UNITS
PUN Load | Transmission | [6 empty] | PUN Load |  | Not in table | Not in table
Station Details | Transmission | [6 empty] | PUN Load |  | Not in table | Not in table
Station Code | Transmission | [5 empty] | ADD 04/2012 | PUN Load |  | PUN_LOAD | SUBSTATION_CODE
Load Name | Transmission | [5 empty] | ADD 04/2012 | PUN Load |  | PUN_LOAD | LOAD_NAME |  | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Value should following the following convention SiteCode_LoadName. Load Name (Load Name) should be as it appears in the ERCOT Model | L | Alpha | B
Load Code | Transmission | [5 empty] | ADD 04/2012 | PUN Load |  | PUN_LOAD | LOAD_CODE
168 HR Data | Transmission | [6 empty] | PUN Load |  | Not in table
Hour Ending | Transmission | [5 empty] | ADD 04/2012 | PUN Load |  | PUN_LOAD | HR_ENDING
Day of Week | Transmission | [5 empty] | ADD 04/2012 | PUN Load |  | PUN_LOAD | DAY_WEEK |  | 1) These fields are conditionally required if "Private Network - Private Network?" = 'Y' and for each Load identified 2) Value must be >= 0 (for zero load, place a 0 in that space)
MW | Transmission | [5 empty] | ADD 04/2012 | PUN Load |  | PUN_LOAD | MW
General Information - ALL | Distributed Generation | [6 empty] | General Information - DG |  | Not in table | Not in table |  |  | R
Reason for Submission | Distributed Generation | Updated 03/09/2012 validation rule to match view |  |  |  |  | ADD 04/2012 | General Information - |  | SITECODES | SUBMIT_REASON |  | Not null. Select from the list: New Site, Revision, Addition of Unit(s), Deletion of Unit(s)* | R | Dropdown List | B,DVB
Date Form Completed: | Distributed Generation | [5 empty] | ADD 04/2012 | General Information - DG |  | SITECODES | FORM_COMP_DT |  | 1. mm/dd/yyyy format 2. Not null | R | Date | B
Resource Entity Submitting Form: | Distributed Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | General Information - DG |  | RE_RARF | RE_NAME |  | This field should not be null. Resource Entity Name must match with the data existing in Siebel. Resource Entity Name should not allow any special characters except spaces 1.This field is not null. 2. All should be capital letters 3.No Special characters except spaces and dashes. | R | Character | B,DVE
Resource Entity DUNS #: | Distributed Generation | [5 empty] | ADD 04/2012 | General Information - DG |  | SITECODES & RE_RARF | RE_DUNS |  | 1. Not null 2. Must match with the data existing in Siebel 3. Data type: varchar (as sometimes the value contains # with a leading zero) 4. Either a 9 or 13 digit DUNS number | R | Character | B,DVE
Primary Contact | Distributed Generation | [6 empty] | General Information - DG |  | Not in table | Not in table
Printed Name: | Distributed Generation | [6 empty] | General Information - DG |  | Not in table | FORM_COMP_DT |  |  | R | Character | B,DVE
Title: | Distributed Generation | [6 empty] | General Information - DG |  | Not in table | FORM_COMP_DT |  |  | R | Character | B
Phone Number: | Distributed Generation | [6 empty] | General Information - DG |  | Not in table | FORM_COMP_DT |  |  | R | Character | B
E-mail Address: | Distributed Generation | [6 empty] | General Information - DG |  | Not in table | FORM_COMP_DT |  |  | R | Character | B
Fax Number: | Distributed Generation | [6 empty] | General Information - DG |  | Not in table | FORM_COMP_DT |  |  | O | Character | B
Secondary Contact | Distributed Generation | [6 empty] | General Information - DG |  | Not in table | Not in table
Printed Name: | Distributed Generation | [6 empty] | General Information - DG |  | Not in table | Not in table
Title: | Distributed Generation | [6 empty] | General Information - DG |  | Not in table | Not in table
Phone Number: | Distributed Generation | [6 empty] | General Information - DG |  | Not in table | Not in table
E-mail Address: | Distributed Generation | [6 empty] | General Information - DG |  | Not in table | Not in table
Fax Number: | Distributed Generation | [6 empty] | General Information - DG |  | Not in table | Not in table
Site Info - DG | Distributed Generation | [6 empty] | Site Info - DG |  | Not in table | Not in table
Generator Site Name | Distributed Generation | [5 empty] | ADD 04/2012 | Site Info - DG | all caps | SITECODES | SITE_NAME |  | Not null | R | Character | B,DVB
Generator Site Code | Distributed Generation | [5 empty] | ADD 04/2012 | Site Info - DG | all caps | SITECODES | SITE_CODE |  | 1. Not null 2. All should be capital letters | R | Character | B,DVB
Address | Distributed Generation | [5 empty] | ADD 04/2012 | Site Info - DG |  | SITECODES | STREET_ADDRESS |  | Not null | R | Character | B
State | Distributed Generation | [5 empty] | ADD 04/2012 | Site Info - DG |  | SITECODES | STATE |  | Not null | R | Character | B
County | Distributed Generation | [5 empty] | ADD 04/2012 | Site Info - DG |  | SITECODES | COUNTY |  | Not null | R | Character | B
Site In-Service Date | Distributed Generation | [5 empty] | ADD 04/2012 | Site Info - DG | mm/dd/yyyy | SITECODES | SITE_IN_SRVC_DT |  | 1. Must be earlier than Site-Stop Service Date 2. mm/dd/yyyy format 3. Not null | R | Date | B,DVB
Site Stop Service Date | Distributed Generation | [5 empty] | ADD 04/2012 | Site Info - DG | mm/dd/yyyy | SITECODES | SITE_STOP_SRVC_DT |  | 1. Must be later than Site In-Service Date 2. mm/dd/yyyy format | O | Date | B,DVB
Is generation behind a NOIE Settlement Meter Point? | Distributed Generation | [5 empty] | ADD 04/2012 | Site Info - DG | Y/N | SITECODES | RE_BHND_NOIE_SMP_FLG |  | 1. Select from the list: Y or N 2. Not Null | R | Dropdown List | B,DVB
TDSP Providing Service To Gen Site | Distributed Generation | [5 empty] | ADD 04/2012 | Site Info - DG | List | SITECODES | TDSP_PROVIDING_SVC |  | Not null
TDSP DUNS Number | Distributed Generation | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Site Info - DG | Automatic | SITECODES | TDSP_DUNS |  | 1. Not null 2. Must match with the data existing in Siebel 3. Data type: varchar (as sometimes the value contains # with a leading zero) 4. Either a 9 or 13 digit DUNS number | R | Integer | B,DVE
ESI-ID if H9 is "No" | Distributed Generation | [5 empty] | ADD 04/2012 | Site Info - DG |  | SITECODES | ESIID _NOT_BEHIND_NOIE_SETMENT_MTR_PNT |  | Not Required if Resource Behind NOIE Settlement point is 'Y' | C | Character | B,DVE
ERCOT Read | Distributed Generation | [5 empty] | ADD 04/2012 | Site Info - DG | Y/N | SITECODES | ERCOT_READ |  | 1. Select from the list: Y or N 2. Not Null | R | Dropdown List | B,DVB
Number of EPS Primary meters | Distributed Generation | [5 empty] | ADD 04/2012 | Site Info - DG | # | SITECODES | NUM_EPS_METERS |  | Not null | R | Integer | B
Is Resource claiming status as a Non-Modeled Generator as defined in ERCOT Protocol Section 2, Resource | Distributed Generation | [5 empty] | ADD 04/2012 | Site Info - DG | Y/N | SITECODES | RE_CLAIM_NONMOD_STATUS |  | 1. Select from the list: Y or N 2. Not Null | R | Dropdown List | B,DVB
Is Resource >10 MW? | Distributed Generation | [5 empty] | ADD 04/2012 | Site Info - DG | Y/N | SITECODES | RES_GREAT_TEN_MW |  | 1. Select from the list: Y or N 2. Not Null | R | Dropdown List | B,DVB
Unit Info - DG | Distributed Generation | [6 empty] | Unit Info - DG |  | Not in table | Not in table
Generator Details | Distributed Generation | [6 empty] | Unit Info - DG |  | Not in table | Not in table
Unit Name | Distributed Generation | 03/13/12 Updated Validation Rules |  |  |  |  | ADD 04/2012 | Unit Info - DG | all caps | NON_MODELED | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2.All letters should be capital 3. Should not allow spaces | R | Character | B
Unit Code | Distributed Generation | 03/13/12 Updated Validation Rules |  |  |  |  | ADD 04/2012 | Unit Info - DG | Automatic | NON_MODELED | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB
Unit Dates | Distributed Generation | [6 empty] | Unit Info - DG |  | Not in table | Not in table |  | 2.All letters should be capital
Unit Start Date | Distributed Generation | 03/13/12 Updated Validation Rules |  |  |  |  | ADD 04/2012 | Unit Info - DG | mm/dd/yyyy | NON_MODELED | UNIT_MRD_ST_DT |  | This field is not null. Format should be: MM/DD/YYYY | R | Date | B
Unit End Date | Distributed Generation | 03/13/12 Updated Validation Rules |  |  |  |  | ADD 04/2012 | Unit Info - DG | mm/dd/yyyy | NON_MODELED | UNIT_END_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date | B
Fuel Information | Distributed Generation | [6 empty] | Unit Info - DG |  | Not in table | Not in table
Name Plate Rating | Distributed Generation | 3/9/2012 Updated Validation and Added to form |  |  |  |  | ADD 04/2012 | Unit Info - DG | MVA | NON_MODELED | NAME_PLT_RTG_MW | Not null | 1. Not Null 2. Numeric Value | R | Numeric | B,DVB
Technology Type | Distributed Generation | 03/9/2012 Corrected Field name |  |  |  |  | ADD 04/2012 | Unit Info - DG | List | NON_MODELED | TECHNOLOGY_TYPE |  | 1. Select from drop down list: FS, GT, H, W, S, X 2. Not null | R | Dropdown List | B,DVB
Name Plate Rating | Distributed Generation | 3/9/2012 Updated Validation and Added to form |  |  |  |  | ADD 04/2012 | Unit Info - DG | MVA | NON_MODELED | NAME_PLT_RTG_MVA |  | 1. Not Null 2. Numeric Value | R | Numeric | B,DVB
Renewable | Distributed Generation | 03/9/2012 Corrected Field name |  |  |  |  | ADD 04/2012 | Unit Info - DG | Y/N | NON_MODELED | RENEWABLE_FLG |  | 1. Select from the list: Y or N 2. Not Null | R | Dropdown List | B,DVB
Renewable/Offset | Distributed Generation | 03/9/2012 Corrected Field name |  |  |  |  | ADD 04/2012 | Unit Info - DG | List | NON_MODELED | RENEWABLE_OFFSET |  | 1. Select from the list: NA, RN, OS 2. Not Null | R | Dropdown List | B,DVB
If Wind, Number of Turbines | Distributed Generation | 03/9/2012 Corrected Field name |  |  |  |  | ADD 04/2012 | Unit Info - DG | # | NON_MODELED | NUM_WIND_TURBINES |  | 1. Data type: Integer 2. N/A is not valid. Leave blank if unknown.
Physical Unit Type | Distributed Generation | 03/9/2012 Corrected Field name |  |  |  |  | ADD 04/2012 | Unit Info - DG | List | NON_MODELED | PHYS_UNIT_TYPE |  | 1. Select from drop down list: CA, CC, CE, CS, CT, FC, GT, HY, IC, NA, OT, PS, PV, ST, WT 2. Not null | R | Dropdown List | B,DVB
Primary Fuel Type | Distributed Generation | 03/9/2012 Corrected Field name |  |  |  |  | ADD 04/2012 | Unit Info - DG | List | NON_MODELED | PRIM_FUELTYPE |  | 1. Select from drop down list: AB, BFG, BIT, BL, DFO, GEO, JF, KER, LFG, LIG, MSW, NA, NG, NUC, OBG, OBL, OBS, OG, OO, OTH, PC, PG, RFO, SLW, STM, SUB, SUN, T, TDF, WAT, WDL, WDS, WH, WND, WOC 2. Not null | R | Dropdown List | B,DVB
Secondary Fuel Type | Distributed Generation | 03/9/2012 Corrected Field name |  |  |  |  | ADD 04/2012 | Unit Info - DG | List | NON_MODELED | SEC_FUELTYPE |  | 1. Select from drop down list: AB, BFG, BIT, BL, DFO, GEO, JF, KER, LFG, LIG, MSW, NA, NG, NUC, OBG, OBL, OBS, OG, OO, OTH, PC, PG, RFO, SLW, STM, SUB, SUN, T, TDF, WAT, WDL, WDS, WH, WND, WOC 2. Not null | R | Dropdown List | B,DVB
Private Network Info | Distributed Generation | [6 empty] | Unit Info - DG |  | Not in table | Not in table
Private Network / Cogen | Distributed Generation | 03/9/2012 Corrected Field name |  |  |  |  | ADD 04/2012 | Unit Info - DG | Y/N | NON_MODELED | PUN_FLG |  | 1. Select from the list: Y or N 2. Not Null | R | Dropdown List | B,DVB
Amount of Self Serve for Cogen | Distributed Generation | 03/9/2012 Corrected Field name |  |  |  |  | ADD 04/2012 | Unit Info - DG | MW | NON_MODELED | AMT_SELFSRV_COGEN |  | Required if Private Network / Cogen is 'Y' | R | Dropdown List | B,DVB
Private Network Net Interchange | Distributed Generation | 03/9/2012 Corrected Field name |  |  |  |  | ADD 04/2012 | Unit Info - DG | MW | NON_MODELED | PRIVATE_NWK_NET_INTERCHANGE |  | Required if Private Network / Cogen is 'Y' | R | Dropdown List | B,DVB
Private Network Gross Unit MW | Distributed Generation | 03/9/2012 Corrected Field name |  |  |  |  | ADD 04/2012 | Unit Info - DG | MW | NON_MODELED | PRIVATE_NET_GROSS_UNT_MW |  | Required if Private Network / Cogen is 'Y' | R | Dropdown List | B,DVB
Private Network Gross Unit MVAR | Distributed Generation | 03/9/2012 Corrected Field name |  |  |  |  | ADD 04/2012 | Unit Info - DG | MVAR | NON_MODELED | PRIVATE_NET_GROSS_UNT_MVAR |  | Required if Private Network / Cogen is 'Y' | R | Dropdown List | B,DVB
Generic Info | Distributed Generation | [6 empty] | Unit Info - DG |  | Not in table | Not in table
Generic Fuel Category | Distributed Generation | 03/9/2012 Corrected Field name |  |  |  |  | ADD 04/2012 | Unit Info - DG | List | NON_MODELED | GEN_FUEL_CAT |  | 1. Select from drop down list: Coal and Lignite, Combined Cycle greater than 90 MW, Combined Cycle less than or equal to 90 MW, Diesel (and all other diesel or gas-fired Resources), Gas Steam Non-reheat Boiler or Boiler without air-preheater, Gas Steam Reheat Boiler, Gas Steam Supercritical Boiler, Hydro, Nuclear, Other Renewable (i.e. non-hydro renewable Resources), Power Storage, Simple Cycle greater than 90 MW, Simple Cycle less than or equal to 90 MW 2. Not null | R | Dropdown List | B,DVB
Generic Start-up / Operating Category | Distributed Generation | 03/9/2012 Corrected Field name |  |  |  |  | ADD 04/2012 | Unit Info - DG | List | NON_MODELED | GEN_STUP_OPER_CAT |  | 1. Select from drop down list: Base Load, Gas-Cyclic, Gas-Intermediate, Gas-Peaking, Renewable (Including Hydro) 2. Not null | R | Dropdown List | B,DVB
Resource Owner Data | Distributed Generation | [6 empty] | Unit Info - DG |  | Not in table | Not in table
Resource Entity Name | Distributed Generation | Update 03/13/2012 |  |  |  |  | ADD 04/2012 | Unit Info - DG | all caps | NON_MODELED | RE_DUNS RE_NAME |  | 1. Not null 2. Must match with the data existing in Siebel 3. Do not allow any special characters except spaces and dashes. | R | Character | B,DVE
Resource Entity Duns Number | Distributed Generation | Updated 03/07/2012 |  |  |  |  | ADD 04/2012 | Unit Info - DG |  | NON_MODELED | RE_NAME RE_DUNS |  | 1. Not null 2. Must match with the data existing in Siebel 3. Data type: varchar (as sometimes the value contains # with a leading zero) 4. Either a 9 or 13 digit DUNS number | R | Character | B,DVE
UNIT INFO - Solar | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar |  | Not in table | Not in table
GENERATOR DETAILS | Solar | [6 empty] | UNIT INFO - Solar |  | Not in table | Not in table
Unit Name | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | all caps | Solar | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B
Resource Name (Unit Code/Mnemonic) | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | Automatic | Solar | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | Character | B,DVB
Non Modeled Generation | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | Y/N | Solar | NON_MOD_GEN |  | 1.Select from the list: Y or N 2.Not Null
PUC Registration Number (Docket Number) | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar |  | Solar | PUC_NUM |  | This field is optional and it should be a number. NA is not valid , Leave it blank if not applicable.
ERCOT Interconnection Project Number - Only new Units | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar |  | Solar | ERCOT_INTRCONN_PROJ_NUM |  | 1.This field is optional. Required only for new units. Enter a Valid Number or leave it blank if not applicable 2. Cross check with the data entered in the field 'This submittal is for' in General Information Tab. If the value is 'New Site' then only this field is required.
NERC Number (NERC ID#) | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar |  | Solar | NERC_NUM |  | This field is optional. NA is not valid , Leave it blank if not applicable.
Qualifying facility | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | Y/N | Solar | QUAL_FACILITY_FLG |  | QF flag is not null. Select from the list: Y or N
SITE AND UNIT DATES | Solar | [6 empty] | UNIT INFO - Solar |  | Not in table | Not in table
Transmission Only Date (POI) | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | mm/dd/yyyy | Solar | TRANS_ONLY_DT |  | 1.This field is optional. Format should be: MM/DD/YYYY 2. Data type must be Date.
Standard Generation Interconnection Agreement (SGIA) Signature Date | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | mm/dd/yyyy | Solar | SGIA_SIG_DT |  | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date.
Unit Start Date (Model Ready Date) | Solar | 03/13/2012 Updated Validation |  |  |  |  | ADD 04/2012 | UNIT INFO - Solar | mm/dd/yyyy | Solar | UNIT_MRD_ST_DT |  | This field is optional. Format should be: MM/DD/YYYY
Unit Commercial Date | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | mm/dd/yyyy | Solar | UNIT_START_DT |  | This field is not null. Format should be: MM/DD/YYYY Unit Start Date should be >= Site Start Date ( Site-Information Tab)
Unit End Date | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | mm/dd/yyyy | Solar | UNIT_END_DT |  | This field is optional. Format should be: MM/DD/YYYY
POINT OF INTERCONNECTION | Solar | [6 empty] | UNIT INFO - Solar |  | Not in table | Not in table
SubStation Code/SubStation Mnemonic | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | all caps | Solar | SUBSTAT_CODE_SUB_MNEMONIC |  | 1) This field is not null (required). Data type must be Character. 2) Must match ERCOT records (unless new). Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" . 4) Must be <= 8 characters. Warning! Substation Code should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) Substation code should be in Upper case letters. Generate an error if the rule fails.
Voltage Level | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | kV | Solar | VOL_LEV |  | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0.
PTI Bus Number | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | # | Solar | PTI_BUS_NUM |  | 1) This field isnot null (required). Data type must be Integer. 2) The value must be > 0.
FUEL INFORMATION | Solar | [6 empty] | UNIT INFO - Solar |  | Not in table | Not in table
Primary Fuel Type | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | List | Solar | PRIM_FUELTYPE |  | 1)Resource Category is not null. 2)Select from the list: SUN,NA,NG and OT
Secondary Fuel Type | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | List | Solar | SEC_FUELTYPE |  | 1)Resource Category is not null. 2)Select from the list: SUN,NA,NG and OT
Fuel Transportation Type | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | List | Solar | FUEL_TRANSTYPE |  | NA
Resource Category | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | List | Solar | RES_CATG |  | 1)Resource Category is not null. 2)Select from the list: Solar
RATINGS AND DESIGNS | Solar | [6 empty] | UNIT INFO - Solar |  | Not in table | Not in table
Renewable | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | Y/N | Solar | RENEWABLE_FLG |  | Renewable Flag is not null. Select from the list: Y or N
Renewable/Offset | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | List | Solar | RENEWABLE_OFFSET |  | Select from the list : RN, OS, NA. This field is not null.
Physical Unit Type | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | List | Solar | PHYS_UNIT_TYPE |  | Select from the list:CA, CC, CE, CS, CT, FC, GT, HY, IC, NA, OT, PS, PV, ST, WT. This field is not null.
Name Plate Rating | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | MVA | Solar | NAME_PLT_RTG |  | Name Plate Rating should be >= Real Power Rating
Real Power Rating | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | MW | Solar | RTG_MW |  | Real Power Rating should be > Reactive Power Rating
Reactive Power Rating | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | MVAR | Solar | RTG_MVAR |  | Name Plate Rating should be >= Reactive Power Rating
Unit Generating Voltage | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | kV | Solar | UNIT_KV |  | 1. This field is not null and it should be a number 2. Unit Generating voltage can not be below 4.16 KV
Governor Droop Setting | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | Percent | Solar | GOV_DROOP |  | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if it is not between 0 and 25. Generate Warning if > 5 (protocol requirement).
Governor Dead-Band | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | Hz | Solar | GOV_DEAD_BND |  | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if > 0.1. Generate Warning if > 0.03.
Design Max Ambient Temperature | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | degree F | Solar | DESIGN_MAX_AMB_TEMP |  | >100 <150
Design Min Ambient Temperature | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | degree F | Solar | DESIGN_MIN_AMB_TEMP |  | >-100 <32
GEOGRAPHIC LOCATION (CENTER OF PLANT) | Solar | [6 empty] | UNIT INFO - Solar |  | Not in table | Not in table
Latitude Of Center Of Plant | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | decimal degrees (N) | Solar | LAT_CENTER_PLT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if Latitude < 25.0 or > 37.0.
Longitude Of Center Of Plant | Solar | [5 empty] | ADD 04/2012 | UNIT INFO - Solar | decimal degrees (W) | Solar | LONG_CENTER_PLT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if <93 or > 107 .
Unit Info - Solar Inverter | Solar | [6 empty] | Unit Info - Solar Inverter |  | Not in table | Not in table
GENERATOR Details | Solar | [6 empty] | Unit Info - Solar Inverter |  | Not in table | Not in table
Unit Name | Solar | Do not show Message on Audit or Delta |  |  |  |  | ADD 04/2012 | Unit Info - Solar Inverter | List | SOLAR_INVERTER | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B
Resource Name (Unit Code/Mnemonic) | Solar | [5 empty] | ADD 04/2012 | Unit Info - Solar Inverter | Automatic | SOLAR_INVERTER | UNIT_CODE |  | .This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | Character | B,DVB
Total Number of Inverters | Solar | [5 empty] | ADD 04/2012 | Unit Info - Solar Inverter | # | SOLAR_INVERTER | TOTNUM_INVERTERS |  | 1.This is not null and it should be an Integer 2. Not null.
GROUP 1 - INVERTER DETAILS | Solar | [6 empty] | Unit Info - Solar Inverter |  | Not in table | Not in table
Group 1 - Type of INVERTER (Manufacturer/Model) | Solar | [5 empty] | ADD 04/2012 | Unit Info - Solar Inverter | all caps | SOLAR_INVERTER | GRP1_INV_TYPE |  | This field is not null and the Data type should be character.
Group 1 - MW Rating for this model of INVERTER | Solar | [5 empty] | ADD 04/2012 | Unit Info - Solar Inverter | MW | SOLAR_INVERTER | GRP1_INV_MW_MDL_RTG |  | This field is not null and it should be an integer
Group 1 - Number of this type of INVERTER | Solar | [5 empty] | ADD 04/2012 | Unit Info - Solar Inverter | # | SOLAR_INVERTER | GRP1_INV_NUM |  | 1. This field is optional. If entered it should be a character. If the data is entered for Group2, then reactive capability- Solar Tab should have values for this group. 2. Inverter groups of Inverters within a unit must be of the same type and size. RARF Audit report should generate a warning if this rule fails
GROUP 2 - INVERTER DETAILS | Solar | [6 empty] | Unit Info - Solar Inverter |  | Not in table | Not in table
Group 2 - Type of INVERTER (Manufacturer/Model) | Solar | [5 empty] | ADD 04/2012 | Unit Info - Solar Inverter | all caps | SOLAR_INVERTER | GRP2_INV_TYPE |  | This field is optional/conditional. Required if Type of Inverter info is entered for Group2 otherwise it is optional. Data type should be Integer. If the data is entered for Group2, then reactive capability-Solar Tab should have values for this group.
Group 2 - MW Rating for this model of INVERTER | Solar | [5 empty] | ADD 04/2012 | Unit Info - Solar Inverter | MW | SOLAR_INVERTER | GRP2_INV_MW_MDL_RTG |  | 1. This field is optional. If entered it should be a character. If the data is entered for Group3, then reactive capability-Solar Tab should have values for this group. 2. Wind groups of Inverters within a unit must be of the same type and size. RARF Audit report should generate a warning if this rule fails
Group 2 - Number of this type of INVERTER | Solar | [5 empty] | ADD 04/2012 | Unit Info - Solar Inverter | # | SOLAR_INVERTER | GRP2_INV_NUM |  | 1. Conditional required if Type of Inverter info is entered for Group2 2. Data type should be numeric.
GROUP 3 - INVERTER DETAILS | Solar | [6 empty] | Unit Info - Solar Inverter |  | Not in table | Not in table
Group 3 - Type of INVERTER (Manufacturer/Model) | Solar | [5 empty] | ADD 04/2012 | Unit Info - Solar Inverter | all caps | SOLAR_INVERTER | GRP3_INV_TYPE |  | 1. Conditional required if Type of Inverter info is entered for Group3 2. Data type should be numeric.
Group 3 - MW Rating for this model of INVERTER | Solar | [5 empty] | ADD 04/2012 | Unit Info - Solar Inverter | MW | SOLAR_INVERTER | GRP3_INV_MW_MDL_RTG |  | This field is optional/conditional. Required if Type of Inverter info is entered for Group5 otherwise it is optional. Data type should be Integer. If the data is entered for Group5, then reactive capability-Solar Tab should have values for this group.
Group 3 - Number of this type of INVERTER | Solar | [5 empty] | ADD 04/2012 | Unit Info - Solar Inverter | # | SOLAR_INVERTER | GRP3_INV_NUM |  | This field is optional/conditional. Required if Type of Inverter info is entered for Group4 otherwise it is optional. Data type should be Integer. If the data is entered for Group4, then reactive capability-Solar Tab should have values for this group.
GROUP 4 - INVERTER DETAILS | Solar | [6 empty] | Unit Info - Solar Inverter |  | Not in table | Not in table
Group 4 - Type of INVERTER (Manufacturer/Model) | Solar | [5 empty] | ADD 04/2012 | Unit Info - Solar Inverter | all caps | SOLAR_INVERTER | GRP4_INV_TYPE |  | 1. Optional. 2. Group4 reactive capability-Solar Tab should have values for this group.
Group 4 - MW Rating for this model of INVERTER | Solar | [5 empty] | ADD 04/2012 | Unit Info - Solar Inverter | MW | SOLAR_INVERTER | GRP4_INV_MW_MDL_RTG |  | This field is optional/conditional. Required if Type of Inverter info is entered for Group5 otherwise it is optional. Data type should be Integer. If the data is entered for Group5, then reactive capability-Solar Tab should have values for this group.
Group 4 - Number of this type of INVERTER | Solar | [5 empty] | ADD 04/2012 | Unit Info - Solar Inverter | # | SOLAR_INVERTER | GRP4_INV_NUM |  | 1. Conditional required if Type of Inverter info is entered for Group3 2. Data type should be numeric.
GROUP 5 - INVERTER DETAILS | Solar | [6 empty] | Unit Info - Solar Inverter |  | Not in table | Not in table
Group 5 - Type of INVERTER (Manufacturer/Model) | Solar | [5 empty] | ADD 04/2012 | Unit Info - Solar Inverter | all caps | SOLAR_INVERTER | GRP5_INV_TYPE
Group 5 - MW Rating for this model of INVERTER | Solar | [5 empty] | ADD 04/2012 | Unit Info - Solar Inverter | MW | SOLAR_INVERTER | GRP5_INV_MW_MDL_RTG
Group 5 - Number of this type of INVERTER | Solar | [5 empty] | ADD 04/2012 | Unit Info - Solar Inverter | # | SOLAR_INVERTER | GRP5_INV_NUM
Site Information - ESG | ESG | [6 empty] | Site Information - ESG |  | Not in table | Not in table
Site Information for ESG Resource | ESG | [6 empty] | Site Information - ESG |  | Not in table | Not in table
Dispatch Asset Code | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | all caps | ESGUNIT | DISPATCH_ASSET_CODE
Resource Site Name: | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | all caps | SITECODES | SITE_NAME
ESG Resource Site Code: | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | all caps | SITECODES | SITE_CODE |  | 8
Street Address: | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG |  | SITECODES | STREET_ADDRESS
City: | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG |  | SITECODES | CITY
State | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG |  | SITECODES | STATE
Zipcode | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG |  | SITECODES | ZIPCODE
County: | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG |  | SITECODES | COUNTY
Congestion Management Zone for 2003: | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | List | SITECODES | CMZ_2003 |  | 1. Select from the list: North,South,Houston,West. 2. Not Null
Is Storage Netted From Generation at ERCOT Read Gensite? | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | Y/N | SITECODES | RE_OWNED_NOIE_FLG |  | 1. Select from the list: Y or N 2. Not Null
Is Storage Behind a NOIE Settlement Meter Point? | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | Y/N | SITECODES | RE_BHND_NOIE_SMP_FLG |  | 1. Select from the list: Y or N 2. Not Null
Will site be acting as a CLR during Charging State? | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | Y/N | ESGUNIT | CLR_CHARGING_STATE_FLG
Load Resource Type (CLR/UFR/Interruptible) | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | List | ESGUNIT | LR_TYPE_CLR_UFR_FLG
If CLR, will CLR be Dynamically Scheduling? | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | Y/N | ESGUNIT | CLR_DS_FLG
Storage Resource Effective Date | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | mm/dd/yyyy | ESGUNIT | STORAGE_RE_START_DT |  | 1. Must be earlier than Site-Stop Service Date. 2. mm/dd/yy format. 3. Not null.
Storage Resource Expiration Date | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | mm/dd/yyyy | ESGUNIT | STORAGE_RE_STOP_DT |  | 1. Must be later than Site In-Service Date. 2. mm/dd/yy format. 3. Not null.
Substation Name for POD | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | all caps | ESGUNIT | SUBSTATION_NAME_POD
Substation Code for POD | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | all caps | ESGUNIT | SUBSTATION_NAME_POD
Transmission Bus POD (PTI Bus No) | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | # | ESGUNIT | TRANSMISSION_BUS_POD_PTI_BUS_NO
Voltage Level of Telemetered load(s) | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | kV | ESGUNIT | VOLTAGE_LEVEL_TELEMETERED_LOAD
Meter Reading Entity (TDSP) | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | List | ESGUNIT | METER_READING_ENTITY
Meter Reading Entity Duns Number | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | Automatic | ESGUNIT | METER_READING_ENTITY_DUNS_NO
ESI-ID assigned to meter | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG |  | ESGUNIT | ESIID_ASSIGNED_METER
Wholesale Delivery Point? | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | Y/N | ESGUNIT | WHOLESALE_DELIVERY_PT
Load Resource Control Device | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | List | ESGUNIT | LR_CONTROL_DEVICE
ERCOT Load Zone | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | List | ESGUNIT | ERCOT_LOAD_ZONE
Private Use Network? | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | Y/N | ESGUNIT | PUN_FLG
Resource owned by NOIE? | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | Y/N | ESGUNIT | NOIE_FLG |  | Select from the list: Y or N
Is Resource behind a NOIE Settlement Meter Point? | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | Y/N | ESGUNIT | RE_NOIE_SETTLEMENT_METER_POINT_FLG |  | Select from the list: Y or N
Number of EPS Primary meters: | ESG | [5 empty] | ADD 04/2012 | Site Information - ESG | Integer | SITECODES | NUM_EPS_METERS |  | This field is required and it should be an integer
Unit Info - ESG | ESG | [6 empty] | Unit Info - ESG |  | Not in table | Not in table
GENERATOR Details | ESG | [6 empty] | Unit Info - ESG |  | Not in table | Not in table
Unit Name | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | all caps | ESGUNIT | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | Lodestar,NMMS | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | Automatic | ESGUNIT | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Lodestar,NMMS | Lodestar,NMMS
Non Modeled Generation | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | Y/N | ESGUNIT | NON_MOD_GEN |  | Select from the list: Y or N | R | Dropdown List | B,DVB
PUC Registration Number (Docket Number) | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG |  | ESGUNIT | PUC_NUM |  | This field is optional. Enter a Valid Number or leave it blank if not applicable | O | Integer | B
ERCOT Interconnection Project Number - only new units | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG |  | ESGUNIT | ERCOT_INTRCONN_PROJ_NUM |  | 1.This field is optional. Required only for new units. Enter a Valid Number or leave it blank if not applicable 2. Cross check with the data entered in the field 'This submittal is for' in General Information Tab. If the value is 'New Site' then only this field is required. | O | Character | B,DVE
NERC Number (NERC ID#) | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG |  | ESGUNIT | NERC_NUM |  | This field is optional. Enter a Valid Number or leave it blank if not applicable | O | Character | B
Qualifying facility | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | Y/N | ESGUNIT | QUAL_FACILITY_FLG |  | QF flag is not null. Select from the list: Y or N | R | Dropdown List | B,DVB
SITE AND UNIT DATES | ESG | [6 empty] | Unit Info - ESG |  | Not in table | Not in table
Transmission Only Date (POI) | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | mm/dd/yyyy | ESGUNIT | TRANS_ONLY_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB
Standard Generation Interconnection Agreement (SGIA) Signature Date | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | mm/dd/yyyy | ESGUNIT | SGIA_SIG_DT |  | 1) This field is required 2) Data type must be date 3) Generate an Error if blank. Generate Warning if > current date | R | Date | B/DVB
Unit Start Date (Model Ready Date) | ESG | 03/13/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Unit Info - ESG | mm/dd/yyyy | ESGUNIT | UNIT_MRD_ST_DT |  | This field is optional. Format should be: MM/DD/YYYY | R | Date | B/DVB
Unit Commercial Date | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | mm/dd/yyyy | ESGUNIT | UNIT_START_DT |  | This field is not null. Format should be: MM/DD/YYYY Unit Start Date should be >= Site Start Date ( Site-Information Tab) | R | Date | B/DVB
Unit End Date | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | mm/dd/yyyy | ESGUNIT | UNIT_END_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date | B
POINT OF INTERCONNECTION | ESG | [6 empty] | Unit Info - ESG |  | Not in table | Not in table
SubStation Code/SubStation Mnemonic | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | all caps | ESGUNIT | SUBSTAT_CODE_SUB_MNEMONIC |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital. 3. Should not allow spaces. 4. Can not exceed 13 characters for split gen resources | R |  | B/DVB
Voltage Level | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | kV | ESGUNIT | VOL_LEV |  | 1) This field is not null (required). Data type must be a numeric. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0. | T | Float | B/DVE
PTI Bus Number | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG |  | ESGUNIT | PTI_BUS_NUM |  | 1) This field is not null (required). Data type must be a numeric. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0. | T | Float | B
FUEL INFORMATION | ESG | [6 empty] | Unit Info - ESG |  | Not in table | Not in table
Physical Unit Type Energy Storage Technology Type | ESG | 03/08/2012 Updated List |  |  |  |  | ADD 04/2012 | Unit Info - ESG | List | ESGUNIT | PHYS_UNIT_TYPE |  | 1) This field is required 2) Data type must be one from a list of possibilities FC,NA,OT | R
Primary Fuel Type | ESG | 03/08/2012 Updated List |  |  |  |  | ADD 04/2012 | Unit Info - ESG | List | ESGUNIT | PRIM_FUELTYPE |  | Select from the list: OTH, NA | R | Dropdown List | B,DVB
Secondary Fuel Type | ESG | 03/08/2012 Updated List |  |  |  |  | ADD 04/2012 | Unit Info - ESG | List | ESGUNIT | SEC_FUELTYPE |  | Select from the list: OTH, NA | R | Dropdown List | B,DVB
Fuel Transportation Type | ESG | 03/08/2012 Updated List |  |  |  |  | ADD 04/2012 | Unit Info - ESG | List | ESGUNIT | FUEL_TRANSTYPE |  | Select from the list: NA | R | Dropdown List | B,DVB
RATINGS AND DESIGNS | ESG | [6 empty] | Unit Info - ESG |  | Not in table | Not in table
Renewable | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | Y/N | ESGUNIT | RENEWABLE_FLG |  | Renewable Flag is not null. Select from the list: Y or N | R | Dropdown List | B,DVB
Renewable/Offset | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | List | ESGUNIT | RENEWABLE_OFFSET |  | Select from the list : RN, OS, NA. This field is not null. | R | Dropdown List | B,DVB
Resource Category | ESG | 03/08/2012 Updated List |  |  |  |  | ADD 04/2012 | Unit Info - ESG | List | ESGUNIT | RES_CATG |  | Select from the list: Energy Storage | R | Dropdown List | B,DVB
Name Plate Rating | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | MVA | ESGUNIT | NAME_PLT_RTG |  | Name Plate Rating should be >= Real Power Rating | R | Numeric | B,DVB
Real Power Rating | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | MW | ESGUNIT | RTG_MW |  | Real Power Rating should be > Reactive Power Rating | R | Numeric | B,DVB
Reactive Power Rating | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | MVAR | ESGUNIT | RTG_MVAR |  | Name Plate Rating should be >= Reactive Power Rating | R | Numeric | B,DVB
Turbine Rating | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | MW | ESGUNIT | TURBINE_RTG |  | This field is optional. Enter Numeric value or leave it blank if not applicable. | O | Numeric | B
Unit Generating Voltage | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | kV | ESGUNIT | UNIT_KV |  | 1. This field is not null and it should be a number 2. Unit Generating voltage can not be below 4.16 KV | R | Numeric | B
Governor (or equivalent) Droop Setting (%) | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | Percent | ESGUNIT | GOV_DROOP |  | 1) This field is required 2) Data type must be Numeric, Positive Value. 3) Generate an Error if it is not between 0 and 25. Generate Warning if > 5 (protocol requirement). | R | Numeric | B,DVB
Governor (or equivalent) Dead-Band (Hz) | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | Hz | ESGUNIT | GOV_DEAD_BND |  | 1) This field is required 2) Data type must be Numeric, Positive Value. 3) Generate an Error if > 0.1. Generate Warning if > 0.03. | R | Numeric | B,DVB
Is Resource Duration Limited (DLR) | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | Y/N | ESGUNIT | DLR_LIMITED |  | 1) This field is required 2) Data type must be 'Y' or 'N' 3) Generate an Error if blank | R
DLR sustained energy output for 1 hour | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | MWh | ESGUNIT | DLR_ENRGY_OUTPUT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if > 1000. | R
Maximum Energy Storage Capability | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | MWh | ESGUNIT | MAX_ENRGY_STORG_CAPB |  | 1. This field is not null and it should be a number | R
GEOGRAPHIC LOCATION (CENTER OF PLANT) | ESG | [6 empty] | Unit Info - ESG |  | Not in table | Not in table
Latitude Of Center Of Plant | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | decimals degrees (N) | ESGUNIT | LAT_CENTER_PLT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if Latitude < 25.0 or > 37.0. | R
Longitude Of Center Of Plant | ESG | [5 empty] | ADD 04/2012 | Unit Info - ESG | decimals degrees (W) | ESGUNIT | LONG_CENTER_PLT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if <93 or > 107 . | R
SubSync - ESG | ESG | [6 empty] | Unit Info - ESG |  | Not in table | Not in table
GENERATOR Details | ESG | [6 empty] | SubSync - ESG |  | Not in table | Not in table
Unit Name | ESG | Do not show Message on Audit or Delta |  |  |  |  | ADD 04/2012 | SubSync | List | SUBSYNC | UNIT_NAME |  | 1.This field is not null. Data type: Character. | R | Character | B
Resource Name (Unit Code/Mnemonic) | ESG | [5 empty] | ADD 04/2012 | SubSync | Automatic | SUBSYNC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | Character | B,DVB
SUBSYNCHRONOUS RESONANCE | ESG | [6 empty] | SubSync - ESG |  | Not in table | Not in table |  | 2.All letters should be capital
Mass # | ESG | Correction 02/28/2012 |  |  |  |  | ADD 04/2012 NOT IN TABLE | SubSync | List | SUBSYNC NOT IN TABLE SUBSYNC | MASS NOT IN TABLE MASS_NUMBER |  | 3. Should not allow spaces
Mass Name | ESG | Change |  |  |  |  | ADD 04/2012 | SubSync |  | SUBSYNC | NAME |  | 4. Can not exceed 13 characters for split gen resources
Mass Code | ESG | Corrected |  |  |  |  | ADD 04/2012 | SubSync | Automatic | SUBSYNC | MASS_CODE MASS |  | CONCATENATE Unit_CODE_MASS
Mass Inertia | ESG | [5 empty] | ADD 04/2012 | SubSync |  | SUBSYNC | MASS_INERTIA
Inertia units | ESG | [5 empty] | ADD 04/2012 | SubSync |  | SUBSYNC | INERTIA_UNITS
Associated damping | ESG | [5 empty] | ADD 04/2012 | SubSync |  | SUBSYNC | ASST_DMPG
Damping units | ESG | [5 empty] | ADD 04/2012 | SubSync |  | SUBSYNC | DMPG_UNITS
Stiffness Between Masses Previous And Current Mass | ESG | [5 empty] | ADD 04/2012 | SubSync |  | SUBSYNC | STFNS_BTWN_MASSES
Stiffness units | ESG | [5 empty] | ADD 04/2012 | SubSync |  | SUBSYNC | STFNS_UNITS
Parameters - Solar | Solar | [6 empty] | Parameters - Solar |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type Selected is 'GEN' where GEN is non-CC non-wind Generation Resources. | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,MMS,NMMS
Generator Details | Solar | [6 empty] | Parameters - Solar |  | Not in table | Not in table
Unit Name | Solar | Do not show Message on Audit or Delta |  |  |  |  | ADD 04/2012 | Parameters - Solar | List | SOLAR | UNIT_NAME | 1. Not Null. 2. Must not exceed 4 characters for Jointly Owned Units 3. Maximum of 8 character allowed | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | Automatic | SOLAR & SOLAR_DERATING | UNIT_CODE | 1. Not Null. 2. Enter Site Code and Unit Name for this field (Sitecode_Unit Name) 3. All letters must be capital | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Reasonability Limits | Solar | [6 empty] | Parameters - Solar |  | Not in table | Not in table
High Reasonability Limit | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW | SOLAR | HR_LMT | 1. High Reasonability Limit >0 2. HighReasonabilityLimit >= LowReasonablityLimit 3. Not Null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Low Reasonability Limit | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW | SOLAR | LR_LMT | 1. Low Reasonability Limit >0 for Non PUN sites 2. Low ReasonabilityLimit <= High ReasonablityLimit 3. PUN (Private Use Network) Sites LRL should equal zero or produce a Warning 4. Not Null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
High Reasonability Ramp Rate Limit | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW/min | SOLAR | HR_RAMPRATE_LMT | 1. High Reasonability Ramp Rate Limit >= Low Reasonability Ramp Rate Limit. 2. Not null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS
Low Reasonability Ramp Rate Limit | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW/min | SOLAR | LR_RAMP_RATE_LMT | 1. Low Reasonability Ramp Rate Limit >=0. 2. Not null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS
Seasonal Ratings Spring | Solar | [6 empty] | Parameters - Solar |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Spring | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW | SOLAR | SEASON_NET_MAX_SUST_RTG_SP | 1.Seasonal Net Max Sustainable Rating - Spring >= Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Spring > Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS
Seasonal Net Min Sustainable Rating - Spring | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW | SOLAR | SEASON_NET_MIN_SUST_RTG_SP | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS
Seasonal Net Max Emergency Rating - Spring | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW | SOLAR | SEASON_NET_MAX_EMGY_RTG_SP | 1.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS
Seasonal Net Min Emergency Rating - Spring | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW | SOLAR | SEASON_NET_MIN_EMGY_RTG_SP | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit 2. Not Null | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS
Seasonal Ratings Summer | Solar | [6 empty] | Parameters - Solar |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Summer | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW | SOLAR | SEASON_NET_MAX_SUST_RTG_SM | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Summer > Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Sustainable Rating - Summer | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW | SOLAR | SEASON_NET_MIN_SUST_RTG_SM | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu | MMS
Seasonal Net Max Emergency Rating - Summer | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW | SOLAR | SEASON_NET_MAX_EMGY_RTG_SM | 1.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Summer > Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Emergency Rating - Summer | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW | SOLAR | SEASON_NET_MIN_EMGY_RTG_SM | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Ratings Fall | Solar | [6 empty] | Parameters - Solar |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Fall | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW | SOLAR | SEASON_NET_MAX_SUST_RTG_FL | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Sustainable Rating - Fall | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW | SOLAR | SEASON_NET_MIN_SUST_RTG_FL | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall. >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Max Emergency Rating - Fall | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW | SOLAR | SEASON_NET_MAX_EMGY_RTG_FL | 1.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Fall > Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Emergency Rating - Fall | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW | SOLAR | SEASON_NET_MIN_EMGY_RTG_FL | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Ratings Winter | Solar | [6 empty] | Parameters - Solar |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Winter | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW | SOLAR | SEASON_NET_MAX_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Sustainable Rating - Winter | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW | SOLAR | SEASON_NET_MIN_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Max Emergency Rating - Winter | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW | SOLAR | SEASON_NET_MAX_EMGY_RTG_WT | 1.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Winter > Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Emergency Rating - Winter | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW | SOLAR | SEASON_NET_MIN_EMGY_RTG_WT | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES | Solar | [6 empty] | Parameters - Solar |  | Not in table | Not in table
0°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
5°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
10°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
15°f | Solar | [5 empty] | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
20°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
25°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
30°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
35°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
40°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
45°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
50°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
55°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
60°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
65°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
70°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
75°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
80°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
85°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
90°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
95°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
100°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
105°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
110°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
115°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
120°f | Solar | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - Solar | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Parameters - ESG Injections | ESG | [6 empty] | Parameters - ESG Injections |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type Selected is 'GEN' where GEN is non-CC non-wind Generation Resources. | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,MMS,NMMS
Generator Details | ESG | [6 empty] | Parameters - ESG Injections |  | Not in table | Not in table
Unit Name | ESG | 03/09/2012 Correct DB Field |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | List | ESGUNIT | UNIT_NAME_INJ UNIT_NAME | 1. Not Null. 2. Must not exceed 4 characters for Jointly Owned Units 3. Maximum of 8 character allowed | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | Automatic | ESGUNIT & DERATING | UNIT_CODE_INJ | 1. Not Null. 2. Enter Site Code and Unit Name for this field (Sitecode_Unit Name) 3. All letters must be capital | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
ESG Parameter Type | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | Automatic | ESGUNIT | ESG_TYPE_ |  | Required Injection/Withdrawing | R | Character | B,DVB
Reasonability Limits | ESG | [6 empty] | Parameters - ESG Injections |  | Not in table | Not in table
High Reasonability Limit | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW | ESGUNIT | HR_LMT | 1. High Reasonability Limit >0 2. HighReasonabilityLimit >= LowReasonablityLimit 3. Not Null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Low Reasonability Limit | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW | ESGUNIT | LR_LMT | 1. Low Reasonability Limit >0 for Non PUN sites 2. Low ReasonabilityLimit <= High ReasonablityLimit 3. PUN (Private Use Network) Sites LRL should equal zero or produce a Warning 4. Not Null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
High Reasonability Ramp Rate Limit | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW/min | ESGUNIT | HR_RAMPRATE_LMT | 1. High Reasonability Ramp Rate Limit >= Low Reasonability Ramp Rate Limit. 2. Not null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS
Low Reasonability Ramp Rate Limit | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW/min | ESGUNIT | LR_RAMP_RATE_LMT | 1. Low Reasonability Ramp Rate Limit >=0. 2. Not null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS
Seasonal Ratings Spring | ESG | [6 empty] | Parameters - ESG Injections |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Spring | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW | ESGUNIT | SEASON_NET_MAX_SUST_RTG_SP | 1.Seasonal Net Max Sustainable Rating - Spring >= Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Spring > Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS
Seasonal Net Min Sustainable Rating - Spring | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW | ESGUNIT | SEASON_NET_MIN_SUST_RTG_SP | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS
Seasonal Net Max Emergency Rating - Spring | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW | ESGUNIT | SEASON_NET_MAX_EMGY_RTG_SP | 1.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS
Seasonal Net Min Emergency Rating - Spring | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW | ESGUNIT | SEASON_NET_MIN_EMGY_RTG_SP | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit 2. Not Null | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS
Seasonal Ratings Summer | ESG | [6 empty] | Parameters - ESG Injections |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Summer | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW | ESGUNIT | SEASON_NET_MAX_SUST_RTG_SM | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Summer > Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Sustainable Rating - Summer | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW | ESGUNIT | SEASON_NET_MIN_SUST_RTG_SM | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu | MMS
Seasonal Net Max Emergency Rating - Summer | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW | ESGUNIT | SEASON_NET_MAX_EMGY_RTG_SM | 1.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Summer > Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Emergency Rating - Summer | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW | ESGUNIT | SEASON_NET_MIN_EMGY_RTG_SM | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Ratings Fall | ESG | [6 empty] | Parameters - ESG Injections |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Fall | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW | ESGUNIT | SEASON_NET_MAX_SUST_RTG_FL | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Sustainable Rating - Fall | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW | ESGUNIT | SEASON_NET_MIN_SUST_RTG_FL | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall. >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Max Emergency Rating - Fall | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW | ESGUNIT | SEASON_NET_MAX_EMGY_RTG_FL | 1.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Fall > Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Emergency Rating - Fall | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW | ESGUNIT | SEASON_NET_MIN_EMGY_RTG_FL | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Ratings Winter | ESG | [6 empty] | Parameters - ESG Injections |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Winter | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW | ESGUNIT | SEASON_NET_MAX_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Sustainable Rating - Winter | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW | ESGUNIT | SEASON_NET_MIN_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Max Emergency Rating - Winter | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW | ESGUNIT | SEASON_NET_MAX_EMGY_RTG_WT | 1.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Winter > Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Emergency Rating - Winter | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW | ESGUNIT | SEASON_NET_MIN_EMGY_RTG_WT | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES | ESG | [6 empty] | Parameters - ESG Injections |  | Not in table | Not in table
0°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
5°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
10°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
15°f | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
20°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
25°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
30°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
35°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
40°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
45°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
50°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
55°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
60°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
65°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
70°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
75°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
80°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
85°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
90°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
95°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
100°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
105°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
110°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
115°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
120°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Injections | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Parameters - ESG Withdrawing | ESG | [6 empty] | Parameters - ESG Withdrawing |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type Selected is 'GEN' where GEN is non-CC non-wind Generation Resources. | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,MMS,NMMS
Generator Details | ESG | [6 empty] | Parameters - ESG Withdrawing |  | Not in table | Not in table
Unit Name | ESG | Do not show Message on Audit or Delta |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | List | ESGUNIT | UNIT_NAME | 1. Not Null. 2. Must not exceed 4 characters for Jointly Owned Units 3. Maximum of 8 character allowed | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | Automatic | ESGUNIT & DERATING | UNIT_CODE | 1. Not Null. 2. Enter Site Code and Unit Name for this field (Sitecode_Unit Name) 3. All letters must be capital | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
ESG Parameter Type | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | Automatic | ESGUNIT | ESG_TYPE
Reasonability Limits | ESG | [6 empty] | Parameters - ESG Withdrawing |  | Not in table | Not in table
High Reasonability Limit | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW | ESGUNIT | HR_LMT | 1. High Reasonability Limit >0 2. HighReasonabilityLimit >= LowReasonablityLimit 3. Not Null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Low Reasonability Limit | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW | ESGUNIT | LR_LMT | 1. Low Reasonability Limit >0 for Non PUN sites 2. Low ReasonabilityLimit <= High ReasonablityLimit 3. PUN (Private Use Network) Sites LRL should equal zero or produce a Warning 4. Not Null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
High Reasonability Ramp Rate Limit | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW/min | ESGUNIT | HR_RAMPRATE_LMT | 1. High Reasonability Ramp Rate Limit >= Low Reasonability Ramp Rate Limit. 2. Not null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS
Storage High Reasonability Ramp Rate Limit | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW/min | ESGUNIT | CHG_EFF_COEFF_PER_ENG_LOST_DUR_CHARG
Low Reasonability Ramp Rate Limit | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW/min | ESGUNIT | LR_RAMP_RATE_LMT | 1. Low Reasonability Ramp Rate Limit >=0. 2. Not null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS
StorageLow Reasonability Ramp Rate Limit | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW | ESGUNIT | STRG_LR_RAMP_RATE_LMT
Seasonal Ratings Spring | ESG | [6 empty] | Parameters - ESG Withdrawing |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Spring | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW | ESGUNIT | SEASON_NET_MAX_SUST_RTG_SP | 1.Seasonal Net Max Sustainable Rating - Spring >= Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Spring > Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS
Seasonal Net Min Sustainable Rating - Spring | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW | ESGUNIT | SEASON_NET_MIN_SUST_RTG_SP | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS
Seasonal Net Max Emergency Rating - Spring | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW | ESGUNIT | SEASON_NET_MAX_EMGY_RTG_SP | 1.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS
Seasonal Net Min Emergency Rating - Spring | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW | ESGUNIT | SEASON_NET_MIN_EMGY_RTG_SP | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit 2. Not Null | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS
Seasonal Ratings Summer | ESG | [6 empty] | Parameters - ESG Withdrawing |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Summer | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW | ESGUNIT | SEASON_NET_MAX_SUST_RTG_SM | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Summer > Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Sustainable Rating - Summer | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW | ESGUNIT | SEASON_NET_MIN_SUST_RTG_SM | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu | MMS
Seasonal Net Max Emergency Rating - Summer | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW | ESGUNIT | SEASON_NET_MAX_EMGY_RTG_SM | 1.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Summer > Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Emergency Rating - Summer | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW | ESGUNIT | SEASON_NET_MIN_EMGY_RTG_SM | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Ratings Fall | ESG | [6 empty] | Parameters - ESG Withdrawing |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Fall | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW | ESGUNIT | SEASON_NET_MAX_SUST_RTG_FL | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Sustainable Rating - Fall | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW | ESGUNIT | SEASON_NET_MIN_SUST_RTG_FL | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall. >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Max Emergency Rating - Fall | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW | ESGUNIT | SEASON_NET_MAX_EMGY_RTG_FL | 1.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Fall > Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Emergency Rating - Fall | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW | ESGUNIT | SEASON_NET_MIN_EMGY_RTG_FL | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Ratings Winter | ESG | [6 empty] | Parameters - ESG Withdrawing |  | Not in table | Not in table
Seasonal Net Max Sustainable Rating - Winter | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW | ESGUNIT | SEASON_NET_MAX_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Sustainable Rating - Winter | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW | ESGUNIT | SEASON_NET_MIN_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Max Emergency Rating - Winter | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW | ESGUNIT | SEASON_NET_MAX_EMGY_RTG_WT | 1.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Winter > Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
Seasonal Net Min Emergency Rating - Winter | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW | ESGUNIT | SEASON_NET_MIN_EMGY_RTG_WT | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS
UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES | ESG | [6 empty] | Parameters - ESG Withdrawing |  | Not in table | Not in table
0°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
5°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
10°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
15°f | ESG | [5 empty] | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
20°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
25°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
30°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
35°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
40°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
45°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
50°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
55°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
60°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
65°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
70°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
75°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
80°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
85°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
90°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
95°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
100°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
105°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
110°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
115°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
120°f | ESG | 03/09/2012 Updated Validation |  |  |  |  | ADD 04/2012 | Parameters - ESG Withdrawing | MW | DERATING | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Operational Parameters - Solar | Solar | [6 empty] | Operational Parameters - Solar |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Resource Type Selected is 'WIND units' | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | MMS,NMMS
Unit Name | Solar | Do not show Message on Audit or Delta |  |  |  |  | ADD 04/2012 | Operational Parameters - Solar |  | SOLAR | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Solar | [5 empty] | ADD 04/2012 | Operational Parameters - Solar |  | SOLAR | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
RESOURCE PARAMETERS | Solar | [6 empty] | Operational Parameters - Solar |  | Not in table | Not in table
Minimum On Line Time | Solar | Check |  |  |  |  | ADD 04/2012 | Operational Parameters - Solar | hours | SOLAR | MIN_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum On Line Time >= 0 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Minimum Off Line Time | Solar | Check |  |  |  |  | ADD 04/2012 | Operational Parameters - Solar | hours | SOLAR | MIN_OFFLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum Off Line Time >= 0 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Hot Start Time | Solar | Corrected |  |  |  |  | ADD 04/2012 | Operational Parameters - Solar | hours | SOLAR | HOTSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot Start Time >= 0 3. Hot Start Time <= Intermediate Start Time | O | Integer | B,DVB | Angela Moy/Jamil Daouk | NMMS
Intermediate Start Time | Solar | Corrected |  |  |  |  | ADD 04/2012 | Operational Parameters - Solar | hours | SOLAR | INTERMSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate Start Time >= 0 3. Cold Start Time >= Intermediate Start Time >= Hot Start Time | O | Integer | B,DVB | Angela Moy/Jamil Daouk | NMMS
Cold Start Time | Solar | Corrected |  |  |  |  | ADD 04/2012 | Operational Parameters - Solar | hours | SOLAR | COLDSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Cold Start Time >= 0 3. Cold Start Time >= Intermediate Start Time | O | Integer | B,DVB | Angela Moy/Jamil Daouk | NMMS
Max Weekly Starts | Solar | Check |  |  |  |  | ADD 04/2012 | Operational Parameters - Solar |  | SOLAR | MAXWKLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Integer | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
Max On Line Time | Solar | Corrected |  |  |  |  | ADD 04/2012 | Operational Parameters - Solar | hours | SOLAR | MAX_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Integer | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
Max Daily Starts | Solar | Check |  |  |  |  | ADD 04/2012 | Operational Parameters - Solar |  | SOLAR | MAXDLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Daily Start >= 0 3. Max Daily Start <= 999 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Max Weekly Energy | Solar | Corrected |  |  |  |  | ADD 04/2012 | Operational Parameters - Solar | MWh | SOLAR | MAXWKLYENRGY |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Energy >= 0 3. Max Weekly Energy < 1e10 | R | Numeric | B,DVB | Lin Xu | MMS,NMMS
Hot-to-Intermediate Time | Solar | Check |  |  |  |  | ADD 04/2012 | Operational Parameters - Solar | hours | SOLAR | HOT_TO_INTMDT_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot-to-Intermediate Time >= 0 | R | Integer | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
Intermediate-to-Cold Time | Solar | Check |  |  |  |  | ADD 04/2012 | Operational Parameters - Solar | hours | SOLAR | INTMDT_TO_COLD_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate-to-Cold Time >= 0 | R | Integer | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
Operational Parameters - Solar - NRRC | Solar | [6 empty] | Operational Parameters - Solar - NRRC |  | Not in table | Not in table
Generator Details | Solar | [6 empty] | Operational Parameters - Solar - NRRC |  | Not in table | Not in table
Unit Name | Solar | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Operational Parameters - Solar - NRRC | List | SOLAR | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Solar | [5 empty] | ADD 02/2012 | Operational Parameters - Solar - NRRC | List | RAMP_RATES_NRRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Normal Ramp Rate Curve | Solar | [6 empty] | Operational Parameters - Solar - NRRC |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit.
MW Number | Solar | [6 empty] | Operational Parameters - Solar - NRRC
NRRC Code | Solar | [5 empty] | ADD 02/2012 | Operational Parameters - Solar - NRRC |  | RAMP_RATES_NRRC | UNIT_MW_NRRC |  | This Field is Not in the RARF: Capture Unit Code and MW Number and prepopulate this field with UNIT_CODE_MW_NUMBER_NRRC. | R | Character
NRRC MW | Solar | PHASE II Updated 03/06/2012 Added Step 5 and 6 |  |  |  |  | ADD 04/2012 | Operational Parameters - Solar - NRRC | MW | RAMP_RATES_NRRC | MW_NUMBER_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric | B,DVB | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk | NMMS
Upward Ramprate | Solar | Check |  |  |  |  | ADD 04/2012 | Operational Parameters - Solar - NRRC | MW/min | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | Lin Xu/Kittipong | MMS,NMMS
Downward Ramprate | Solar | Check |  |  |  |  | ADD 04/2012 | Operational Parameters - Solar - NRRC | MW/min | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | Lin Xu/Kittipong | MMS,NMMS
Operational Parameters - Solar - ERRC | Solar | [6 empty] | Operational Parameters - Solar- ERRC |  | Not in table | Not in table
Generator Details | Solar | [6 empty] | Operational Parameters - Solar- ERRC |  | Not in table | Not in table
Unit Name | Solar | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Operational Parameters - Solar- ERRC | List | SOLAR | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | Solar | [5 empty] | ADD 02/2012 | Operational Parameters - Solar- ERRC | List | RAMP_RATES_ERRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Emergency Ramp Rate Curve | Solar | [6 empty] | Operational Parameters - Solar- ERRC |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit.
MW Number | Solar | [6 empty] | Operational Parameters - Solar- ERRC
ERRC Code | Solar | [5 empty] | ADD 02/2012 | Operational Parameters - Solar- ERRC |  | RAMP_RATES_ERRC | UNIT_MW_ERRC |  | Capture Unit Code and MW Number and prepopulate this field with Unit Name_MW_NUMBER_ERRC. | R | Character
ERRC MW | Solar | PHASE II Updated 03/06/2012 Added Step 5 and 6 |  |  |  |  | ADD 04/2012 | Operational Parameters - Solar- ERRC | MW | RAMP_RATES_ERRC | MW_NUMBER_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric | B,DVB | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk | NMMS
Upward Ramprate | Solar | Check |  |  |  |  | ADD 04/2012 | Operational Parameters - Solar- ERRC | MW/min | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | Lin Xu/Kittipong | MMS,NMMS
Downward Ramprate | Solar | Check |  |  |  |  | ADD 04/2012 | Operational Parameters - ERRC | MW/min | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | Lin Xu/Kittipong | MMS,NMMS
Oper Parameters - ESG Injections | ESG | [6 empty] | Oper Parameters - ESG Injections |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Resource Type Selected is 'Solar units' | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | MMS,NMMS
Unit Name | ESG | Do not show Message on Audit or Delta |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Injections | List | ESGUNIT | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | ESG | [5 empty] | ADD 04/2012 | Oper Parameters - ESG Injections | Automatic | ESGUNIT | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
ESG Parameter Type | ESG | [5 empty] | ADD 04/2012 | Oper Parameters - ESG Injections | Automatic | ESGUNIT | ESG_TYPE
RESOURCE PARAMETERS | ESG | [6 empty] | Oper Parameters - ESG Injections |  | Not in table | Not in table
Minimum On Line Time | ESG | Check |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Injections | hours | ESGUNIT | MIN_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum On Line Time >= 0 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Minimum Off Line Time | ESG | Check |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Injections | hours | ESGUNIT | MIN_OFFLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum Off Line Time >= 0 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Hot Start Time | ESG | Corrected |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Injections | hours | ESGUNIT | HOTSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot Start Time >= 0 3. Hot Start Time <= Intermediate Start Time | O | Integer | B,DVB | Angela Moy/Jamil Daouk | NMMS
Intermediate Start Time | ESG | Corrected |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Injections | hours | ESGUNIT | INTERMSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate Start Time >= 0 3. Cold Start Time >= Intermediate Start Time >= Hot Start Time | O | Integer | B,DVB | Angela Moy/Jamil Daouk | NMMS
Cold Start Time | ESG | Corrected |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Injections | hours | ESGUNIT | COLDSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Cold Start Time >= 0 3. Cold Start Time >= Intermediate Start Time | O | Integer | B,DVB | Angela Moy/Jamil Daouk | NMMS
Max Weekly Starts | ESG | Check |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Injections |  | ESGUNIT | MAXWKLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Integer | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
Max On Line Time | ESG | Corrected |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Injections | hours | ESGUNIT | MAX_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Integer | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
Max Daily Starts | ESG | Check |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Injections |  | ESGUNIT | MAXDLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Daily Start >= 0 3. Max Daily Start <= 999 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Max Weekly Energy | ESG | Corrected |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Injections | MWh | ESGUNIT | MAXWKLYENRGY |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Energy >= 0 3. Max Weekly Energy < 1e10 | R | Numeric | B,DVB | Lin Xu | MMS,NMMS
Hot-to-Intermediate Time | ESG | Check |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Injections | hours | ESGUNIT | HOT_TO_INTMDT_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot-to-Intermediate Time >= 0 | R | Integer | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
Intermediate-to-Cold Time | ESG | Check |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Injections | hours | ESGUNIT | INTMDT_TO_COLD_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate-to-Cold Time >= 0 | R | Integer | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
Operational Parameters - ESG Injections -NRRC | ESG | [6 empty] | Operational Parameters - ESG Injections -NRRC |  | Not in table | Not in table
Generator Details | ESG | [6 empty] | Oper Parameters - ESG Injections -NRRC |  | Not in table | Not in table
Unit Name | ESG | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Oper Parameters - ESG Injections -NRRC | List | RAMP_RATES_NRRC | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Dispatch Asset Code (Provided by ERCOT) | ESG | [5 empty] | ADD 04/2012 | Oper Parameters - ESG Injections -NRRC | List | RAMP_RATES_NRRC | DISPATCH_ASSET_CODE |  |  | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
Resource Name (Unit Code/Mnemonic) | ESG | [5 empty] | ADD 02/2012 | Oper Parameters - ESG Injections -NRRC | Automatic | RAMP_RATES_NRRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
ESG Parameter Type | ESG | [6 empty] | Oper Parameters - ESG Injections -NRRC | Automatic | RAMP_RATES_NRRC | ESG_TYPE
Normal Ramp Rate Curve | ESG | [6 empty] | Oper Parameters - ESG Injections -NRRC |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit.
MW Number | ESG | [6 empty] | Oper Parameters - ESG Injections -NRRC
NRRC Code | ESG | [5 empty] | ADD 02/2012 | Oper Parameters - ESG Injections -NRRC |  | RAMP_RATES_NRRC | UNIT_MW_NRRC |  | Capture Unit Code and MW Number and prepopulate this field with Unit Name_MW_NUMBER_ERRC. | R | Character
NRRC MW | ESG | PHASE II Updated 03/06/2012 Added Step 5 and 6 |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Injections -NRRC | MW | RAMP_RATES_NRRC | MW_NUMBER_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric | B,DVB | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk | NMMS
Upward Ramprate | ESG | Check |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Injections -NRRC | MW/min | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | Lin Xu/Kittipong | MMS,NMMS
Downward Ramprate | ESG | Check |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Injections -NRRC | MW/min | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | Lin Xu/Kittipong | MMS,NMMS
Oper Parameters - ESG Injections - ERRC | ESG | [6 empty] | Oper Parameters - ESG Injections -ERRC |  | Not in table | Not in table
Generator Details | ESG | [6 empty] | Oper Parameters - ESG Injections -ERRC |  | Not in table | Not in table
Unit Name | ESG | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Oper Parameters - ESG Injections -ERRC | List | RAMP_RATES_ERRC | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Dispatch Asset Code (Provided by ERCOT) | ESG | [5 empty] | ADD 04/2012 | Oper Parameters - ESG Injections -ERRC | List | RAMP_RATES_ERRC | DISPATCH_ASSET_CODE |  |  | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
Resource Name (Unit Code/Mnemonic) | ESG | [5 empty] | ADD 02/2012 | Oper Parameters - ESG Injections -ERRC | Automatic | RAMP_RATES_ERRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
ESG Parameter Type | ESG | [5 empty] | ADD 02/2012 | Oper Parameters - ESG Injections -ERRC | Automatic | RAMP_RATES_ERRC | ESG_TYPE
Emergency Ramp Rate Curve | ESG | [6 empty] | Oper Parameters - ESG Injections -ERRC |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit.
MW Number | ESG | [6 empty] | Oper Parameters - ESG Injections -ERRC
ERRC Code | ESG | [5 empty] | ADD 02/2012 | Oper Parameters - ESG Injections -ERRC |  | RAMP_RATES_ERRC | UNIT_MW_ERRC |  | Capture Unit Code and MW Number and prepopulate this field with Unit Name_MW_NUMBER_ERRC. | R | Character
ERRC MW | ESG | PHASE II Updated 03/06/2012 Added Step 5 and 6 |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Injections -ERRC | MW | RAMP_RATES_ERRC | MW_NUMBER_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric | B,DVB | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk | NMMS
Upward Ramprate | ESG | Check |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Injections -ERRC | MW/min | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | Lin Xu/Kittipong | MMS,NMMS
Downward Ramprate | ESG | Check |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Injections -ERRC | MW/min | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | Lin Xu/Kittipong | MMS,NMMS
Oper Parameters - ESG Withdrawing | ESG | [6 empty] | Oper Parameters - ESG Withdrawing |  | Not in table | Not in table |  |  | C |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | MMS,NMMS
Unit Name | ESG | Do not show Message on Audit or Delta |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing |  | ESGUNIT | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Resource Name (Unit Code/Mnemonic) | ESG | [5 empty] | ADD 04/2012 | Oper Parameters - ESG Withdrawing |  | ESGUNIT | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
ESG Parameter Type | ESG | [5 empty] | ADD 04/2012 | Oper Parameters - ESG Withdrawing | Automatic | ESGUNIT | ESG_TYPE
RESOURCE PARAMETERS | ESG | [6 empty] | Oper Parameters - ESG Withdrawing |  | Not in table | Not in table
Minimum On Line Time | ESG | Check |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing | hours | ESGUNIT | MIN_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum On Line Time >= 0 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Minimum Off Line Time | ESG | Check |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing | hours | ESGUNIT | MIN_OFFLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum Off Line Time >= 0 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Hot Start Time | ESG | Corrected |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing | hours | ESGUNIT | HOTSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot Start Time >= 0 3. Hot Start Time <= Intermediate Start Time | O | Integer | B,DVB | Angela Moy/Jamil Daouk | NMMS
Intermediate Start Time | ESG | Corrected |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing | hours | ESGUNIT | INTERMSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate Start Time >= 0 3. Cold Start Time >= Intermediate Start Time >= Hot Start Time | O | Integer | B,DVB | Angela Moy/Jamil Daouk | NMMS
Cold Start Time | ESG | Corrected |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing | hours | ESGUNIT | COLDSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Cold Start Time >= 0 3. Cold Start Time >= Intermediate Start Time | O | Integer | B,DVB | Angela Moy/Jamil Daouk | NMMS
Max Weekly Starts | ESG | Check |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing |  | ESGUNIT | MAXWKLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Integer | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
Max On Line Time | ESG | Corrected |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing | hours | ESGUNIT | MAX_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Integer | B,DVB | Lin Xu/Jamil Daouk | MMS,NMMS
Max Daily Starts | ESG | Check |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing |  | ESGUNIT | MAXDLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Daily Start >= 0 3. Max Daily Start <= 999 | R | Integer | B,DVB | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Max Weekly Energy | ESG | Corrected |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing | MWh | ESGUNIT | MAXWKLYENRGY |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Energy >= 0 3. Max Weekly Energy < 1e10 | R | Numeric | B,DVB | Lin Xu | MMS,NMMS
Hot-to-Intermediate Time | ESG | Check |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing | hours | ESGUNIT | HOT_TO_INTMDT_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot-to-Intermediate Time >= 0 | R | Integer | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
Intermediate-to-Cold Time | ESG | Check |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing | hours | ESGUNIT | INTMDT_TO_COLD_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate-to-Cold Time >= 0 | R | Integer | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
Oper Parameters - ESG Withdrawing - NRRC | ESG | [6 empty] | Oper Parameters - ESG Withdrawing - NRRC |  | Not in table | Not in table | [5 empty] | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | MMS,NMMS
Generator Details | ESG | [6 empty] | Oper Parameters - ESG Withdrawing - NRRC |  | Not in table | Not in table
Unit Name | ESG | Do not show Message on Audit or Delta |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing - NRRC | List | RAMP_RATES_NRRC | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Dispatch Asset Code (Provided by ERCOT) | ESG | [5 empty] | ADD 04/2012 | Oper Parameters - ESG Withdrawing - NRRC | List | RAMP_RATES_NRRC | DISPATCH_ASSET_CODE |  |  | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
Resource Name (Unit Code/Mnemonic) | ESG | [5 empty] | ADD 02/2012 | Oper Parameters - ESG Withdrawing - NRRC | Automatic | RAMP_RATES_NRRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
ESG Parameter Type | ESG | [5 empty] | ADD 02/2012 | Oper Parameters - ESG Withdrawing - NRRC | Automatic | RAMP_RATES_NRRC | ESG_TYPE
Normal Ramp Rate Curve | ESG | [6 empty] | Oper Parameters - ESG Withdrawing - NRRC |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit.
MW Number | ESG | [6 empty] | Oper Parameters - ESG Withdrawing - NRRC
NRRC Code | ESG | [5 empty] | ADD 02/2012 | Oper Parameters - ESG Withdrawing - NRRC |  | RAMP_RATES_NRRC | UNIT_MW_NRRC |  | Capture Unit Code and MW Number and prepopulate this field with Unit Name_MW_NUMBER_ERRC. | R | Character
NRRC MW | ESG | PHASE II Updated 03/06/2012 Added Step 5 and 6 |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing - NRRC | MW | RAMP_RATES_NRRC | MW_NUMBER_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric | B,DVB | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk | NMMS
Upward Ramprate | ESG | Check |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing - NRRC | MW/min | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | Lin Xu/Kittipong | MMS,NMMS
Downward Ramprate | ESG | Check |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing - NRRC | MW/min | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | Lin Xu/Kittipong | MMS,NMMS
Oper Parameters - ESG Withdrawing - ERRC | ESG | [6 empty] | Oper Parameters - ESG Withdrawing - ERRC |  | Not in table | Not in table | [5 empty] | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | MMS,NMMS
Generator Details | ESG | [6 empty] | Oper Parameters - ESG Withdrawing - ERRC |  | Not in table | Not in table
Unit Name | ESG | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Oper Parameters - ESG Withdrawing - ERRC | List | RAMP_RATES_ERRC | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Dispatch Asset Code (Provided by ERCOT) | ESG | [5 empty] | ADD 04/2012 | Oper Parameters - ESG Withdrawing - ERRC | List | RAMP_RATES_ERRC | DISPATCH_ASSET_CODE |  |  | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0
Resource Name (Unit Code/Mnemonic) | ESG | [5 empty] | ADD 02/2012 | Oper Parameters - ESG Withdrawing - ERRC | Automatic | RAMP_RATES_ERRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
ESG Parameter Type | ESG | [5 empty] | ADD 02/2012 | Oper Parameters - ESG Withdrawing - ERRC | Automatic | RAMP_RATES_ERRC | ESG_TYPE
Emergency Ramp Rate Curve | ESG | [6 empty] | Oper Parameters - ESG Withdrawing - ERRC |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit.
MW Number | ESG | [6 empty] | Oper Parameters - ESG Withdrawing - ERRC
ERRC Code | ESG | [5 empty] | ADD 02/2012 | Oper Parameters - ESG Withdrawing - ERRC |  | RAMP_RATES_ERRC | UNIT_MW_ERRC |  | Capture Unit Code and MW Number and prepopulate this field with Unit Name_MW_NUMBER_ERRC. | R | Character
ERRC MW | ESG | PHASE II Updated 03/06/2012 Added Step 5 and 6 |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing - ERRC | MW | RAMP_RATES_ERRC | MW_NUMBER_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric | B,DVB | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk | NMMS
Upward Ramprate | ESG | Check |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing - ERRC | MW/min | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | Lin Xu/Kittipong | MMS,NMMS
Downward Ramprate | ESG | Check |  |  |  |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing - ERRC | MW/min | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric | B,DVB | Lin Xu/Kittipong | MMS,NMMS
Reactive Capability - Solar | Solar | [6 empty] | Reactive Capability - Solar |  | Not in table | Not in table
GENERATOR DETAILS | Solar | [6 empty] | Reactive Capability - Solar |  | Not in table | Not in table
Unit Name | Solar | Do not show Message on Audit or Delta |  |  |  |  | ADD 04/2012 | Reactive Capability - Solar | List | REACT_CAP_SOLAR | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B
Resource Name (Unit Code/Mnemonic) | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | Automatic | REACT_CAP_SOLAR | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | Character | B,DVB
REACTIVE CAPABILITY CURVES DETAILS | Solar | [6 empty] | Reactive Capability - Solar |  | Not in table | Not in table
Reactive Capability Data Provided Below is Gross/Net Values? | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | List | REACT_CAP_SOLAR | REACT_CAPB_DATA_GROSS_NET_VAL
Reactive Capability Data Provided Below is from NDCRC Test Data? | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | Y/N | REACT_CAP_SOLAR | REACT_CAPB_NDCRC_TEST_DATA |  | Select from the list: Y or N
If Reactive Capability Data Provided Below Is From Ndcrc Test Data Then Enter The Date On Which The Test Was Performed. | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | mm/dd/yyyy | REACT_CAP_SOLAR | REACT_CAPB_NDCRC_TEST_DATA_DT |  | This field is optional. Format should be: MM/DD/YYYY
MW1 | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | MW | REACT_CAP_SOLAR | MW1 |  | 1. MW1 >=0 .1 2. MW1<MW2. 3. X(1) <= WMN(Unit Minimal output) where X(1) represents MW1( Generate a Warning Only when Business Rule#2 fails) | R | Numeric | B,DVB
Lagging MVAR limit associated with MW1 output | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | MVAR | REACT_CAP_SOLAR | MVAR1LAG |  | 1. Lagging MVAR limit associated with MW1 output >=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB
Leading MVAR limit associated with MW1 output | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | MVAR | REACT_CAP_SOLAR | MVAR1LEAD |  | 1. Leading MVAR limit associated with MW1 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R | Numeric | B,DVB
MW2 | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | MW | REACT_CAP_SOLAR | MW2 |  | 1. MW2>0 2. MW2<MW3 | R | Numeric | B,DVB
Lagging MVAR limit associated with MW2 output | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | MVAR | REACT_CAP_SOLAR | MVAR2LAG |  | 1.Lagging MVAR limit associated with MW2 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB
Leading MVAR limit associated with MW2 output | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | MVAR | REACT_CAP_SOLAR | MVAR2LEAD |  | 1. Leading MVAR limit associated with MW2 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R | Numeric | B,DVB
MW3 | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | MW | REACT_CAP_SOLAR | MW3 |  | 1. MW3 >0 2. MW3<MW4 | R | Numeric | B,DVB
Lagging MVAR limit associated with MW3 output | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | MVAR | REACT_CAP_SOLAR | MVAR3LAG |  | 1. Lagging MVAR limit associated with MW3 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB
Leading MVAR limit associated with MW3 output | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | MVAR | REACT_CAP_SOLAR | MVAR3LEAD |  | 1.Leading MVAR limit associated with MW3 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R | Numeric | B,DVB
MW4 | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | MW | REACT_CAP_SOLAR | MW4 |  | 1. MW4 >0 2. MW4<MW5 3. X(n) > = WMX (Unit Max output) where n is the last MW value in the curve. If the curve has 4 points, X(n) is X(4) [ Generate a Warning Only When Business Rule#2 Fails] | R | Numeric | B,DVB
Lagging MVAR limit associated with MW4 output | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | MVAR | REACT_CAP_SOLAR | MVAR4LAG |  | 1. Lagging MVAR limit associated with MW4 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB
Leading MVAR limit associated with MW4 output | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | MVAR | REACT_CAP_SOLAR | MVAR4LEAD |  | 1.Leading MVAR limit associated with MW4 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R | Numeric | B,DVB
MW5 - Unity Power Factor | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | MW | REACT_CAP_SOLAR | MW5UNITYPF
If hydrogen cooled, indicate hydrogen pressure (psi) associated with your Reactive Curve submitted for ERCOT studies | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | PSI | GENERATION | HYDROCOOLED |  |  | O | Numeric | B
Net Maximum Leading Operating Capability | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | MVAR | REACT_CAP_SOLAR | NETMAXLEAD |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if < .3286(max capability in MW). | R | Float | B,DVB
Net Maximum Lagging Operating Capability | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | MVAR | REACT_CAP_SOLAR | NETMAXLAG |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if < .3286(max capability in MW). | R | Float | B,DVB
Has the Manufacturer's Capability Curve submitted? | Solar | [5 empty] | ADD 04/2012 | Reactive Capability - Solar | Y/N | REACT_CAP_SOLAR | MFR_CAP_CURVE
Reactive Capability -ESG | ESG | [5 empty] | ADD 04/2012 | Reactive Capability -ESG |  | Not in table | Not in table
GENERATOR DETAILS | ESG | [6 empty] | Reactive Capability -ESG |  | Not in table | Not in table
Unit Name | ESG | Do not show Message on Audit or Delta |  |  |  |  | ADD 04/2012 | Reactive Capability -ESG | List | REACT_CAP_ESG | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B
Resource Name (Unit Code/Mnemonic) | ESG | [5 empty] | ADD 04/2012 | Reactive Capability -ESG | Automatic | REACT_CAP_ESG | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | Character | B,DVB
REACTIVE CAPABILITY CURVES DETAILS | ESG | [6 empty] | Reactive Capability -ESG |  | Not in table | Not in table
Reactive Capability Data Provided Below is Gross/Net Values? | ESG | [5 empty] | ADD 04/2012 | Reactive Capability -ESG | Y/N | REACT_CAP_ESG | REACT_CAPB_DATA_GROSS_NET_VAL
Reactive Capability Data Provided Below is from NDCRC Test Data? | ESG | [5 empty] | ADD 04/2012 | Reactive Capability -ESG | Y/N | REACT_CAP_ESG | REACT_CAPB_NDCRC_TEST_DATA
If Reactive Capability Data Provided Below Is From Ndcrc Test Data Then Enter The Date On Which The Test Was Performed. | ESG | [5 empty] | ADD 04/2012 | Reactive Capability -ESG | mm/dd/yyyy | REACT_CAP_ESG | REACT_CAPB_NDCRC_TEST_DATA_DT
MW1 | ESG | [5 empty] | ADD 04/2012 | Reactive Capability -ESG | MW | REACT_CAP_ESG | MW1 |  | 1. MW1 >=0 .1 2. MW1<MW2. 3. X(1) <= WMN(Unit Minimal output) where X(1) represents MW1( Generate a Warning Only when Business Rule#2 fails) | R | Numeric | B,DVB
Lagging MVAR limit associated with MW1 output | ESG | [5 empty] | ADD 04/2012 | Reactive Capability -ESG | MVAR | REACT_CAP_ESG | MVAR1LAG |  | 1. Lagging MVAR limit associated with MW1 output >=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB
Leading MVAR limit associated with MW1 output | ESG | [5 empty] | ADD 04/2012 | Reactive Capability -ESG | MVAR | REACT_CAP_ESG | MVAR1LEAD |  | 1. Leading MVAR limit associated with MW1 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R | Numeric | B,DVB
MW2 | ESG | [5 empty] | ADD 04/2012 | Reactive Capability -ESG | MW | REACT_CAP_ESG | MW2 |  | 1. MW2>0 2. MW2<MW3 | R | Numeric | B,DVB
Lagging MVAR limit associated with MW2 output | ESG | [5 empty] | ADD 04/2012 | Reactive Capability -ESG | MVAR | REACT_CAP_ESG | MVAR2LAG |  | 1.Lagging MVAR limit associated with MW2 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB
Leading MVAR limit associated with MW2 output | ESG | [5 empty] | ADD 04/2012 | Reactive Capability -ESG | MVAR | REACT_CAP_ESG | MVAR2LEAD |  | 1. Leading MVAR limit associated with MW2 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R | Numeric | B,DVB
MW3 | ESG | [5 empty] | ADD 04/2012 | Reactive Capability -ESG | MW | REACT_CAP_ESG | MW3 |  | 1. MW3 >0 2. MW3<MW4 | R | Numeric | B,DVB
Lagging MVAR limit associated with MW3 output | ESG | [5 empty] | ADD 04/2012 | Reactive Capability -ESG | MVAR | REACT_CAP_ESG | MVAR3LAG |  | 1. Lagging MVAR limit associated with MW3 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB
Leading MVAR limit associated with MW3 output | ESG | [5 empty] | ADD 04/2012 | Reactive Capability -ESG | MVAR | REACT_CAP_ESG | MVAR3LEAD |  | 1.Leading MVAR limit associated with MW3 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R | Numeric | B,DVB
MW4 | ESG | [5 empty] | ADD 04/2012 | Reactive Capability -ESG | MW | REACT_CAP_ESG | MW4 |  | 1. MW4 >0 2. MW4<MW5 3. X(n) > = WMX (Unit Max output) where n is the last MW value in the curve. If the curve has 4 points, X(n) is X(4) [ Generate a Warning Only When Business Rule#2 Fails] | R | Numeric | B,DVB
Lagging MVAR limit associated with MW4 output | ESG | [5 empty] | ADD 04/2012 | Reactive Capability -ESG | MVAR | REACT_CAP_ESG | MVAR4LAG |  | 1. Lagging MVAR limit associated with MW4 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric | B,DVB
Leading MVAR limit associated with MW4 output | ESG | [5 empty] | ADD 04/2012 | Reactive Capability -ESG | MVAR | REACT_CAP_ESG | MVAR4LEAD |  | 1.Leading MVAR limit associated with MW4 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R | Numeric | B,DVB
Maximum Leading Operating Capability | ESG | [5 empty] | ADD 04/2012 | Reactive Capability -ESG | MVAR | REACT_CAP_ESG | NETMAXLEAD
Maximum Lagging Operating Capability | ESG | [5 empty] | ADD 04/2012 | Reactive Capability -ESG | MVAR | REACT_CAP_ESG | NETMAXLAG
Has the Manufacturer's Capability Curve submitted? | ESG | [5 empty] | ADD 04/2012 | Reactive Capability -ESG | Y/N | REACT_CAP_ESG | MFR_CAP_CURVE |  | Select from the list: Y or N
Ownership - Solar | Solar | [6 empty] | Ownership - Solar |  | Not in table | Not in table
Generator Detail | Solar | [6 empty] | Ownership - Solar |  | Not in table | Not in table
Unit Name | Solar | Do not show Message on Audit or Delta |  |  |  |  | ADD 04/2012 | Ownership - Solar |  | OWNERSHIP | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B
Resource Name (Unit Code/Mnemonic) | Solar | [5 empty] | ADD 04/2012 | Ownership - Solar |  | OWNERSHIP | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | Character | B,DVB
Ownership Percentages | Solar | [6 empty] | Ownership - Solar |  | Not in table | Not in table |  | 2.All letters should be capital
Joint Ownership Code | Solar | [5 empty] | ADD 04/2012 | Ownership - Solar | Y/N | OWNERSHIP | J0CODE |  | 3. Should not allow spaces
Resource Entity Name | Solar | Update 03/13/2012 |  |  |  |  | ADD 04/2012 | Ownership - Solar |  | OWNERSHIP | MKT_PRTCPT |  | 1. Not null 2. Must match with the data existing in Siebel 3. Do not allow any special characters except spaces and dashes.
Resource Duns Number | Solar | [5 empty] | ADD 04/2012 | Ownership - Solar |  | OWNERSHIP | MKT_PRTCPT_DUNS
Fixed Ownership | Solar | [5 empty] | ADD 04/2012 | Ownership - Solar | % | OWNERSHIP | FIX_OWNRSHP_PCT
Master Owner (Y or N) | Solar | [5 empty] | ADD 04/2012 | Ownership - Solar | Y/N | OWNERSHIP | MASTR_OWNR_FLG
Ownership Start Date | Solar | 03/07/2012 Updated with Business Rule |  |  |  |  | ADD 04/2012 | Ownership - Solar | mm/dd/yyyy | OWNERSHIP | OWNR_START_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB
Ownership Start Date | Solar | 03/07/2012 Updated with Business Rule |  |  |  |  | ADD 04/2012 | Ownership - Solar | mm/dd/yyyy | OWNERSHIP | OWNR_END_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB
Ownership - ESG | ESG | [6 empty] | Ownership - ESG |  | Not in table | Not in table
Generator Detail | ESG | [6 empty] | Ownership - ESG |  | Not in table | Not in table
Unit Name | ESG | Do not show Message on Audit or Delta |  |  |  |  | ADD 04/2012 | Ownership - ESG | List | OWNERSHIP | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B
Resource Name (Unit Code/Mnemonic) | ESG | [5 empty] | ADD 04/2012 | Ownership - ESG | Automatic | OWNERSHIP | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | Character | B,DVB
Ownership Percentages | ESG | [6 empty] | Ownership - ESG |  | Not in table | Not in table |  | 2.All letters should be capital
Joint Ownership | ESG | [5 empty] | ADD 04/2012 | Ownership - ESG | Y/N | OWNERSHIP | J0CODE |  | 3. Should not allow spaces | R | Dropdown List
Resource Entity Name | ESG | Update 03/13/2012 |  |  |  |  | ADD 04/2012 | Ownership - ESG |  | OWNERSHIP | MKT_PRTCPT |  | 1. Not null 2. Must match with the data existing in Siebel 3. Do not allow any special characters except spaces and dashes. | C | Character | B,DVB
Resource Duns Number | ESG | [5 empty] | ADD 04/2012 | Ownership - ESG |  | OWNERSHIP | MKT_PRTCPT_DUNS |  | This field is Conditional : Required if single entity represents the Resource. This should be either 9 or 13 digit number | C | Integer | B,DVB
Fixed Ownership | ESG | [5 empty] | ADD 04/2012 | Ownership - ESG | Percent | OWNERSHIP | FIX_OWNRSHP_PCT
Master Owner (Y or N) | ESG | [5 empty] | ADD 04/2012 | Ownership - ESG | Y/N | OWNERSHIP | MASTR_OWNR_FLG
Ownership Start Date | ESG | 03/07/2012 Updated with Business Rule |  |  |  |  | ADD 04/2012 | Ownership - ESG | mm/dd/yyyy | OWNERSHIP | OWNR_START_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB
Ownership Start Date | ESG | 03/07/2012 Updated with Business Rule |  |  |  |  | ADD 04/2012 | Ownership - ESG | mm/dd/yyyy | OWNERSHIP | OWNR_END_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB
Planning - Solar | Solar | [6 empty] | Planning - Solar |  | Not in table | Not in table
GENERATION DETAILS | Solar | [6 empty] | Planning - Solar |  | Not in table | Not in table
Unit Name | Solar | Do not show Message on Audit or Delta |  |  |  |  | ADD 04/2012 | Planning - Solar |  | Solar | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B
Resource Name (Unit Code/Mnemonic) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar |  | Solar | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | B,DVB
INVERTER TYPE | Solar | [5 empty] | ADD 04/2012 | Planning - Solar |  | Solar | INVERTER_TYPE
PLANNING DETAILS | Solar | [6 empty] | Planning - Solar |  | Not in table | Not in table
What is the MVA base that the following data is based on? | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | MVA | Solar | MVABASE |  | 1) This field is required 2) Value must be Float 3) Generate a Warning if MVABASE > 2500 4)[ If MVABASE value is within +/- 25% range of Unit Name Plate Rating] OR [MVABASE value = 100, then it is OK.If MVABASE value is outside the +/- 25% range of Unit Name Plate Rating, then Generate a Warning that the MVABSE is outside the typical +/- 25% variation of unit name plate rating
What is the kV base that the following data is based on? | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | kV | Solar | KVBASE |  | 1) This field is required 2) Value must be >0 and <1000 3) Generate a Warning if KVBASE > 40 4) If KVBASE value is within +/- 25% range of Unit KV value in the unit-information tab then it is OK.If If KVBASE value is outside the typical +/- 25% variation of Unit KV value in the unit-information tab then Generate a Warning that the KVBASE is outside the typical +/- 25% variation of Unit KV value
Direct Axis Subtransient reactance, X"di (unsaturated) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | pu | Solar | DIRECT_AXIS_SUBSTNT_REACTANCE_UNSATURATED |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Direct Axis Transient reactance, X'di (unsaturated) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | pu | Solar | DIRECT_AXIS_TRANSNT_REACTANCE_UNSATURATED |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Positive Sequence Z (unsaturated) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | R in p.u. | Solar | POSITIVE_SEQ_Z_R_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1
Positive Sequence Z (unsaturated) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | X in p.u. | Solar | POSITIVE_SEQ_Z_X_UNSATURARTED_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Negative Sequence Z (unsaturated) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | R in p.u. | Solar | NEGATIVE_SEQ_Z_R_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning when value is > 1.0 P.U
Negative Sequence Z (unsaturated) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | X in p.u. | Solar | NEGATIVE_SEQ_Z_X_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Does Zero Sequence Z exist? | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | Y/N | Solar | DOES_ZERO_SEQ_EXIST |  |  | R | Dropdown List |  | Planning Team
Zero Sequence Z (unsaturated) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | R in p.u. | Solar | ZERO_SEQ_Z_R_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U
Zero Sequence Z (unsaturated) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | X in p.u. | Solar | ZERO_SEQ_Z_X_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Direct Axis Subtransient reactance, X"dv (saturated) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | p.u. | Solar | DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Direct Axis Transient reactance, X'dv (saturated) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | p.u. | Solar | DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Positive Sequence Z (saturated) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | R in p.u. | Solar | POSITIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1
Positive Sequence Z (saturated) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | X in p.u. | Solar | POSITIVE_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Negative Sequence Z (saturated) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | R in p.u. | Solar | NEGATIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1
Negative Sequence Z (saturated) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | X in p.u. | Solar | NEGATIVE_SEQ_Z_X-SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Zero Sequence Z (saturated) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | R in p.u. | Solar | ZERO_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U
Zero Sequence Z (saturated) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | X in p.u. | Solar | ZERO_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | p.u. | Solar | ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | p.u. | Solar | ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Zero Sequence Resistance In P.u. (100 Mva Base) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | p.u. | Solar | ZERO_SEQ_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Zero Sequence Reactance In P.u. (100 Mva Base) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | p.u. | Solar | ZERO_SEQ_Reactance_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Generator Auxiliary Load | Solar | [6 empty] | Planning - Solar |  | Not in table | Not in table
Average Amount of Auxiliary Real Power | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | MW | Solar | AUX_MWTOTAL |  | 1) This field is optional 2) Data type is float 3) Value must be < Parameters - GEN - High Reasonability Limit 4) Warn if value > (High Reasonability Limit) * .75 5) Error if value > (High Reasonability Limit) * .66
Average Amount of Auxiliary Reactive Power | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | MVAR | Solar | AUX_MVARTOTAL |  | 1) This field is optional 2) Data type is Float 3) Value must be < Reactive Capability - GEN - Maximum Lagging Operating Capability (MVAR) 4) Warn if value > ( Maximum Lagging Operating Capability) * .75 5) Error if value > ( Maximum Lagging Operating Capability) * .66
Auxiliary Load Power Factor | Solar | [5 empty] | ADD 04/2012 | Planning - Solar |  | Solar | AUX_LOAD_PWR_FACT
Generation Auxiliary Load Characteristics for MW Load | Solar | [6 empty] | Planning - Solar |  | Not in table | Not in table
Large Motor, percent of total MW load | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | % | Solar | LRG_MTR_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
Small Motor, percent of total MW load | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | % | Solar | SML_MTR_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
Resistive (Heating) Load, percent of total MW load | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | % | Solar | RESISTIVE_LOAD_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
Discharge Lighting, percent of total MW load | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | % | Solar | DISCHARGE LIGHT_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
Other, percent of total MW load | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | % | Solar | OTH_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
Generation Auxiliary Load Characteristics for MVAR Load | Solar | [6 empty] | Planning - Solar |  | Not in table | Not in table
Large Motor, percent of total MVAR load | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | % | Solar | LRG_MTR_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y'
Small Motor, percent of total MVAR load | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | % | Solar | SML_MTR_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y'
Discharge Lighting, percent of total MVAR load | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | % | Solar | DISCHARGE LIGHT_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y'
Other, percent of total MVAR load | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | % | Solar | OTH_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y'
INVERTER STEP-UP TRANSFORMER DATA | Solar | [6 empty] | Planning - Solar |  | Not in table | Not in table
High Side Voltage Level (nominal) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | kV | Solar | HIGH_SIDE_VT_LEVL |  | 1) This field is required 2) Data type must be real 3) Generate an Error if not between 345 and 69
Low Side Voltage Level (nominal) | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | kV | Solar | LOW_SIDE_VT_LEVL |  | 1) This field is required 2) Data type must be real 3) Generate an Error if not < 69
High Side Voltage Connection - Wye / Wye - Grounded / Delta | Solar | [5 empty] | ADD 04/2012 | Planning - Solar |  | Solar | HIGH_SIDE_VT_CONNT |  | 1) This field is required 2) Data type must be from list 3) Generate an Error if blank
Low Side Voltage Connection - Wye / Wye - Grounded / Delta | Solar | [5 empty] | ADD 04/2012 | Planning - Solar |  | Solar | LOW_SIDE_VT_CONNT |  | 1) This field is required 2) Data type must be from list 3) Generate an Error if blank
Impedance Z | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | p.u. | Solar | IMPEDANCE_Z |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0
X/r Ratio | Solar | [5 empty] | ADD 04/2012 | Planning - Solar |  | Solar | X_R_RATIO |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 1
Zero Sequence Z | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | p.u. | Solar | ZERO_SEQ_Z |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0
Zero Sequence X/r Ratio | Solar | [5 empty] | ADD 04/2012 | Planning - Solar |  | Solar | ZERO_SEQ_X_R_RATIO |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 1
Base Mva For Transformer Data | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | MVA | Solar | BASE_MVA_TRANSFORMER_DATA |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank, Generate Warning if > 2000
Inverter Limits In P.u. Of Nominal Output For Fault Duty Studies | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | p.u. | Solar | INVERTER_LIMT_PU_NOMINAL_FAULT_DUTY_STUDIES
VOLTAGE REGULATION | Solar | [6 empty] | Planning - Solar |  | Not in table | Not in table
Automatic Voltage Regulation | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | Y/N | Solar | AUTO_VLT_REG
Does Transformer Have A Load Tap Changer? | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | Y/N | Solar | TRANS_LOAD_TAPCHARGER
Location Of Load Tap Changer - High Or Low | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | HIGH/LOW/BOTH/NONE | Solar | LOC_LOAD_TAPCHARGER
Base Kv Of Regulated Side | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | kV | Solar | BASE_LV_REG_SIDE
Target Kv Of Regulated Side | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | kV | Solar | TARG_KV_REG_SIDE
Acceptable Deviation Of Target Voltage | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | % | Solar | DEVITON_TARG_VT
ONLY IF HIGH SIDE TAP EXISTS | Solar | [6 empty] | Planning - Solar |  | Not in table | Not in table
Tap Position At Manufactured Nominal Voltage | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | Y/N | Solar | TAP_POS_MAN_NOMINAL_VT_HIGH
Total Number Of Tap Positions | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | Integer | Solar | TOT_NUM_TAP_POSITNS_HIGH
Normal Tap Position | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | Integer | Solar | NORML_TAP_POSITNS_HIGH
Lowest Tap Position | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | Integer | Solar | LOW_TAP_POSITNS_HIGH
Voltage At Lowest Tap Position | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | kV | Solar | VT_LOWST_TAP_POSITNS_HIGH
Highest Tap Position | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | Integer | Solar | HIGH_TAP_POSITNS_HIGH
Voltage At Highest Tap Position | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | kV | Solar | VT_HIGHST_TAP_POSITNS_HIGH
Size Of Each Voltage Level Step | Solar | [5 empty] | ADD 04/2012 | Planning - Solar | kV | Solar | SIZE_EACH_VT_LEVL_STEP_HIGH
PSSE MODEL : THE FOLLOWING LIST OF FILES ARE REQUIRED TO BE SUBMITTED IF THIS IS AN INITIAL REGISTRATION OR IF THERE ARE CHANGES MODIFYING PREVIOUSLY SUBMITTED PSSE FILES. PLEASE INCLUDE ALL PSSE FILES IN A ZIP OR COMPRESSED FOLDER FILE ALONG WITH YOUR RARF SUBMITTAL IN THE SAME SERVICE REQUEST | Solar | [6 empty] | Planning - Solar |  | Not in table | Not in table
Psse Compatible Solar Pv Generator Models | Solar | [6 empty] | Planning - Solar | Y/N | Not in table | Not in table
Dynamic Reactive Device Form/models | Solar | [6 empty] | Planning - Solar | Y/N | Not in table | Not in table
Planning - ESG | ESG | [6 empty] | Planning - ESG |  | Not in table | Not in table
GENERATOR DETAILS | ESG | [6 empty] | Planning - ESG |  | Not in table | Not in table
Unit Name | ESG | Do not show Message on Audit or Delta |  |  |  |  | ADD 04/2012 | Planning - ESG | List | ESGUNIT | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B
Resource Name (Unit Code/Mnemonic) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Automatic | ESGUNIT | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | Character | B,DVB
PLANNING DETAILS | ESG | [6 empty] | Planning - ESG |  | Not in table | Not in table |  | 2.All letters should be capital
What is the MVA base that the following data is based on? | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | MVA | ESGUNIT | MVABASE |  | 3. Should not allow spaces | R | Float | B
What is the kV base that the following data is based on? | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | kV | ESGUNIT | KVBASE |  | 4. Can not exceed 13 characters for split gen resources | R | Float | B,DVB
Direct Axis Subtransient reactance, X"di (unsaturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | p.u. | ESGUNIT | DIRECT_AXIS_SUBSTNT_REACTANCE_UNSATURATED |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value.(* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Direct Axis Transient reactance, X'di (unsaturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | p.u. | ESGUNIT | DIRECT_AXIS_TRANSNT_REACTANCE_UNSATURATED |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Positive Sequence Z (unsaturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | R in p.u. | ESGUNIT | POSITIVE_SEQ_Z_R_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1
Positive Sequence Z (unsaturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | X in p.u. | ESGUNIT | POSITIVE_SEQ_Z_X_UNSATURARTED_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Negative Sequence Z (unsaturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | R in p.u. | ESGUNIT | NEGATIVE_SEQ_Z_R_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1
Negative Sequence Z (unsaturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | X in p.u. | ESGUNIT | NEGATIVE_SEQ_Z_X_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Does Zero Sequence Z exist? | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Y/N | ESGUNIT | DOES_ZERO_SEQ_EXIST |  |  | R | Dropdown List |  | Planning Team
Zero Sequence Z (unsaturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | R in p.u. | ESGUNIT | ZERO_SEQ_Z_R_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 . Generate a Warning when value is > 1.0 P.U
Zero Sequence Z (unsaturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | X in p.u. | ESGUNIT | ZERO_SEQ_Z_X_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Direct Axis Subtransient reactance, X"dv (saturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | p.u. | ESGUNIT | DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value.(* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B
Direct Axis Transient reactance, X'dv (saturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | p.u. | ESGUNIT | DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B
Positive Sequence Z (saturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | R in p.u. | ESGUNIT | POSITIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B
Positive Sequence Z (saturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | X in p.u. | ESGUNIT | POSITIVE_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | B
Negative Sequence Z (saturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | R in p.u. | ESGUNIT | NEGATIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | B
Negative Sequence Z (saturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | X in p.u. | ESGUNIT | NEGATIVE_SEQ_Z_X-SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B
Zero Sequence Z (saturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | R in p.u. | ESGUNIT | ZERO_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U | R | Float | B
Zero Sequence Z (saturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | X in p.u. | ESGUNIT | ZERO_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | B
Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | p.u. | ESGUNIT | ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU
Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | p.u. | ESGUNIT | ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU
Zero Sequence Resistance In P.u. (100 Mva Base) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | p.u. | ESGUNIT | ZERO_SEQ_RESISTANCE_PU
Zero Sequence Reactance In P.u. (100 Mva Base) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | p.u. | ESGUNIT | ZERO_SEQ_Reactance_PU
Generator Auxiliary Load | ESG | [6 empty] | Planning - ESG |  | Not in table | Not in table
Average Amount of Auxiliary Real Power | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | MW | ESGUNIT | AUX_MWTOTAL |  | 1) This field is optional 2) Data type is float 3) Value must be < Parameters - GEN - High Reasonability Limit 4) Warn if value > (High Reasonability Limit) * .75 5) Error if value > (High Reasonability Limit) * .66
Average Amount of Auxiliary Reactive Power | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | MVAR | ESGUNIT | AUX_MVARTOTAL |  | 1) This field is optional 2) Data type is Float 3) Value must be < Reactive Capability - GEN - Maximum Lagging Operating Capability (MVAR) 4) Warn if value > ( Maximum Lagging Operating Capability) * .75 5) Error if value > ( Maximum Lagging Operating Capability) * .66
Auxiliary Load Power Factor | ESG | [5 empty] | ADD 04/2012 | Planning - ESG |  | ESGUNIT | AUX_LOAD_PWR_FACT
Generation Auxiliary Load Characteristics for MW Load | ESG | [6 empty] | Planning - ESG |  | Not in table | Not in table
Large Motor, percent of total MW load | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Percent | ESGUNIT | LRG_MTR_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
Small Motor, percent of total MW load | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Percent | ESGUNIT | SML_MTR_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
Resistive (Heating) Load, percent of total MW load | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Percent | ESGUNIT | RESISTIVE_LOAD_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
Discharge Lighting, percent of total MW load | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Percent | ESGUNIT | DISCHARGE LIGHT_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
Other, percent of total MW load | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Percent | ESGUNIT | OTH_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
Generation Auxiliary Load Characteristics for MVAR Load | ESG | [6 empty] | Planning - ESG |  | Not in table | Not in table
Large Motor, percent of total MVAR load | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Percent | ESGUNIT | LRG_MTR_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y'
Small Motor, percent of total MVAR load | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Percent | ESGUNIT | SML_MTR_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y'
Discharge Lighting, percent of total MVAR load | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Percent | ESGUNIT | DISCHARGE LIGHT_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y'
Other, percent of total MVAR load | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Percent | ESGUNIT | OTH_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y'
Voltage Regulation | ESG | [6 empty] | Planning - ESG |  | Not in table | Not in table
Automatic Voltage Regulation | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Y/N | ESGUNIT | AUTO_VLT_REG |  | 1) This field is required 2) Value must be from the following list: 'Y', 'N'
Does Transformer have a Load Tap Changer? | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Y/N | ESGUNIT | TRANS_LOAD_TAPCHARGER |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) Value must be from the following list: 'Y', 'N' 3) Load Tap Changer is expected to be 'Y' when total number of tap positions >=16. Warn if "Load Tap Changer" = 'N' and Total Number of Tap Positions>=16
Location of Load Tap Changer - High or Low | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | List | ESGUNIT | LOC_LOAD_TAPCHARGER
Base kV of Regulated Side | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | kV | ESGUNIT | BASE_LV_REG_SIDE |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 5) The value must be >= Low Voltage Level (no-load)
Target kV of Regulated Side | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | kV | ESGUNIT | TARG_KV_REG_SIDE |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) Value must be > 0
Acceptable Deviation of Target Voltage | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Percent | ESGUNIT | DEVITON_TARG_VT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0
Only if High Side Tap Exists | ESG | [6 empty] | Planning - ESG |  | Not in table | Not in table
Tap position at Manufactured Nominal Voltage | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Integer | ESGUNIT | TAP_POS_MAN_NOMINAL_VT_HIGH |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
Total Number of Tap Positions | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Integer | ESGUNIT | TOT_NUM_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
Normal Tap Position | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Integer | ESGUNIT | NORML_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
Lowest Tap Position | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Integer | ESGUNIT | LOW_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
Voltage at Lowest Tap Position | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | kV | ESGUNIT | VT_LOWST_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be real 3) Generate an Warning if not within 15% of nominal on tapped side of transformer
Highest Tap Position | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Integer | ESGUNIT | HIGH_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
Voltage at Highest Tap Position | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | kV | ESGUNIT | VT_HIGHST_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be real 3) Generate an Warning if not within 15% of nominal on tapped side of transformer
Size of each Voltage Level Step | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | kV | ESGUNIT | SIZE_EACH_VT_LEVL_STEP_HIGH |  | 1) This field is required 2) Data type must be real 3) Generate an Warning if not within 10% of nominal kV / number of taps
Only if Low Side Tap Exists | ESG | [6 empty] | Planning - ESG |  | Not in table | Not in table
Tap position at Manufactured Nominal Voltage | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Integer | ESGUNIT | TAP_POSITNS_MANFACTURED_NOMINAL_VT_LOW |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
Total Number of Tap Positions | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Integer | ESGUNIT | TOT_NUM_TAP_POSITNS_LOW |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
Normal Tap Position | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Integer | ESGUNIT | NORML_TAP_POSITNS_LOW |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
Lowest Tap Position | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Integer | ESGUNIT | LOW_TAP_POSITNS_LOW |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
Voltage at Lowest Tap Position | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | kV | ESGUNIT | VT_LOWST_TAP_POSITNS_LOW |  | 1) This field is required 2) Data type must be real 3) Generate an Warning if not within 15% of nominal on tapped side of transformer
Highest Tap Position | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | Integer | ESGUNIT | HIGH_TAP_POSITNS_LOW |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
Voltage at Highest Tap Position | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | kV | ESGUNIT | VT_HIGHST_TAP_POSITNS_LOW |  | 1) This field is required 2) Data type must be real 3) Generate an Warning if not within 15% of nominal on tapped side of transformer
Size of each Voltage Level Step | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | kV | ESGUNIT | SIZE_EACH_VT_LEVL_STEP_LOW |  | 1) This field is required 2) Data type must be real 3) Generate an Warning if not within 10% of nominal kV / number of taps
Inverter Data (if applicable) | ESG | [6 empty] | Planning - ESG |  | Not in table | Not in table
What is the MVA base that the following data is based on? | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | MVA | ESGUNIT | INVERTER_MVA_BASE |  | 1) This field is required 2) Value must be Float 3) Generate a Warning if MVABASE > 2500 4)[ If MVABASE value is within +/- 25% range of Unit Name Plate Rating] OR [MVABASE value = 100, then it is OK.If MVABASE value is outside the +/- 25% range of Unit Name Plate Rating, then Generate a Warning that the MVABSE is outside the typical +/- 25% variation of unit name plate rating
What is the kV base that the following data is based on? | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | kV | ESGUNIT | INVERTER_KV_BASE |  | 1) This field is required 2) Value must be >0 and <1000 3) Generate a Warning if KVBASE > 40 4) If KVBASE value is within +/- 25% range of Unit KV value in the unit-information tab then it is OK.If If KVBASE value is outside the typical +/- 25% variation of Unit KV value in the unit-information tab then Generate a Warning that the KVBASE is outside the typical +/- 25% variation of Unit KV value
Direct Axis Subtransient reactance, X"di | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | p.u. | ESGUNIT | DIRECT_AXIS_SUBSTNT_REACTANCE_INVERTER |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Direct Axis Transient reactance, X'di | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | p.u. | ESGUNIT | DIRECT_AXIS_TRANSNT_REACTANCE_UINVERTER |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Positive Sequence Z (Unsaturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | R in p.u. | ESGUNIT | POSITIVE_SEQ_Z_R_UNSATURARTED_PU_INVERTER |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1
Positive Sequence Z (Unsaturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | X in p.u. | ESGUNIT | POSITIVE_SEQ_Z_X_UNSATURARTED_PU_INVERTER |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Negative Sequence Z (Unsaturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | R in p.u. | ESGUNIT | NEGATIVE_SEQ_Z_R_UNSATURARTED_PU_INVERTER. |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1
Negative Sequence Z (Unsaturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | X in p.u. | ESGUNIT | NEGATIVE_SEQ_Z_X_UNSATURARTED_PU_INVERTER |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Zero Sequence Z (Unsaturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | R in p.u. | ESGUNIT | ZERO_SEQ_Z_R_UNSATURARTED_PU_INVERTER |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 . Generate a Warning when value is > 1.0 P.U
Zero Sequence Z (Unsaturated) | ESG | [5 empty] | ADD 04/2012 | Planning - ESG | X in p.u. | ESGUNIT | ZERO_SEQ_Z_X_UNSATURARTED_PU_INVERTER |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
PSSE Models : The following files are required to be submitted if not listed in the Wind Turbine Dynamic Models available at ERCOT or if additional equipment has been added to the site requiring Model updates. Please include all PSSE files in a ZIP or Compressed Folder along with your RARF submittal Service Request. | ESG | [6 empty] | Planning - ESG |  | Not in table | Not in table
PSSE Compatible Solar Pv Generator Models | ESG | [6 empty] | Planning - ESG |  | Not in table | Not in table
Dynamic Reactive Device Form/models | ESG | [6 empty] | Planning - ESG |  | Not in table | Not in table
Protection - Solar | Solar | [5 empty] | ADD 04/2012 | Protection - Solar |  | Not in table | Not in table
GENERATOR DETAILS | Solar | [6 empty] | Protection - Solar |  | Not in table | Not in table
Unit Name | Solar | Do not show Message on Audit or Delta |  |  |  |  | ADD 04/2012 | Protection - Solar |  | Solar | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B
Resource Name (Unit Code/Mnemonic) | Solar | [5 empty] | ADD 04/2012 | Protection - Solar |  | Solar | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | Character | B,DVB
Breaker Interruption Time | Solar | [6 empty] | Protection - Solar |  | Not in table | Not in table
Breaker Interruption Time | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | cycles | Solar | BREAKER_INTERRUP |  | 1) this field is required 2) Data type must be Integer | R | Integer | B
PLANT VOLTAGE PROTECTION | Solar | [6 empty] | Protection - Solar |  | Not in table | Not in table
Instantaneous Undervoltage Trip | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | p.u. | Solar | UVOLT_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Undervoltage 1 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | p.u. | Solar | UVOLT_TRIP_VOLT1 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Time 1 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | sec | Solar | UVOLT_TRIP_TIME1 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Undervoltage 2 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | p.u. | Solar | UVOLT_TRIP_VOLT2 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Time 2 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | sec | Solar | UVOLT_TRIP_TIME2 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Undervoltage 3 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | p.u. | Solar | UVOLT_TRIP_VOLT3 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Time 3 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | sec | Solar | UVOLT_TRIP_TIME3 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Undervoltage 4 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | p.u. | Solar | UVOLT_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Time 4 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | sec | Solar | UVOLT_TRIP_VOLT4 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Instantaneous Overvoltage Trip | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | p.u. | Solar | OVOLT_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Overvoltage 1 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | p.u. | Solar | OVOLT_TRIP_VOLT1 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Time 1 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | sec | Solar | OVOLT_TRIP_TIME1 |  | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Overvoltage 2 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | p.u. | Solar | OVOLT_TRIP_VOLT2 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Time 2 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | sec | Solar | OVOLT_TRIP_TIME2 |  | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Overvoltage 3 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | p.u. | Solar | OVOLT_TRIP_VOLT3 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Time 3 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | sec | Solar | OVOLT_TRIP_TIME3 |  | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Overvoltage 4 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | p.u. | Solar | OVOLT_TRIP_VOLT4 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Time 4 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | sec | Solar | OVOLT_TRIP_TIME4 |  | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
PLANT FREQUENCY PROTECTION | Solar | [6 empty] | Protection - Solar |  | Not in table | Not in table
Instantaneous Underfrequency Trip | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | Hz | Solar | UFREQ_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float
Underfrequency 1 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | Hz | Solar | UFREQ_TRIP_HZ1 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab
Time 1 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | sec | Solar | UFREQ_TRIP_TIME1 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Underfrequency 2 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | Hz | Solar | UFREQ_TRIP_HZ2 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab
Time 2 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | sec | Solar | UFREQ_TRIP_TIME2 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Underfrequency 3 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | Hz | Solar | UFREQ_TRIP_HZ3 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab
Time 3 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | sec | Solar | UFREQ_TRIP_TIME3 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Underfrequency 4 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | Hz | Solar | UFREQ_TRIP_HZ4 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab
Time 4 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | sec | Solar | UFREQ_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Instantaneous Overfrequency Trip | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | Hz | Solar | OFREQ_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float
Overfrequency 1 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | Hz | Solar | OFREQ_TRIP_HZ1 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab
Time 1 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | sec | Solar | OFREQ_TRIP_TIME1 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Overfrequency 2 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | Hz | Solar | OFREQ_TRIP_HZ2 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab
Time 2 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | sec | Solar | OFREQ_TRIP_TIME2 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Overfrequency 3 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | Hz | Solar | OFREQ_TRIP_HZ3 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab
Time 3 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | sec | Solar | OFREQ_TRIP_TIME3 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Overfrequency 4 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | Hz | Solar | OFREQ_TRIP_HZ4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab
Time 4 | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | sec | Solar | OFREQ_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
PV INVERTER VRT CAPABILITY | Solar | [6 empty] | Protection - Solar |  | Not in table | Not in table
Provide Manufacturer's Technical Document / Simulation Results / Test Result, Etc. Describing The Solar Technology & Vrt OPTIons Purchased With Inverter, If Any | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | Y/N | Solar | MAN_TECH_DOC_SIM_RESULTS
Do Personnel (onsite Operator/engineer Etc.) Have Control To Enable/disable Or Change The Settings For Voltage Ride-through | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | Y/N | Solar | PERSONNEL_CHANGE_SET_CNTRL
Does The Resource Use Dynamic Reactive Devices (SVC/statcom, Etc.) At Solar Plant Facility? - (note: Capacitor Banks Used For Conventional Reactive Support Cannot Be Considered As Dynamic Reactive Devices) - If Yes, Please Provide Supporting Documentation. (manufacturer's Technical Document, Pss/e Model Etc.) | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | Y/N | Solar | DYNAMIC_REACT_DEVICES
Provide Inverter Voltage & Frequency Protection Settings As Per Manufacturer - Technical Document And/or Spec Sheet | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | Y/N | Solar | INVERTER_VOLTAGE_FREQ_PROT_SET
Does The Resource Have Plant Voltage Protection? If Yes, Please Provide Supporting Documentation. | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | Y/N | Solar | RE_PLANT_VOLTAGE_PROT
Does The Resource Have Feeder Voltage Protection? If Yes, Please Provide Supporting Documentation. | Solar | [5 empty] | ADD 04/2012 | Protection - Solar | Y/N | Solar | RE_VOLTAGE_FEEDER_PROT
Protection - ESG | ESG | [6 empty] | Protection - ESG |  | Not in table | Not in table
GENERATOR DETAILS | ESG | [6 empty] | Protection - ESG |  | Not in table | Not in table
Unit Name | ESG | Do not show Message on Audit or Delta |  |  |  |  | ADD 04/2012 | Protection - ESG | List | ESGUNIT | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B
Resource Name (Unit Code/Mnemonic) | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | Automatic | ESGUNIT | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | Character | B,DVB
Breaker Interruption Time | ESG | [6 empty] | Protection - ESG |  | Not in table | Not in table |  | 3. Should not allow spaces
Breaker Interruption Time | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | cycles | ESGUNIT | BREAKER_INTERRUP |  | 3. Should not allow spaces
PLANT VOLTAGE PROTECTION | ESG | [6 empty] | Protection - ESG |  | Not in table | Not in table |  | 4. Can not exceed 13 characters for split gen resources
Instantaneous Undervoltage Trip | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | p.u. | ESGUNIT | UVOLT_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | O | Float | B
Undervoltage 1 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | p.u. | ESGUNIT | UVOLT_TRIP_VOLT1 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | R | Float
Time 1 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | sec | ESGUNIT | UVOLT_TRIP_TIME1 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | R | Float | B
Undervoltage 2 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | p.u. | ESGUNIT | UVOLT_TRIP_VOLT2 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | O | Float | B
Time 2 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | sec | ESGUNIT | UVOLT_TRIP_TIME2 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | R | Float | B
Undervoltage 3 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | p.u. | ESGUNIT | UVOLT_TRIP_VOLT3 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | R | Float | B
Time 3 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | sec | ESGUNIT | UVOLT_TRIP_TIME3 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | O | Float | B
Undervoltage 4 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | p.u. | ESGUNIT | UVOLT_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | R | Float | B
Time 4 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | sec | ESGUNIT | UVOLT_TRIP_VOLT4 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | R | Float | B
Instantaneous Overvoltage Trip | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | p.u. | ESGUNIT | OVOLT_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | O | Float | B
Overvoltage 1 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | p.u. | ESGUNIT | OVOLT_TRIP_VOLT1 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | R | Float | B
Time 1 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | sec | ESGUNIT | OVOLT_TRIP_TIME1 |  | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | R | Float | B
Overvoltage 2 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | p.u. | ESGUNIT | OVOLT_TRIP_VOLT2 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | R | Float | B
Time 2 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | sec | ESGUNIT | OVOLT_TRIP_TIME2 |  | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | R | Float | B
Overvoltage 3 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | p.u. | ESGUNIT | OVOLT_TRIP_VOLT3 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | R | Float | B
Time 3 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | sec | ESGUNIT | OVOLT_TRIP_TIME3 |  | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | R | Float | B
Overvoltage 4 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | p.u. | ESGUNIT | OVOLT_TRIP_VOLT4 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | R | Float | B
Time 4 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | sec | ESGUNIT | OVOLT_TRIP_TIME4 |  | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | R | Float | B
PLANT FREQUENCY PROTECTION | ESG | [6 empty] | Protection - ESG |  | Not in table | Not in table
Instantaneous Underfrequency Trip | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | Hz | ESGUNIT | UFREQ_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float | O | Float | B
Underfrequency 1 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | Hz | ESGUNIT | UFREQ_TRIP_HZ1 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | R | Float | B
Time 1 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | sec | ESGUNIT | UFREQ_TRIP_TIME1 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R | Float | B
Underfrequency 2 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | Hz | ESGUNIT | UFREQ_TRIP_HZ2 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | R | Float | B
Time 2 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | sec | ESGUNIT | UFREQ_TRIP_TIME2 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R | Float | B
Underfrequency 3 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | Hz | ESGUNIT | UFREQ_TRIP_HZ3 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | R | Float | B
Time 3 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | sec | ESGUNIT | UFREQ_TRIP_TIME3 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R | Float | B
Underfrequency 4 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | Hz | ESGUNIT | UFREQ_TRIP_HZ4 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | R | Float | B
Time 4 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | sec | ESGUNIT | UFREQ_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R | Float | B
Instantaneous Overfrequency Trip | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | Hz | ESGUNIT | OFREQ_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float | O | Float | B
Overfrequency 1 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | Hz | ESGUNIT | OFREQ_TRIP_HZ1 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | R | Float | B
Time 1 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | sec | ESGUNIT | OFREQ_TRIP_TIME1 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R | Float | B
Overfrequency 2 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | Hz | ESGUNIT | OFREQ_TRIP_HZ2 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | R | Float | B
Time 2 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | sec | ESGUNIT | OFREQ_TRIP_TIME2 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R | Float | B
Overfrequency 3 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | Hz | ESGUNIT | OFREQ_TRIP_HZ3 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | R | Float | B
Time 3 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | sec | ESGUNIT | OFREQ_TRIP_TIME3 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R | Float | B
Overfrequency 4 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | Hz | ESGUNIT | OFREQ_TRIP_HZ4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | R | Float | B
Time 4 | ESG | [5 empty] | ADD 04/2012 | Protection - ESG | sec | ESGUNIT | OFREQ_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R | Float | B
Collector System - Solar | Solar | 03/13/2012 Updated | [5 empty] | Collector System - Solar |  | Not in table | Not in table
COLLECTION SYSTEM DETAILED MODEL | Solar | 03/13/2012 Updated | [5 empty] | Collector System - Solar |  | Not in table | Not in table
Cable Type | Solar | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System-Solar |  | COLLECTOR_SYS | CABLE_TYPE |  | 1) This field is required 2) Data type must string 3) Generate an Warning if blank
Voltage Level kV | Solar | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System-Solar | kV | COLLECTOR_SYS | VT_LEVEL_KV |  | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0
POSITIVE SEQUENCE DATA | Solar | 03/13/2012 Updated | [5 empty] | Collector System - Solar | Label | Not in table | Not in table
R/kft | Solar | 03/09/2012 Updated |  |  |  |  | ADD 04/2012 | Collector System-Solar | R/kft | COLLECTOR_SYS | POS_R_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank
X/kft | Solar | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System-Solar | X/kft | COLLECTOR_SYS | POS_X_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank
Charging Bc/kft | Solar | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System-Solar | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_CHRG_BC_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank
ZERO SEQUENCE DATA | Solar | 03/13/2012 Updated | [5 empty] | Collector System - Solar | Label | Not in table | Not in table
R0/kft | Solar | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System-Solar | (p.u. on 100 MVA base) | COLLECTOR_SYS | ZERO_R0_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank
X0/kft | Solar | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System-Solar | (p.u. on 100 MVA base) | COLLECTOR_SYS | ZERO_X0_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank
Collector System-Solar Seg Data | Solar | 03/13/2012 Updated | [5 empty] | Collector System-Solar Seg Data |  | Not in table | Not in table
CABLE TYPE | Solar | 03/13/2012 Updated | [5 empty] | Collector System-Solar Seg Data |  | Not in table | Not in table
Cable Type | Solar | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System-Solar Seg Data |  | CABLE_SEG_DATA | CABLE_TYPE |  | 1) This field is required 2) Data type must string 3) Generate an Warning if blank
CABLE SEGAMENT DATA | Solar | 03/13/2012 Updated | [5 empty] | Collector System-Solar Seg Data |  | Not in table | Not in table
From | Solar | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System-Solar Seg Data | Integer | CABLE_SEG_DATA | CABLE_SEG_DATA_FROM |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank
To | Solar | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System-Solar Seg Data | Integer | CABLE_SEG_DATA | CABLE_SEG_DATA_TO |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank
Circuit Number | Solar | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System-Solar Seg Data | Integer | CABLE_SEG_DATA | CIRCT_NUM |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank
Voltage Level | Solar | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System-Solar Seg Data | kV | CABLE_SEG_DATA | VT_LEVL |  | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0.
Cable Type | Solar | 03/13/12 REMOVED Duplicated Line |  |  |  |  | ADD 04/2012 | Collector System-Solar Seg Data |  | CABLE_SEG_DATA | CABLE_TYPE
Cable Segment Length | Solar | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System-Solar Seg Data | in kft | CABLE_SEG_DATA | CABLE_SEG_LENTH |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank
Number of Turbines On Cable Segment | Solar | 03/13/12 Updated |  |  |  |  | ADD 04/2012 | Collector System-Solar Seg Data | Integer | CABLE_SEG_DATA | NUM_TURBIN_ON_CABLE_SEG |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank
Private Network - Site - ESG | ESG | [6 empty] | Private Network - Site - ESG |  | Not in table | Not in table
SITE DETAILS | ESG | [6 empty] | Private Network - Site - ESG |  | Not in table | Not in table
Private Network? | ESG | [5 empty] | ADD 04/2012 | Private Network - Site - ESG | Y/N | SITECODES | PRIVATE_NTWK_SITE_FLG
SITE CODE | ESG | Removed from Form 03/05/2012 |  |  |  |  | ADD 04/2012 | Private Network - Site - ESG | Automatic | SITECODES | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B
PRIVATE NETWORK - SITE INFORMATION | ESG | [6 empty] | Private Network - Site - ESG |  | Not in table | Not in table |  | 2.All letters should be capital
Average Amount of Self-Serve private load | ESG | [5 empty] | ADD 04/2012 | Private Network - Site - ESG | MW | ESGUNIT | AVG_LD_MW_UNIT
Average Amount of Self-Serve private reactive load | ESG | [5 empty] | ADD 04/2012 | Private Network - Site - ESG | MVAR | ESGUNIT | AVG_LD_MVAR_UNIT
Expected Typical Private Network Net Interchange | ESG | [5 empty] | ADD 04/2012 | Private Network - Site - ESG | MW | ESGUNIT | NET_INTERCHNG_MW_UNIT
Expected Typical Private Network Net Reactive Interchange | ESG | [5 empty] | ADD 04/2012 | Private Network - Site - ESG | MVAR | ESGUNIT | NET_INTERCHNG_MVAR_UNIT
Private Network Gross Unit Capability | ESG | [5 empty] | ADD 04/2012 | Private Network - Site - ESG | MW | ESGUNIT | GROSS_CAPBLTY_MW_UNIT
Private Network Gross Unit Reactive Capability | ESG | [5 empty] | ADD 04/2012 | Private Network - Site - ESG | MVAR | ESGUNIT | GROSS_CAPBLTY_MVAR_UNIT
Load Characteristics for MW Load | ESG | [6 empty] | Private Network - Site - ESG |  | Not in table | Not in table
Large Motor, percent of total MW load | ESG | [5 empty] | ADD 04/2012 | Private Network - Site - ESG | % | SITECODES | PUN_MW_LARGEMTR_PCT
Small Motor, percent of total MW load | ESG | [5 empty] | ADD 04/2012 | Private Network - Site - ESG | % | SITECODES | PUN_MW_SMALLMTR_PCT
Resistive (Heating) Load, percent of total MW load | ESG | [5 empty] | ADD 04/2012 | Private Network - Site - ESG | % | SITECODES | PUN_MW_RESISTIVE_PCT
Discharge Lighting, percent of total MW load | ESG | [5 empty] | ADD 04/2012 | Private Network - Site - ESG | % | SITECODES | PUN_MW_DISCHARGE_PCT
Other, percent of total MW load | ESG | [5 empty] | ADD 04/2012 | Private Network - Site - ESG | % | SITECODES | PUN_MW_OTHER_PCT
Load Characteristics for MVAR Load | ESG | [6 empty] | Private Network -ESG |  | Not in table | Not in table
Large Motor, percent of total MVAR load | ESG | [5 empty] | ADD 04/2012 | Private Network - Site - ESG | % | SITECODES | PUN_MVAR_LARGEMTR_PCT
Small Motor, percent of total MVAR load | ESG | [5 empty] | ADD 04/2012 | Private Network - Site - ESG | % | SITECODES | PUN_MVAR_SMALLMTR_PCT
Discharge Lighting, percent of total MVAR load | ESG | [5 empty] | ADD 04/2012 | Private Network - Site - ESG | % | SITECODES | PUN_MVAR_DISCHARGE_PCT
Other, percent of total MVAR load | ESG | [5 empty] | ADD 04/2012 | Private Network - Site - ESG | % | SITECODES | PUN_MVAR_OTHER_PCT
Private Network - Unit - ESG | ESG | [6 empty] | Private Network - Unit - ESG |  | Not in table | Not in table
GENERATOR DETAILS | ESG | [6 empty] | Private Network - Unit - ESG |  | Not in table | Not in table
Unit Name | ESG | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Private Network - Unit - ESG | List | SITECODES | UNIT_NAME | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | 1. This field is not null. Data type: Character. | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
SITE_CODE | ESG | [5 empty] | ADD 02/2012 | Private Network - Unit - ESG | Automatic | SITECODES | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
Resource Name (Unit Code/Mnemonic) | ESG | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Private Network - Unit - ESG | Automatic | SITECODES | UNIT_CODE | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
PRIVATE NETWORK - UNIT INFORMATION | ESG | [6 empty] | Private Network - Unit - ESG |  | Not in table | Not in table
Average Amount of Self-Serve private load | ESG | [5 empty] | ADD 04/2012 | Private Network - Unit - ESG | MW | ESGUNIT | AVG_LD_MW_UNIT
Average Amount of Self-Serve private reactive load | ESG | [5 empty] | ADD 04/2012 | Private Network - Unit - ESG | MVAR | ESGUNIT | AVG_LD_MVAR_UNIT
Expected Typical Private Network Net Interchange | ESG | [5 empty] | ADD 04/2012 | Private Network - Unit - ESG | MW | ESGUNIT | NET_INTERCHNG_MW_UNIT
Expected Typical Private Network Net Reactive Interchange | ESG | [5 empty] | ADD 04/2012 | Private Network - Unit - ESG | MVAR | ESGUNIT | NET_INTERCHNG_MVAR_UNIT
Private Network Gross Unit Capability | ESG | [5 empty] | ADD 04/2012 | Private Network - Unit - ESG | MW | ESGUNIT | GROSS_CAPBLTY_MW_UNIT
Private Network Gross Unit Reactive Capability | ESG | [5 empty] | ADD 04/2012 | Private Network - Unit - ESG | MWAR | ESGUNIT | GROSS_CAPBLTY_MVAR_UNIT
If Unit trips, does Load trip? | ESG | [5 empty] | ADD 04/2012 | Private Network - Unit - ESG | Y/N | ESGUNIT | LOAD_TRIP_FLG
If yes, approximate percentage of Load that will trip? | ESG | [5 empty] | ADD 04/2012 | Private Network -ESG | % | ESGUNIT | LOAD_TRIP_PCT
Private Network - Site - Solar | Solar | [6 empty] | Private Network - Site - Solar |  | Not in table | Not in table
GENERATOR DETAILS | Solar | [6 empty] | Private Network - Site - Solar |  | Not in table | Not in table
Private Network? | Solar | [5 empty] | ADD 04/2012 | Private Network - Site - Solar | Y/N | SITECODES | PRIVATE_NTWK_SITE_FLG
Unit Name | Solar | REMOVED from Form Do not show Message on Audit or Delta |  |  |  |  | ADD 04/2012 | Private Network - Site - Solar | List | SITECODES | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B
Resource Name (Unit Code/Mnemonic) | Solar | Removed from Form 03/05/2012 |  |  |  |  | ADD 04/2012 | Private Network - Site - Solar | Automatic | SITECODES | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | Character | B,DVB
PRIVATE NETWORK - SITE INFORMATION | Solar | [6 empty] | Private Network -Solar |  | Not in table | Not in table |  | 2.All letters should be capital
Average Amount of Self-Serve private load | Solar | [5 empty] | ADD 04/2012 | Private Network - Site - Solar | MW | SOLAR | AVG_LD_MW_UNIT |  | 3. Should not allow spaces
Average Amount of Self-Serve private reactive load | Solar | [5 empty] | ADD 04/2012 | Private Network - Site - Solar | MVAR | SOLAR | AVG_LD_MVAR_UNIT |  | 4. Can not exceed 13 characters for split gen resources
Expected Typical Private Network Net Interchange | Solar | [5 empty] | ADD 04/2012 | Private Network - Site - Solar | MW | SOLAR | NET_INTERCHNG_MW_UNIT
Expected Typical Private Network Net Reactive Interchange | Solar | [5 empty] | ADD 04/2012 | Private Network - Site - Solar | MVAR | SOLAR | NET_INTERCHNG_MVAR_UNIT
Private Network Gross Unit Capability | Solar | [5 empty] | ADD 04/2012 | Private Network - Site - Solar | MW | SOLAR | GROSS_CAPBLTY_MW_UNIT
Private Network Gross Unit Reactive Capability | Solar | [5 empty] | ADD 04/2012 | Private Network - Site - Solar | MVAR | SOLAR | GROSS_CAPBLTY_MVAR_UNIT
Load Characteristics for MW Load | Solar | [6 empty] | Private Network -Solar |  | Not in table | Not in table
Large Motor, percent of total MW load | Solar | [5 empty] | ADD 04/2012 | Private Network - Site - Solar | % | SITECODES | PUN_MW_LARGEMTR_PCT
Small Motor, percent of total MW load | Solar | [5 empty] | ADD 04/2012 | Private Network - Site - Solar | % | SITECODES | PUN_MW_SMALLMTR_PCT
Resistive (Heating) Load, percent of total MW load | Solar | [5 empty] | ADD 04/2012 | Private Network - Site - Solar | % | SITECODES | PUN_MW_RESISTIVE_PCT
Discharge Lighting, percent of total MW load | Solar | [5 empty] | ADD 04/2012 | Private Network - Site - Solar | % | SITECODES | PUN_MW_DISCHARGE_PCT
Other, percent of total MW load | Solar | [5 empty] | ADD 04/2012 | Private Network - Site - Solar | % | SITECODES | PUN_MW_OTHER_PCT
Load Characteristics for MVAR Load | Solar | [6 empty] | Private Network -Solar |  | Not in table | Not in table
Large Motor, percent of total MVAR load | Solar | [5 empty] | ADD 04/2012 | Private Network - Site - Solar | % | SITECODES | PUN_MVAR_LARGEMTR_PCT
Small Motor, percent of total MVAR load | Solar | [5 empty] | ADD 04/2012 | Private Network - Site - Solar | % | SITECODES | PUN_MVAR_SMALLMTR_PCT
Discharge Lighting, percent of total MVAR load | Solar | [5 empty] | ADD 04/2012 | Private Network - Site - Solar | % | SITECODES | PUN_MVAR_DISCHARGE_PCT
Other, percent of total MVAR load | Solar | [5 empty] | ADD 04/2012 | Private Network - Site - Solar | % | SITECODES | PUN_MVAR_OTHER_PCT
Private Network - Unit - Solar | Solar | [6 empty] | Private Network - Unit - Solar |  | Not in table | Not in table
GENERATOR DETAILS | Solar | [6 empty] | Private Network - Unit - Solar |  | Not in table | Not in table
Unit Name | Solar | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Private Network - Unit - Solar | List | SITECODES | UNIT_NAME | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | 1. This field is not null. Data type: Character. | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
SITE_CODE | Solar | [5 empty] | ADD 02/2012 | Private Network - Unit - Solar | Automatic | SITECODES | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
Resource Name (Unit Code/Mnemonic) | Solar | Do not show Message on Audit or Delta |  |  |  |  | ADD 02/2012 | Private Network - Unit - Solar | Automatic | SITECODES | UNIT_CODE | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | Character | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
PRIVATE NETWORK - Unit Information | Solar | [6 empty] | Private Network - Unit - Solar |  | Not in table | Not in table
Average Amount of Self-Serve private load | Solar | [5 empty] | ADD 04/2012 | Private Network - Unit - Solar | MW | SOLAR | AVG_LD_MW_UNIT
Average Amount of Self-Serve private reactive load | Solar | [5 empty] | ADD 04/2012 | Private Network - Unit - Solar | MVAR | SOLAR | AVG_LD_MVAR_UNIT
Expected Typical Private Network Net Interchange | Solar | [5 empty] | ADD 04/2012 | Private Network - Unit - Solar | MW | SOLAR | NET_INTERCHNG_MW_UNIT
Expected Typical Private Network Net Reactive Interchange | Solar | [5 empty] | ADD 04/2012 | Private Network - Unit - Solar | MVAR | SOLAR | NET_INTERCHNG_MVAR_UNIT
Private Network Gross Unit Capability | Solar | [5 empty] | ADD 04/2012 | Private Network - Unit - Solar | MW | SOLAR | GROSS_CAPBLTY_MW_UNIT
Private Network Gross Unit Reactive Capability | Solar | [5 empty] | ADD 04/2012 | Private Network - Unit - Solar | MVAR | SOLAR | GROSS_CAPBLTY_MVAR_UNIT
If Unit trips, does Load trip? | Solar | [5 empty] | ADD 04/2012 | Private Network - Unit - Solar | Y/N | SOLAR | LOAD_TRIP_FLG
If yes, approximate percentage of Load that will trip? | Solar | [5 empty] | ADD 04/2012 | Private Network - Unit - Solar | % | SOLAR | LOAD_TRIP_PCT

## Sheet6 (hidden)
RARF DATA FIELD | RARF DATA FIELD | Corrections and Updates | Change Description
General and Site Information | General and Site Information |  |  |  | field
This submittal is for | This submittal is for | Updated 03/09/2012 validation rule to match view |  |  | TRUE | Updated 03/09/2012 validation rule to match view
Submittal Information | Submittal Information |  |  |  | TRUE
Date Form Completed: | Date Form Completed: |  |  |  | TRUE
Resource Entity Submitting Form: | Resource Entity Submitting Form: | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
Resource Entity DUNS #: | Resource Entity DUNS #: |  |  |  | TRUE
Site Information | Site Information |  |  |  | TRUE
Resource Site Name: | Resource Site Name: |  |  |  | TRUE
Resource Site Code: | Resource Site Code: |  |  |  | TRUE
Street Address: | Street Address: |  |  |  | TRUE
City: | City: |  |  |  | TRUE
State | State |  |  |  | TRUE
Zip Code | Zip Code |  |  |  | TRUE
County: | County: |  |  |  | TRUE
Site In-Service Date: | Site In-Service Date: |  |  |  | TRUE
Site Stop Service Date: | Site Stop Service Date: |  |  |  | TRUE
Congestion Management Zone for 2003: | Congestion Management Zone for 2003: |  |  |  | TRUE
Resource owned by NOIE? | Resource owned by NOIE? |  |  |  | TRUE
Is Resource behind a NOIE Settlement Meter Point? | Is Resource behind a NOIE Settlement Meter Point? |  |  |  | TRUE
Number of EPS Primary meters: | Number of EPS Primary meters: |  |  |  | TRUE
Primary Contact (name of person ERCOT can contact with questions regarding this form) | Primary Contact (name of person ERCOT can contact with questions regarding this form) |  |  |  | TRUE
Printed Name: | Printed Name: |  |  |  | TRUE
Title: | Title: |  |  |  | TRUE
Phone Number: | Phone Number: |  |  |  | TRUE
E-mail Address: | E-mail Address: |  |  |  | TRUE
Fax Number: | Fax Number: |  |  |  | TRUE
Secondary Contact (if available) | Secondary Contact (if available) |  |  |  | TRUE
Printed Name: | Printed Name: |  |  |  | TRUE
Title: | Title: |  |  |  | TRUE
Phone Number: | Phone Number: |  |  |  | TRUE
E-mail Address: | E-mail Address: |  |  |  | TRUE
Fax Number: | Fax Number: |  |  |  | TRUE
GEN Load Split -ESIID | GEN Load Split -ESIID |  |  |  | TRUE
GENERATION SITE LOAD DETAILS | GENERATION SITE LOAD DETAILS |  |  |  | TRUE
ESIID_NUMBER | ESIID_NUMBER |  | ADD 02/2012 to RARF FORM |  | TRUE |  | ADD 02/2012 to RARF FORM
SITECODE_ESIID | SITECODE_ESIID |  | ADD 02/2012 to RARF FORM |  | TRUE |  | ADD 02/2012 to RARF FORM
Generation Load Split? | Generation Load Split? | Corrected 02/29/2012 |  |  | TRUE | Corrected 02/29/2012
ERCOT Read Meter? | ERCOT Read Meter? |  |  |  | TRUE | Corrected
SITECODE | SITECODE |  | ADD 02/2012 |  | TRUE | Corrected | ADD 02/2012
ESI ID: | ESI ID: | Corrected | UPDATE 02/2012 |  | TRUE | 03/09/2012 Updated Validation | UPDATE 02/2012
TDSP Providing Service To Resource: | TDSP Providing Service To Resource: | Corrected |  |  | TRUE | Corrected
TDSP DUNS Number: | TDSP DUNS Number: | 03/09/2012 Updated Validation |  |  | TRUE | 03/09/2012 Updated Validation
Fixed Load Splitting % | Fixed Load Splitting % |  |  |  | TRUE
Load Serving Entity | Load Serving Entity |  |  |  | TRUE
Load Serving Entity Duns# | Load Serving Entity Duns# |  |  |  | TRUE
Unit Info - GEN | Unit Info - GEN |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name |  |  |  | TRUE
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  |  |  | TRUE
Non_Modeled Generator | Non_Modeled Generator |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Number of Generators in this Unit? (AGR Only) | Number of Generators in this Unit? (AGR Only) | Added field which is needed for PRR437 | ADD 04/2012 |  | TRUE | Added field which is needed for PRR437 | ADD 04/2012
PUC Registration Number | PUC Registration Number |  |  |  | TRUE
ERCOT Interconnection Project Number - only new units | ERCOT Interconnection Project Number - only new units |  |  |  | TRUE
NERC Number | NERC Number |  |  |  | TRUE
Qualifying facility | Qualifying facility |  |  |  | TRUE
SITE AND UNIT DATES | SITE AND UNIT DATES |  |  |  | TRUE
Transmission Only Date (POI) | Transmission Only Date (POI) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Standard Generation Interconnection Agreement (SGIA) Signature Date | Standard Generation Interconnection Agreement (SGIA) Signature Date |  | ADD 04/2012 |  | TRUE | 03/13/2012 Updated Validation | ADD 04/2012
Unit Start Date (Model Ready Date) | Unit Start Date (Model Ready Date) | 03/13/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/13/2012 Updated Validation | ADD 04/2012
Unit Commercial Date | Unit Commercial Date |  |  |  | TRUE
Unit End Date | Unit End Date |  |  |  | TRUE
POINT OF INTERCONNECTION | POINT OF INTERCONNECTION |  |  |  | TRUE
SubStation Code/SubStation Mnemonic | SubStation Code/SubStation Mnemonic |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Voltage Level | Voltage Level |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
PTI Bus Number | PTI Bus Number |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
FUEL INFORMATION | FUEL INFORMATION |  |  |  | TRUE
Primary Fuel Type | Primary Fuel Type |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Secondary Fuel Type | Secondary Fuel Type |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Fuel Transportation Type | Fuel Transportation Type |  |  |  | TRUE
Resource Category | Resource Category |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
RATINGS AND DESIGNS | RATINGS AND DESIGNS |  |  |  | TRUE
Renewable | Renewable |  |  |  | TRUE
Renewable/Offset | Renewable/Offset |  |  |  | TRUE
Physical Unit Type | Physical Unit Type |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Name Plate Rating | Name Plate Rating |  |  |  | TRUE
Real Power Rating | Real Power Rating |  |  |  | TRUE
Reactive Power Rating | Reactive Power Rating |  |  |  | TRUE
Turbine Rating | Turbine Rating |  |  |  | TRUE
Unit Generating Voltage | Unit Generating Voltage |  |  |  | TRUE
Governor Droop Setting | Governor Droop Setting |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Governor Dead-band | Governor Dead-band |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Design Max Ambient Temperature | Design Max Ambient Temperature |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Design Min Ambient Temperature | Design Min Ambient Temperature |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
GEOGRAPHIC LOCATION (CENTER OF PLANT) | GEOGRAPHIC LOCATION (CENTER OF PLANT) |  |  |  | TRUE
Latitude Of Center Of Plant | Latitude Of Center Of Plant |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Longitude Of Center Of Plant | Longitude Of Center Of Plant |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Unit Info - Train | Unit Info - Train |  |  |  | TRUE
CC TRAIN DETAILS | CC TRAIN DETAILS |  |  |  | TRUE
Train Name | Train Name |  |  |  | TRUE
Train Code | Train Code |  |  |  | TRUE
Non_Moldeled Generator | Non_Moldeled Generator |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
PUC Registration Number | PUC Registration Number |  |  |  | TRUE
NERC Number | NERC Number |  |  |  | TRUE
Qualifying Facility? | Qualifying Facility? |  |  |  | TRUE
SITE AND UNIT DATES | SITE AND UNIT DATES |  |  |  | TRUE
Train Unit Commercial Date | Train Unit Commercial Date |  |  |  | TRUE
Train Unit End Date | Train Unit End Date |  |  |  | TRUE
FUEL INFORMATION | FUEL INFORMATION |  |  |  | TRUE
Fuel Transportation Type | Fuel Transportation Type |  |  |  | TRUE
Resource Category | Resource Category |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
POWER AUGMENTATION | POWER AUGMENTATION |  |  |  | TRUE
Is Train Augmented With Duct Burner(s)? | Is Train Augmented With Duct Burner(s)? |  |  |  | TRUE
Is Train Augmented with Evap Cooler(s)? | Is Train Augmented with Evap Cooler(s)? |  |  |  | TRUE
Is Train augmented with Chiller(s)? | Is Train augmented with Chiller(s)? |  |  |  | TRUE
Other Augmentation? | Other Augmentation? |  |  |  | TRUE
GEOGRAPHIC LOCATION (CENTER OF PLANT) | GEOGRAPHIC LOCATION (CENTER OF PLANT) |  |  |  | TRUE
Latitude of center of Plant | Latitude of center of Plant |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Longitude of center of Plant | Longitude of center of Plant |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Unit Info - CC | Unit Info - CC |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name |  |  |  | TRUE
SITE_CODE | SITE_CODE |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  |  |  | TRUE
ERCOT Interconnection Project Number - Only New Units | ERCOT Interconnection Project Number - Only New Units |  |  |  | TRUE
SITE AND UNIT DATES | SITE AND UNIT DATES |  |  |  | TRUE
Transmission Only Date (POI) | Transmission Only Date (POI) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Standard Generation Interconnection Agreement (SGIA) Signature Date | Standard Generation Interconnection Agreement (SGIA) Signature Date |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Unit Start Date (Model Ready Date) | Unit Start Date (Model Ready Date) | 03/13/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/13/2012 Updated Validation | ADD 04/2012
Unit Commercial Date | Unit Commercial Date |  |  |  | TRUE
Unit End Date | Unit End Date |  |  |  | TRUE
POINT OF INTERCONNECTION | POINT OF INTERCONNECTION |  |  |  | TRUE
SubStation Code/SubStation Mnemonic | SubStation Code/SubStation Mnemonic |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Voltage Level | Voltage Level |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
PTI Bus Number | PTI Bus Number |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
FUEL INFORMATION | FUEL INFORMATION |  |  |  | TRUE
Primary Fuel Type | Primary Fuel Type |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Secondary Fuel Type | Secondary Fuel Type |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
RATINGS AND DESIGNS | RATINGS AND DESIGNS |  |  |  | TRUE
Physical Unit Type | Physical Unit Type |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Name Plate Rating | Name Plate Rating |  |  |  | TRUE
Real Power Rating | Real Power Rating |  |  |  | TRUE
Reactive Power Rating | Reactive Power Rating |  |  |  | TRUE
Turbine Rating | Turbine Rating |  |  |  | TRUE
Unit Generating Voltage | Unit Generating Voltage |  |  |  | TRUE
Governor Droop Setting | Governor Droop Setting |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Governor Dead-band | Governor Dead-band |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Design Max Ambient Temperature | Design Max Ambient Temperature |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Design Min Ambient Temperature | Design Min Ambient Temperature |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Unit Info - Wind | Unit Info - Wind |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name |  |  |  | TRUE
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  |  |  | TRUE
Non_Modeled Generator | Non_Modeled Generator |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
PUC Registration Number | PUC Registration Number |  |  |  | TRUE
ERCOT Interconnection Project Number - only new units | ERCOT Interconnection Project Number - only new units |  |  |  | TRUE
NERC Number | NERC Number |  |  |  | TRUE
Qualifying Facility | Qualifying Facility |  |  |  | TRUE
SITE AND UNIT DATES | SITE AND UNIT DATES |  |  |  | TRUE
Transmission Only Date (POI) | Transmission Only Date (POI) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Standard Generation Interconnection Agreement (SGIA) Signature Date | Standard Generation Interconnection Agreement (SGIA) Signature Date |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Unit Start Date (Model Ready Date) | Unit Start Date (Model Ready Date) | 03/13/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/13/2012 Updated Validation | ADD 04/2012
Unit Commercial Date | Unit Commercial Date |  |  |  | TRUE
Unit End Date | Unit End Date |  |  |  | TRUE
POINT OF INTERCONNECTION | POINT OF INTERCONNECTION |  |  |  | TRUE
SubStation Code/SubStation Mnemonic | SubStation Code/SubStation Mnemonic |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Voltage Level | Voltage Level |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
PTI Bus Number | PTI Bus Number |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
FUEL INFORMATION | FUEL INFORMATION |  |  |  | TRUE
Renewable | Renewable |  |  |  | TRUE
Renewable/Offset | Renewable/Offset |  |  |  | TRUE
Resource Category | Resource Category |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
RATINGS AND DESIGNS | RATINGS AND DESIGNS |  |  |  | TRUE
Physical Unit Type | Physical Unit Type |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Name Plate Rating | Name Plate Rating |  |  |  | TRUE
Real Power Rating | Real Power Rating |  |  |  | TRUE
Reactive Power Rating | Reactive Power Rating |  |  |  | TRUE
Unit Generating Voltage | Unit Generating Voltage |  |  |  | TRUE
Governor Droop Setting | Governor Droop Setting |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Governor Dead-Band | Governor Dead-Band |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Design Max Ambient Temperature | Design Max Ambient Temperature |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Design Min Ambient Temperature | Design Min Ambient Temperature |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
METEOROLOGICAL TOWER AND INSTRUMENTATION INFORMATION | METEOROLOGICAL TOWER AND INSTRUMENTATION INFORMATION |  |  |  | TRUE
Average Height Above Ground Of Turbine Hub | Average Height Above Ground Of Turbine Hub |  |  |  | TRUE
Latitude of Meteorological Tower | Latitude of Meteorological Tower |  |  |  | TRUE
Longitude of Meteorological Tower | Longitude of Meteorological Tower |  |  |  | TRUE
Height of Meteorological Instrumentation - Wind Speed | Height of Meteorological Instrumentation - Wind Speed |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Height of Meteorological Instrumentation - Wind Direction | Height of Meteorological Instrumentation - Wind Direction |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Height of Meteorological Instrumentation - Barometric Pressure | Height of Meteorological Instrumentation - Barometric Pressure |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Height of Meteorological Instrumentation - Temperature | Height of Meteorological Instrumentation - Temperature |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
GEOGRAPHIC LOCATION (CENTER OF PLANT) | GEOGRAPHIC LOCATION (CENTER OF PLANT) |  |  |  | TRUE
Latitude Of Center Of Plant | Latitude Of Center Of Plant |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Longitude Of Center Of Plant | Longitude Of Center Of Plant |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Unit Info - Wind Turbine | Unit Info - Wind Turbine |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Resoure Name (Unit Code/Mnemonic) | Resoure Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
TURBINE DETAILS | TURBINE DETAILS |  |  |  | TRUE
Type of Turbine (Manufacturer/Model) | Type of Turbine (Manufacturer/Model) | Added 02/28/2012 Updated 02/29/2012 Removed all caps |  |  | TRUE | Added 02/28/2012 Updated 02/29/2012 Removed all caps
MW Rating for this model of Turbine | MW Rating for this model of Turbine | Added 02/28/2012 |  |  | TRUE | Added 02/28/2012
Number of this type of Turbine | Number of this type of Turbine | Added 02/28/2012 |  |  | TRUE | Added 02/28/2012
Ownership-GEN | Ownership-GEN |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Ownership Percentages | Ownership Percentages |  |  |  | TRUE
Joint Ownership? | Joint Ownership? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resource Entity Name | Resource Entity Name |  |  |  | TRUE
Resource Duns Number | Resource Duns Number |  |  |  | TRUE
Fixed Ownership | Fixed Ownership |  |  |  | TRUE
Master Owner | Master Owner |  |  |  | TRUE
Ownership Start Date | Ownership Start Date |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Ownership Stop Date | Ownership Stop Date |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Ownership-CC | Ownership-CC |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Train Name | Train Name |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Train Code | Train Code | Corrected 02/23/2012 | ADD 02/2012 |  | TRUE | Corrected 02/23/2012 | ADD 02/2012
Resource Entity Name | Resource Entity Name | Corrected | ADD 04/2012 Existing Field |  | TRUE | Corrected | ADD 04/2012 Existing Field
Resource Duns Number | Resource Duns Number | Corrected | ADD 04/2012 Existing Field |  | TRUE | Corrected | ADD 04/2012 Existing Field
Fixed Ownership | Fixed Ownership | Added Back 02/29/2012 | Ownership - CC |  | TRUE | Added Back 02/29/2012 | Ownership - CC
Master Owner | Master Owner | Added Back 02/29/2012 | Ownership - CC |  | TRUE | Added Back 02/29/2012 | Ownership - CC
Ownership Start Date | Ownership Start Date |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Ownership Stop Date | Ownership Stop Date |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Ownership - WIND | Ownership - WIND |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
OWNERSHIP PERCENTAGES | OWNERSHIP PERCENTAGES |  |  |  | TRUE
Joint Ownership? | Joint Ownership? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resource Entity Name | Resource Entity Name |  |  |  | TRUE
Resource Duns Number | Resource Duns Number |  |  |  | TRUE
Fixed Ownership | Fixed Ownership |  |  |  | TRUE
Master Owner | Master Owner |  |  |  | TRUE
Ownership Start Date | Ownership Start Date |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Ownership Stop Date | Ownership Stop Date |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Parameters - GEN | Parameters - GEN |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
REASONABILITY LIMITS | REASONABILITY LIMITS |  |  |  | TRUE
High Reasonability Limit | High Reasonability Limit |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Low Reasonability Limit | Low Reasonability Limit |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
High Reasonability Ramp Rate Limit | High Reasonability Ramp Rate Limit |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Low Reasonability Ramp Rate Limit | Low Reasonability Ramp Rate Limit |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
SEASONAL RATINGS - SPRING | SEASONAL RATINGS - SPRING |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Spring | Seasonal Net Max Sustainable Rating - Spring |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Sustainable Rating - Spring | Seasonal Net Min Sustainable Rating - Spring |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Max Emergency Rating - Spring | Seasonal Net Max Emergency Rating - Spring |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Emergency Rating - Spring | Seasonal Net Min Emergency Rating - Spring |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
SEASONAL RATINGS - SUMMER | SEASONAL RATINGS - SUMMER |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Summer | Seasonal Net Max Sustainable Rating - Summer |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Sustainable Rating - Summer | Seasonal Net Min Sustainable Rating - Summer |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Max Emergency Rating - Summer | Seasonal Net Max Emergency Rating - Summer |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Emergency Rating - Summer | Seasonal Net Min Emergency Rating - Summer |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
SEASONAL RATINGS - FALL | SEASONAL RATINGS - FALL |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Fall | Seasonal Net Max Sustainable Rating - Fall |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Sustainable Rating - Fall | Seasonal Net Min Sustainable Rating - Fall |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Max Emergency Rating - Fall | Seasonal Net Max Emergency Rating - Fall |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Emergency Rating - Fall | Seasonal Net Min Emergency Rating - Fall |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
SEASONAL RATINGS - WINTER | SEASONAL RATINGS - WINTER |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Winter | Seasonal Net Max Sustainable Rating - Winter |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Sustainable Rating - Winter | Seasonal Net Min Sustainable Rating - Winter |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Max Emergency Rating - Winter | Seasonal Net Max Emergency Rating - Winter |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Emergency Rating - Winter | Seasonal Net Min Emergency Rating - Winter |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES | UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES |  |  |  | TRUE
0°f | 0°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
5°f | 5°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
10°f | 10°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
15°f | 15°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
20°f | 20°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
25°f | 25°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
30°f | 30°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
35°f | 35°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
40°f | 40°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
45°f | 45°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
50°f | 50°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
55°f | 55°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
60°f | 60°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
65°f | 65°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
70°f | 70°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
75°f | 75°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
80°f | 80°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
85°f | 85°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
90°f | 90°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
95°f | 95°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
100°f | 100°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
105°f | 105°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
110°f | 110°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
115°f | 115°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
120°f | 120°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
Parameters - CC | Parameters - CC |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
REASONABILITY LIMITS | REASONABILITY LIMITS |  |  |  | TRUE
High Reasonability Limit | High Reasonability Limit |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Low Reasonability Limit | Low Reasonability Limit |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
High Reasonability Ramp Rate Limit | High Reasonability Ramp Rate Limit |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Low Reasonability Ramp Rate Limit | Low Reasonability Ramp Rate Limit |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
SEASONAL RATINGS - SPRING | SEASONAL RATINGS - SPRING |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Spring | Seasonal Net Max Sustainable Rating - Spring |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Sustainable Rating - Spring | Seasonal Net Min Sustainable Rating - Spring |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Max Emergency Rating - Spring | Seasonal Net Max Emergency Rating - Spring |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Emergency Rating - Spring | Seasonal Net Min Emergency Rating - Spring |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
SEASONAL RATINGS - SUMMER | SEASONAL RATINGS - SUMMER |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Summer | Seasonal Net Max Sustainable Rating - Summer |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Sustainable Rating - Summer | Seasonal Net Min Sustainable Rating - Summer |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Max Emergency Rating - Summer | Seasonal Net Max Emergency Rating - Summer |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Emergency Rating - Summer | Seasonal Net Min Emergency Rating - Summer |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
SEASONAL RATINGS - FALL | SEASONAL RATINGS - FALL |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Fall | Seasonal Net Max Sustainable Rating - Fall |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Sustainable Rating - Fall | Seasonal Net Min Sustainable Rating - Fall |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Max Emergency Rating - Fall | Seasonal Net Max Emergency Rating - Fall |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Emergency Rating - Fall | Seasonal Net Min Emergency Rating - Fall |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
SEASONAL RATINGS - WINTER | SEASONAL RATINGS - WINTER |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Winter | Seasonal Net Max Sustainable Rating - Winter |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Sustainable Rating - Winter | Seasonal Net Min Sustainable Rating - Winter |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Max Emergency Rating - Winter | Seasonal Net Max Emergency Rating - Winter |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Emergency Rating - Winter | Seasonal Net Min Emergency Rating - Winter |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES | UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES |  |  |  | TRUE
0°f | 0°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
5°f | 5°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
10°f | 10°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
15°f | 15°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
20°f | 20°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
25°f | 25°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
30°f | 30°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
35°f | 35°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
40°f | 40°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
45°f | 45°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
50°f | 50°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
55°f | 55°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
60°f | 60°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
65°f | 65°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
70°f | 70°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
75°f | 75°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
80°f | 80°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
85°f | 85°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
90°f | 90°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
95°f | 95°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
100°f | 100°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
105°f | 105°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
110°f | 110°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
115°f | 115°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
120°f | 120°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
Parameters - CFG | Parameters - CFG |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
SITECODE | SITECODE |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Train Code | Train Code | Corrected 02/23/2012 | ADD 02/2012 |  | TRUE | Corrected 02/23/2012 | ADD 02/2012
Configuration Code | Configuration Code |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
REASONABILITY LIMITS | REASONABILITY LIMITS |  |  |  | TRUE
High Reasonability Limit | High Reasonability Limit | PHASE II Updated 03/06/2012 Added Step 4, 5 and 6 | UPDATE 02/2012 |  | TRUE | PHASE II Updated 03/06/2012 Added Step 4, 5 and 6 | UPDATE 02/2012
Low Reasonability Limit | Low Reasonability Limit |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
High Reasonability Ramp Rate Limit | High Reasonability Ramp Rate Limit |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Low Reasonability Ramp Rate Limit | Low Reasonability Ramp Rate Limit |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
SEASONAL RATINGS - SPRING | SEASONAL RATINGS - SPRING |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Spring | Seasonal Net Max Sustainable Rating - Spring |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Sustainable Rating - Spring | Seasonal Net Min Sustainable Rating - Spring |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Max Emergency Rating - Spring | Seasonal Net Max Emergency Rating - Spring |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Emergency Rating - Spring | Seasonal Net Min Emergency Rating - Spring |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
SEASONAL RATINGS - SUMMER | SEASONAL RATINGS - SUMMER |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Summer | Seasonal Net Max Sustainable Rating - Summer |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Sustainable Rating - Summer | Seasonal Net Min Sustainable Rating - Summer |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Max Emergency Rating - Summer | Seasonal Net Max Emergency Rating - Summer |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Emergency Rating - Summer | Seasonal Net Min Emergency Rating - Summer |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
SEASONAL RATINGS - FALL | SEASONAL RATINGS - FALL |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Fall | Seasonal Net Max Sustainable Rating - Fall |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Sustainable Rating - Fall | Seasonal Net Min Sustainable Rating - Fall |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Max Emergency Rating - Fall | Seasonal Net Max Emergency Rating - Fall |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Emergency Rating - Fall | Seasonal Net Min Emergency Rating - Fall |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
SEASONAL RATINGS - WINTER | SEASONAL RATINGS - WINTER |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Winter | Seasonal Net Max Sustainable Rating - Winter |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Sustainable Rating - Winter | Seasonal Net Min Sustainable Rating - Winter |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Max Emergency Rating - Winter | Seasonal Net Max Emergency Rating - Winter |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Emergency Rating - Winter | Seasonal Net Min Emergency Rating - Winter |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES | UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES |  |  |  | TRUE
0°f | 0°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
5°f | 5°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
10°f | 10°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
15°f | 15°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
20°f | 20°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
25°f | 25°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
30°f | 30°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
35°f | 35°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
40°f | 40°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
45°f | 45°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
50°f | 50°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
55°f | 55°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
60°f | 60°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
65°f | 65°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
70°f | 70°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
75°f | 75°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
80°f | 80°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
85°f | 85°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
90°f | 90°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
95°f | 95°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
100°f | 100°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
105°f | 105°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
110°f | 110°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
115°f | 115°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
120°f | 120°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
Parameters - WIND | Parameters - WIND |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
REASONABILITY LIMITS | REASONABILITY LIMITS |  |  |  | TRUE
High Reasonability Limit | High Reasonability Limit |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Low Reasonability Limit | Low Reasonability Limit |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
High Reasonability Ramp Rate Limit | High Reasonability Ramp Rate Limit |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Low Reasonability Ramp Rate Limit | Low Reasonability Ramp Rate Limit |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
SEASONAL RATINGS - SPRING | SEASONAL RATINGS - SPRING |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Spring | Seasonal Net Max Sustainable Rating - Spring |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Sustainable Rating - Spring | Seasonal Net Min Sustainable Rating - Spring |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Max Emergency Rating - Spring | Seasonal Net Max Emergency Rating - Spring |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Emergency Rating - Spring | Seasonal Net Min Emergency Rating - Spring |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
SEASONAL RATINGS - SUMMER | SEASONAL RATINGS - SUMMER |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Summer | Seasonal Net Max Sustainable Rating - Summer |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Sustainable Rating - Summer | Seasonal Net Min Sustainable Rating - Summer |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Max Emergency Rating - Summer | Seasonal Net Max Emergency Rating - Summer |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Emergency Rating - Summer | Seasonal Net Min Emergency Rating - Summer |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
SEASONAL RATINGS - FALL | SEASONAL RATINGS - FALL |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Fall | Seasonal Net Max Sustainable Rating - Fall |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Sustainable Rating - Fall | Seasonal Net Min Sustainable Rating - Fall |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Max Emergency Rating - Fall | Seasonal Net Max Emergency Rating - Fall |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Emergency Rating - Fall | Seasonal Net Min Emergency Rating - Fall |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
SEASONAL RATINGS - WINTER | SEASONAL RATINGS - WINTER |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Winter | Seasonal Net Max Sustainable Rating - Winter |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Sustainable Rating - Winter | Seasonal Net Min Sustainable Rating - Winter |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Max Emergency Rating - Winter | Seasonal Net Max Emergency Rating - Winter |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Seasonal Net Min Emergency Rating - Winter | Seasonal Net Min Emergency Rating - Winter |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES | UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES |  |  |  | TRUE
0°f | 0°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
5°f | 5°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
10°f | 10°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
15°f | 15°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
20°f | 20°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
25°f | 25°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
30°f | 30°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
35°f | 35°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
40°f | 40°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
45°f | 45°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
50°f | 50°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
55°f | 55°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
60°f | 60°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
65°f | 65°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
70°f | 70°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
75°f | 75°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
80°f | 80°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
85°f | 85°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
90°f | 90°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
95°f | 95°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
100°f | 100°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
105°f | 105°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
110°f | 110°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
115°f | 115°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
120°f | 120°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
Operational Parameters - GEN | Operational Parameters - GEN |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
RESOURCE PARAMETERS | RESOURCE PARAMETERS |  |  |  | TRUE
Minimum On Line Time | Minimum On Line Time | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Minimum Off Line Time | Minimum Off Line Time | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Hot Start Time | Hot Start Time | Corrected | UPDATE 02/2012 |  | TRUE | Corrected | UPDATE 02/2012
Intermediate Start Time | Intermediate Start Time | Corrected | UPDATE 02/2012 |  | TRUE | Corrected | UPDATE 02/2012
Cold Start Time | Cold Start Time | Corrected | UPDATE 02/2012 |  | TRUE | Corrected | UPDATE 02/2012
Max Weekly Starts | Max Weekly Starts | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Max On Line Time | Max On Line Time | Corrected | UPDATE 02/2012 |  | TRUE | Corrected | UPDATE 02/2012
Max Daily Starts | Max Daily Starts | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Max Weekly Energy | Max Weekly Energy | Corrected | UPDATE 02/2012 |  | TRUE | Corrected | UPDATE 02/2012
Hot-to-intermediate Time | Hot-to-intermediate Time | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Intermediate-to-cold Time | Intermediate-to-cold Time | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Operational Parameters - GEN - NRRC | Operational Parameters - GEN - NRRC |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
NORMAL RAMP RATE CURVE | NORMAL RAMP RATE CURVE |  |  |  | TRUE
MW Number | MW Number |  |  |  | TRUE
NRRC Code | NRRC Code |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
NRRC MW | NRRC MW | PHASE II Updated 03/06/2012 Added Step 5 and 6 | UPDATE 02/2012 |  | TRUE | PHASE II Updated 03/06/2012 Added Step 5 and 6 | UPDATE 02/2012
Upward Ramprate | Upward Ramprate | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Downward Ramprate | Downward Ramprate | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Operational Parameters - GEN - ERRC | Operational Parameters - GEN - ERRC |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
EMERGENCY RAMP RATE CURVE | EMERGENCY RAMP RATE CURVE |  |  |  | TRUE
MW Number | MW Number |  |  |  | TRUE
ERRC Code | ERRC Code |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
ERRC MW | ERRC MW | PHASE II Updated 03/06/2012 Added Step 5 and 6 | UPDATE 02/2012 |  | TRUE | PHASE II Updated 03/06/2012 Added Step 5 and 6 | UPDATE 02/2012
Upward Ramprate | Upward Ramprate | Updated 03/06/2012 | UPDATE 02/2012 |  | TRUE | Updated 03/06/2012 | UPDATE 02/2012
Downward Ramprate | Downward Ramprate |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Operational Parameters - CFG | Operational Parameters - CFG |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
SITECODE | SITECODE |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Train Code | Train Code |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Configuration Code | Configuration Code |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
RESOURCE PARAMETERS | RESOURCE PARAMETERS |  |  |  | TRUE
Minimum On Line Time | Minimum On Line Time | Corrected | UPDATE 02/2012 |  | TRUE | Corrected | UPDATE 02/2012
Minimum Off Line Time | Minimum Off Line Time | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Hot Start Time | Hot Start Time | Corrected | UPDATE 02/2012 |  | TRUE | Corrected | UPDATE 02/2012
Intermediate Start Time | Intermediate Start Time | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Cold Start Time | Cold Start Time | Corrected | UPDATE 02/2012 |  | TRUE | Corrected | UPDATE 02/2012
Max Weekly Starts | Max Weekly Starts | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Max On Line Time | Max On Line Time | Corrected | UPDATE 02/2012 |  | TRUE | Corrected | UPDATE 02/2012
Max Daily Starts | Max Daily Starts | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Max Weekly Energy | Max Weekly Energy | Corrected | UPDATE 02/2012 |  | TRUE | Corrected | UPDATE 02/2012
Hot-to-intermediate Time | Hot-to-intermediate Time | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Intermediate-to-cold Time | Intermediate-to-cold Time | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Operational Parameters - NRRC | Operational Parameters - NRRC |  |  |  | TRUE
Train Code | Train Code | Corrected 02/23/2012 | ADD 02/2012 |  | TRUE | Corrected 02/23/2012 | ADD 02/2012
Configuration Code | Configuration Code |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
NORMAL RAMP RATE CURVE | NORMAL RAMP RATE CURVE |  |  |  | TRUE
MW Number | MW Number |  |  |  | TRUE
NRRC Code | NRRC Code |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
NRRC MW | NRRC MW | PHASE II Updated 03/06/2012 Added Step 5 and 6 | UPDATE 02/2012 |  | TRUE | PHASE II Updated 03/06/2012 Added Step 5 and 6 | UPDATE 02/2012
Upward Ramprate | Upward Ramprate | Updated 03/06/2012 | UPDATE 02/2012 |  | TRUE | Updated 03/06/2012 | UPDATE 02/2012
Downward Ramprate | Downward Ramprate |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Operational Parameters - ERRC | Operational Parameters - ERRC |  |  |  | TRUE
Train Code | Train Code | Corrected 02/23/2012 | ADD 02/2012 |  | TRUE | Corrected 02/23/2012 | ADD 02/2012
Configuration Code | Configuration Code |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
EMERGENCY RAMP RATE CURVE | EMERGENCY RAMP RATE CURVE |  |  |  | TRUE
MW Number | MW Number |  |  |  | TRUE
ERRC Code | ERRC Code |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
ERRC MW | ERRC MW | PHASE II Updated 03/06/2012 Added Step 5 and 6 | UPDATE 02/2012 |  | TRUE | PHASE II Updated 03/06/2012 Added Step 5 and 6 | UPDATE 02/2012
Upward Ramprate | Upward Ramprate |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Downward Ramprate | Downward Ramprate |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Operational Parameters - WIND | Operational Parameters - WIND |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
RESOURCE PARAMETERS | RESOURCE PARAMETERS |  |  |  | TRUE
Minimum On Line Time | Minimum On Line Time | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Minimum Off Line Time | Minimum Off Line Time | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Hot Start Time | Hot Start Time | Corrected | UPDATE 02/2012 |  | TRUE | Corrected | UPDATE 02/2012
Intermediate Start Time | Intermediate Start Time | Corrected | UPDATE 02/2012 |  | TRUE | Corrected | UPDATE 02/2012
Cold Start Time | Cold Start Time | Corrected | UPDATE 02/2012 |  | TRUE | Corrected | UPDATE 02/2012
Max Weekly Starts | Max Weekly Starts | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Max On Line Time | Max On Line Time | Corrected | UPDATE 02/2012 |  | TRUE | Corrected | UPDATE 02/2012
Max Daily Starts | Max Daily Starts | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Max Weekly Energy | Max Weekly Energy | Corrected | UPDATE 02/2012 |  | TRUE | Corrected | UPDATE 02/2012
Hot-to-Intermediate Time | Hot-to-Intermediate Time | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Intermediate-to-Cold Time | Intermediate-to-Cold Time | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Operational Parameters - Wind - NRRC | Operational Parameters - Wind - NRRC |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
NORMAL RAMP RATE CURVE | NORMAL RAMP RATE CURVE |  |  |  | TRUE
MW Number | MW Number |  |  |  | TRUE
NRRC Code | NRRC Code |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
NRRC MW | NRRC MW | PHASE II Updated 03/06/2012 Added Step 5 and 6 | UPDATE 02/2012 |  | TRUE | PHASE II Updated 03/06/2012 Added Step 5 and 6 | UPDATE 02/2012
Upward Ramprate | Upward Ramprate | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Downward Ramprate | Downward Ramprate | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Operational Parameters - Wind - ERRC | Operational Parameters - Wind - ERRC |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
EMERGENCY RAMP RATE CURVE | EMERGENCY RAMP RATE CURVE |  |  |  | TRUE
MW Number | MW Number |  |  |  | TRUE
ERRC Code | ERRC Code |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
ERRC MW | ERRC MW | PHASE II Updated 03/06/2012 Added Step 5 and 6 | UPDATE 02/2012 |  | TRUE | PHASE II Updated 03/06/2012 Added Step 5 and 6 | UPDATE 02/2012
Upward Ramprate | Upward Ramprate | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Downward Ramprate | Downward Ramprate | Check | UPDATE 02/2012 |  | TRUE | Check | UPDATE 02/2012
Reactive Capability - GEN | Reactive Capability - GEN |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
REACTIVE CAPABILITY CURVES DETAILS | REACTIVE CAPABILITY CURVES DETAILS |  |  |  | TRUE
Reactive Capability Data Provided Below Is Gross/Net Values? | Reactive Capability Data Provided Below Is Gross/Net Values? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Reactive Capability Data Provided Below Is From NDCRC Test Data? | Reactive Capability Data Provided Below Is From NDCRC Test Data? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
If Reactive Capability Data Provided Below Is From NDCRC Test Data Then Enter The Date On Which The Test Was Performed. | If Reactive Capability Data Provided Below Is From NDCRC Test Data Then Enter The Date On Which The Test Was Performed. |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Mw1 | Mw1 |  |  |  | TRUE
Lagging MVAR limit associated with Mw1 output | Lagging MVAR limit associated with Mw1 output |  |  |  | TRUE
Leading MVAR limit associated with Mw1 output | Leading MVAR limit associated with Mw1 output |  |  |  | TRUE
Mw2 | Mw2 |  |  |  | TRUE
Lagging MVAR limit associated with Mw2 output | Lagging MVAR limit associated with Mw2 output |  |  |  | TRUE
Leading MVAR limit associated with Mw2 output | Leading MVAR limit associated with Mw2 output |  |  |  | TRUE
Mw3 | Mw3 |  |  |  | TRUE
Lagging MVAR limit associated with Mw3 output | Lagging MVAR limit associated with Mw3 output |  |  |  | TRUE
Leading MVAR limit associated with Mw3 output | Leading MVAR limit associated with Mw3 output |  |  |  | TRUE
Mw4 | Mw4 |  |  |  | TRUE
Lagging MVAR limit associated with Mw4 output | Lagging MVAR limit associated with Mw4 output |  |  |  | TRUE
Leading MVAR limit associated with Mw4 output | Leading MVAR limit associated with Mw4 output |  |  |  | TRUE
Mw5 - Unity Power Factor | Mw5 - Unity Power Factor |  |  |  | TRUE
If Hydrogen Cooled, Indicate Hydrogen Pressure (PSI) Associated With Your Reactive Curve Submitted For ERCOT Studies | If Hydrogen Cooled, Indicate Hydrogen Pressure (PSI) Associated With Your Reactive Curve Submitted For ERCOT Studies |  |  |  | TRUE
Maximum Lagging Operating Capability | Maximum Leading Operating Capability (MVAR) |  |  |  | FALSE
Maximum Leading Operating Capability | Maximum Lagging Operating Capability (MVAR) |  |  |  | FALSE
Manufacturer's Capability Curve submitted? | Manufacturer's Capability Curve submitted? |  |  |  | TRUE
Reactive Capability - CC | Reactive Capability - CC |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
SITE_CODE | SITE_CODE |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
REACTIVE CAPABILITY CURVES DETAILS | REACTIVE CAPABILITY CURVES DETAILS |  |  |  | TRUE
Reactive Capability Data Provided is Gross/Net Values? | Reactive Capability Data Provided is Gross/Net Values? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Reactive Capability Data Provided is from NDCRC Test Data? | Reactive Capability Data Provided is from NDCRC Test Data? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
If Reactive Capability Data Provided Is From NDCRC test Data Then Enter The Date On Which The Test Was Performed. | If Reactive Capability Data Provided Is From NDCRC test Data Then Enter The Date On Which The Test Was Performed. |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Mw1 | Mw1 |  |  |  | TRUE
Lagging MVAR Limit Associated With Mw1 Output | Lagging MVAR Limit Associated With Mw1 Output |  |  |  | TRUE
Leading MVAR Limit Associated With Mw1 Output | Leading MVAR Limit Associated With Mw1 Output |  |  |  | TRUE
Mw2 | Mw2 |  |  |  | TRUE
Lagging MVAR Limit Associated With Mw2 Output | Lagging MVAR Limit Associated With Mw2 Output |  |  |  | TRUE
Leading MVAR Limit Associated With Mw2 Output | Leading MVAR Limit Associated With Mw2 Output |  |  |  | TRUE
Mw3 | Mw3 |  |  |  | TRUE
Lagging MVAR Limit Associated With Mw3 Output | Lagging MVAR Limit Associated With Mw3 Output |  |  |  | TRUE
Leading MVAR Limit Associated With Mw3 Output | Leading MVAR Limit Associated With Mw3 Output |  |  |  | TRUE
Mw4 | Mw4 |  |  |  | TRUE
Lagging MVAR Limit Associated With Mw4 Output | Lagging MVAR Limit Associated With Mw4 Output |  |  |  | TRUE
Leading MVAR Limit Associated With Mw4 Output | Leading MVAR Limit Associated With Mw4 Output |  |  |  | TRUE
Mw5 - Unity Power Factor | Mw5 - Unity Power Factor |  |  |  | TRUE
If Hydrogen Cooled, Indicate Hydrogen Pressure (PSI) Associated With Your Reactive Curve Submitted For ERCOT Studies | If Hydrogen Cooled, Indicate Hydrogen Pressure (PSI) Associated With Your Reactive Curve Submitted For ERCOT Studies |  |  |  | TRUE
Maximum Lagging Operating Capability | Maximum Lagging Operating Capability |  |  |  | TRUE
Maximum Leading Operating Capability | Maximum Leading Operating Capability |  |  |  | TRUE
Manufacturer's Capability Curve Submitted? | Manufacturer's Capability Curve Submitted? |  |  |  | TRUE
Reactive Capability - WIND | Reactive Capability - WIND |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
REACTIVE CAPABILITY CURVES DETAILS | REACTIVE CAPABILITY CURVES DETAILS |  |  |  | TRUE
Reactive Capability Data Provided Below Is Gross/Net Values? | Reactive Capability Data Provided Below Is Gross/Net Values? | Corrected List value Gross or Net 03/05/2012 | ADD 04/2012 |  | TRUE | Corrected List value Gross or Net 03/05/2012 | ADD 04/2012
Reactive Capability Data Provided is from NDCRC Test Data? | Reactive Capability Data Provided is from NDCRC Test Data? | Corrected Label 03/05/2012 | ADD 04/2012 |  | TRUE | Corrected Label 03/05/2012 | ADD 04/2012
If Reactive Capability Data Provided Is From NDCRC test Data Then Enter The Date On Which The Test Was Performed. | If Reactive Capability Data Provided Is From NDCRC test Data Then Enter The Date On Which The Test Was Performed. | Corrected Label 03/05/2012 | ADD 04/2012 |  | TRUE | Corrected Label 03/05/2012 | ADD 04/2012
Mw1 | Mw1 | Corrected Label 03/05/2012 |  |  | TRUE | Corrected Label 03/05/2012
Lagging MVAR Limit Associated With Mw1 Output | Lagging MVAR Limit Associated With Mw1 Output | Corrected Label 03/05/2012 |  |  | TRUE | Corrected Label 03/05/2012
Leading MVAR Limit Associated With Mw1 Output | Leading MVAR Limit Associated With Mw1 Output | Corrected Label 03/05/2012 |  |  | TRUE | Corrected Label 03/05/2012
Mw2 | Mw2 | Corrected Label 03/05/2012 |  |  | TRUE | Corrected Label 03/05/2012
Lagging MVAR Limit Associated With Mw2 Output | Lagging MVAR Limit Associated With Mw2 Output | Corrected Label 03/05/2012 |  |  | TRUE | Corrected Label 03/05/2012
Leading MVAR Limit Associated With Mw2 Output | Leading MVAR Limit Associated With Mw2 Output | Corrected Label 03/05/2012 |  |  | TRUE | Corrected Label 03/05/2012
Mw3 | Mw3 | Corrected Label 03/05/2012 |  |  | TRUE | Corrected Label 03/05/2012
Lagging MVAR Limit Associated With Mw3 Output | Lagging MVAR Limit Associated With Mw3 Output | Corrected Label 03/05/2012 |  |  | TRUE | Corrected Label 03/05/2012
Leading MVAR Limit Associated With Mw3 Output | Leading MVAR Limit Associated With Mw3 Output | Corrected Label 03/05/2012 |  |  | TRUE | Corrected Label 03/05/2012
Mw4 | Mw4 | Corrected Label 03/05/2012 |  |  | TRUE | Corrected Label 03/05/2012
Lagging MVAR Limit Associated With Mw4 Output | Lagging MVAR Limit Associated With Mw4 Output | Corrected Label 03/05/2012 |  |  | TRUE | Corrected Label 03/05/2012
Leading MVAR Limit Associated With Mw4 Output | Leading MVAR Limit Associated With Mw4 Output | Corrected Label 03/05/2012 |  |  | TRUE | Corrected Label 03/05/2012
Maximum Lagging Operating Capability (MVAR) | Maximum Leading Operating Capability |  |  |  | FALSE
Maximum Leading Operating Capability (MVAR) | Maximum Lagging Operating Capability |  |  |  | FALSE
Manufacturer's Capability Curve Submitted? | Manufacturer's Capability Curve Submitted? |  |  |  | TRUE
CC Configurations | CC Configurations |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
TRAIN CODE | TRAIN CODE | Corrected 02/23/2012 | ADD 02/2012 |  | TRUE | Corrected 02/23/2012 | ADD 02/2012
SITE CODE | SITE CODE |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
CONFIGURATION DETAILS | CONFIGURATION DETAILS |  |  |  | TRUE
Configuration # | Configuration # |  |  |  | TRUE
Configuration Code | Configuration Code |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Configuration Type | Configuration Type |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
CC Transitions | CC Transitions |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Sitecode | Sitecode |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Mnemonic for Combine Cyle Train | Mnemonic for Combine Cyle Train |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Configuration Code From | Configuration Code From |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Configuration Code To | Configuration Code To |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Planning - GEN | Planning - GEN |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
PLANNING DETAILS | PLANNING DETAILS |  |  |  | TRUE
What Is The Mva Base That The Following Data Is Based On? | What Is The Mva Base That The Following Data Is Based On? |  |  |  | TRUE
What Is The Kv Base That The Following Data Is Based On? | What Is The Kv Base That The Following Data Is Based On? |  |  |  | TRUE
Direct Axis Subtransient Reactance, X"di (unsaturated) | Direct Axis Subtransient Reactance, X"di (unsaturated) |  |  |  | TRUE
Direct Axis Transient Reactance, X'di (unsaturated) | Direct Axis Transient Reactance, X'di (unsaturated) |  |  |  | TRUE
Positive Sequence Z (unsaturated) | Positive Sequence Z (unsaturated) |  |  |  | TRUE
Positive Sequence Z (unsaturated) | Positive Sequence Z (unsaturated) |  |  |  | TRUE
Negative Sequence Z (unsaturated) | Negative Sequence Z (unsaturated) |  |  |  | TRUE
Negative Sequence Z (unsaturated) | Negative Sequence Z (unsaturated) |  |  |  | TRUE
Does Zero Sequence Z exist? | Does Zero Sequence Z exist? |  |  |  | TRUE
Zero Sequence Z (unsaturated) | Zero Sequence Z (unsaturated) |  |  |  | TRUE
Zero Sequence Z (unsaturated) | Zero Sequence Z (unsaturated) |  |  |  | TRUE
Direct Axis Subtransient Reactance, X"dv (saturated) | Direct Axis Subtransient Reactance, X"dv (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Direct Axis Transient Reactance, X'dv (saturated) | Direct Axis Transient Reactance, X'dv (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Positive Sequence Z (saturated) | Positive Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Positive Sequence Z (saturated) | Positive Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Negative Sequence Z (saturated) | Negative Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Negative Sequence Z (saturated) | Negative Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Z (saturated) | Zero Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Z (saturated) | Zero Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Resistance In P.u. (100 Mva Base) | Zero Sequence Resistance In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Reactance In P.u. (100 Mva Base) | Zero Sequence Reactance In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
GENERATOR AUXILIARY LOAD | GENERATOR AUXILIARY LOAD |  |  |  | TRUE
Average Amount of Auxiliary Real Power | Average Amount of Auxiliary Real Power |  |  |  | TRUE
Average Amount of Auxiliary Reactive Power | Average Amount of Auxiliary Reactive Power |  |  |  | TRUE
Auxilary Load Power Factor | Auxilary Load Power Factor |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Generation Auxiliary Load Characteristics for Mw Load | Generation Auxiliary Load Characteristics for Mw Load |  |  |  | TRUE
Large Motor, Percent Of Total Mw Load | Large Motor, Percent Of Total Mw Load |  |  |  | TRUE
Small Motor, Percent Of Total Mw Load | Small Motor, Percent Of Total Mw Load |  |  |  | TRUE
Resistive (heating) Load, Percent Of Total Mw Load | Resistive (heating) Load, Percent Of Total Mw Load |  |  |  | TRUE
Discharge Lighting, Percent Of Total Mw Load | Discharge Lighting, Percent Of Total Mw Load |  |  |  | TRUE
Other, Percent Of Total Mw Load | Other, Percent Of Total Mw Load |  |  |  | TRUE
Generation Auxiliary Load Characteristics For MVAR Load | Generation Auxiliary Load Characteristics For MVAR Load |  |  |  | TRUE
Large Motor, Percent Of Total Mvar Load | Large Motor, Percent Of Total Mvar Load |  |  |  | TRUE
Small Motor, Percent Of Total Mvar Load | Small Motor, Percent Of Total Mvar Load |  |  |  | TRUE
Discharge Lighting, Percent Of Total Mvar Load | Discharge Lighting, Percent Of Total Mvar Load |  |  |  | TRUE
Other, Percent Of Total Mvar Load | Other, Percent Of Total Mvar Load |  |  |  | TRUE
PSSE MODEL : THE FOLLOWING LIST OF FILES ARE REQUIRED TO BE SUBMITTED IF THIS IS AN INITIAL REGISTRATION OR IF THERE ARE CHANGES MODIFYING PREVIOUSLY SUBMITTED PSSE FILES. PLEASE INCLUDE ALL PSSE FILES IN A ZIP OR COMPRESSED FOLDER FILE ALONG WITH YOUR RARF SUBMITTAL IN THE SAME SERVICE REQUEST. | PSSE MODEL : THE FOLLOWING LIST OF FILES ARE REQUIRED TO BE SUBMITTED IF THIS IS AN INITIAL REGISTRATION OR IF THERE ARE CHANGES MODIFYING PREVIOUSLY SUBMITTED PSSE FILES. PLEASE INCLUDE ALL PSSE FILES IN A ZIP OR COMPRESSED FOLDER FILE ALONG WITH YOUR RARF SUBMITTAL IN THE SAME SERVICE REQUEST. |  |  |  | TRUE
Generator Form | Generator Form |  |  |  | TRUE
Turbine-governor Form | Turbine-governor Form |  |  |  | TRUE
Excitation Form | Excitation Form |  |  |  | TRUE
Power System Stabilizer Form (required If There Is A Power System Stabilizer) | Power System Stabilizer Form (required If There Is A Power System Stabilizer) |  |  |  | TRUE
Compensator Form (required If There Is A Compensator) | Compensator Form (required If There Is A Compensator) |  |  |  | TRUE
Over Excitation Limiter Form (required If There Is An Over Excitation Limiter) | Over Excitation Limiter Form (required If There Is An Over Excitation Limiter) |  |  |  | TRUE
Under Excitation Limiter Form (required If There Is An Under Excitation Limiter) | Under Excitation Limiter Form (required If There Is An Under Excitation Limiter) |  |  |  | TRUE
Planning - CC | Planning - CC |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 | Do not show Message on Audit or Delta | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
SITE_CODE | SITE_CODE |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Resource Name (Unit Code/mnemonic) | Resource Name (Unit Code/mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
PLANNING DETAILS | PLANNING DETAILS |  |  |  | TRUE
What Is The Mva Base That The Following Data Is Based On? | What Is The Mva Base That The Following Data Is Based On? |  |  |  | TRUE
What Is The Kv Base That The Following Data Is Based On? | What Is The Kv Base That The Following Data Is Based On? |  |  |  | TRUE
Direct Axis Subtransient Reactance, X"di (unsaturated) | Direct Axis Subtransient Reactance, X"di (unsaturated) |  |  |  | TRUE
Direct Axis Transient Reactance, X'di (unsaturated) | Direct Axis Transient Reactance, X'di (unsaturated) |  |  |  | TRUE
Positive Sequence Z (unsaturated) | Positive Sequence Z (unsaturated) |  |  |  | TRUE
Positive Sequence Z (unsaturated) | Positive Sequence Z (unsaturated) |  |  |  | TRUE
Negative Sequence Z (unsaturated) | Negative Sequence Z (unsaturated) |  |  |  | TRUE
Negative Sequence Z (unsaturated) | Negative Sequence Z (unsaturated) |  |  |  | TRUE
Does Zero Sequence Z exist? | Does Zero Sequence Z exist? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Z (unsaturated) | Zero Sequence Z (unsaturated) |  |  |  | TRUE
Zero Sequence Z (unsaturated) | Zero Sequence Z (unsaturated) |  |  |  | TRUE
Direct Axis Subtransient Reactance, X"dv (saturated) | Direct Axis Subtransient Reactance, X"dv (saturated) | Corrected | ADD 04/2012 | Corrected | TRUE | Corrected | ADD 04/2012
Direct Axis Transient Reactance, X'dv (saturated) | Direct Axis Transient Reactance, X'dv (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Positive Sequence Z (saturated) | Positive Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Positive Sequence Z (saturated) | Positive Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Negative Sequence Z (saturated) | Negative Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Negative Sequence Z (saturated) | Negative Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Z (saturated) | Zero Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Z (saturated) | Zero Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Resistance In P.u. (100 Mva Base) | Zero Sequence Resistance In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Reactance In P.u. (100 Mva Base) | Zero Sequence Reactance In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
GENERATOR AUXILIARY LOAD | GENERATOR AUXILIARY LOAD |  |  |  | TRUE
Average Amount of Auxiliary Real Power | Average Amount of Auxiliary Real Power |  |  |  | TRUE
Average Amount of Auxiliary Reactive Power | Average Amount of Auxiliary Reactive Power |  |  |  | TRUE
Auxiliary Load Power Factor | Auxiliary Load Power Factor |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Generation Auxiliary Load Characteristics For Mw Load | Generation Auxiliary Load Characteristics For Mw Load |  |  |  | TRUE
Large Motor, Percent Of Total Mw Load | Large Motor, Percent Of Total Mw Load |  |  |  | TRUE
Small Motor, Percent Of Total Mw Load | Small Motor, Percent Of Total Mw Load |  |  |  | TRUE
Resistive (heating) Load, Percent Of Total Mw Load | Resistive (heating) Load, Percent Of Total Mw Load |  |  |  | TRUE
Discharge Lighting, Percent Of Total Mw Load | Discharge Lighting, Percent Of Total Mw Load |  |  |  | TRUE
Other, Percent Of Total Mw Load | Other, Percent Of Total Mw Load |  |  |  | TRUE
Generation Auxiliary Load Characteristics for MVAR Load | Generation Auxiliary Load Characteristics for MVAR Load |  |  |  | TRUE
Large Motor, Percent Of Total Mvar Load | Large Motor, Percent Of Total Mvar Load |  |  |  | TRUE
Small Motor, Percent Of Total Mvar Load | Small Motor, Percent Of Total Mvar Load |  |  |  | TRUE
Discharge Lighting, Percent Of Total Mvar Load | Discharge Lighting, Percent Of Total Mvar Load |  |  |  | TRUE
Other, Percent Of Total Mvar Load | Other, Percent Of Total Mvar Load |  |  |  | TRUE
PSSE MODEL : THE FOLLOWING LIST OF FILES ARE REQUIRED TO BE SUBMITTED IF THIS IS AN INITIAL REGISTRATION OR IF THERE ARE CHANGES MODIFYING PREVIOUSLY SUBMITTED PSSE FILES. PLEASE INCLUDE ALL PSSE FILES IN A ZIP OR COMPRESSED FOLDER FILE ALONG WITH YOUR RARF SUBMITTAL IN THE SAME SERVICE REQUEST. | PSSE MODEL : THE FOLLOWING LIST OF FILES ARE REQUIRED TO BE SUBMITTED IF THIS IS AN INITIAL REGISTRATION OR IF THERE ARE CHANGES MODIFYING PREVIOUSLY SUBMITTED PSSE FILES. PLEASE INCLUDE ALL PSSE FILES IN A ZIP OR COMPRESSED FOLDER FILE ALONG WITH YOUR RARF SUBMITTAL IN THE SAME SERVICE REQUEST. |  |  |  | TRUE
Generator Form | Generator Form |  |  |  | TRUE
Turbine-governor Form | Turbine-governor Form |  |  |  | TRUE
Excitation Form | Excitation Form |  |  |  | TRUE
Power System Stabilizer Form (required If There Is A Power System Stabilizer) | Power System Stabilizer Form (required If There Is A Power System Stabilizer) |  |  |  | TRUE
Compensator Form (required If There Is A Compensator) | Compensator Form (required If There Is A Compensator) |  |  |  | TRUE
Over Excitation Limiter Form (required If There Is An Over Excitation Limiter) | Over Excitation Limiter Form (required If There Is An Over Excitation Limiter) |  |  |  | TRUE
Under Excitation Limiter Form (required If There Is An Under Excitation Limiter) | Under Excitation Limiter Form (required If There Is An Under Excitation Limiter) |  |  |  | TRUE
Planning - WIND | Planning - WIND |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 | Do not show Message on Audit or Delta | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
Type of Turbine | Type of Turbine | Corrected DB_FIELD 03/01/2012 | ADD 02/2012 | Corrected DB_FIELD 03/01/2012 | TRUE | Corrected DB_FIELD 03/01/2012 | ADD 02/2012
PLANNING DETAILS | PLANNING DETAILS |  |  |  | TRUE
What is the Mva Base That the Following Data Is Based On? | What is the Mva Base That the Following Data Is Based On? |  |  |  | TRUE
What Is The Kv Base That The Following Data Is Based On? | What Is The Kv Base That The Following Data Is Based On? |  |  |  | TRUE
Direct Axis Subtransient Reactance, X"di (unsaturated) | Direct Axis Subtransient Reactance, X"di (unsaturated) |  |  |  | TRUE
Direct Axis Transient Reactance, X'di (unsaturated) | Direct Axis Transient Reactance, X'di (unsaturated) |  |  |  | TRUE
Positive Sequence Z (unsaturated) | Positive Sequence Z (unsaturated) |  |  |  | TRUE
Positive Sequence Z (unsaturated) | Positive Sequence Z (unsaturated) |  |  |  | TRUE
Negative Sequence Z (unsaturated) | Negative Sequence Z (unsaturated) |  |  |  | TRUE
Negative Sequence Z (unsaturated) | Negative Sequence Z (unsaturated) |  |  |  | TRUE
Does Zero Sequence Z exist? | Does Zero Sequence Z exist? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Z (unsaturated) | Zero Sequence Z (unsaturated) |  |  |  | TRUE
Zero Sequence Z (unsaturated) | Zero Sequence Z (unsaturated) |  |  |  | TRUE
Direct Axis Subtransient Reactance, X"dv (saturated) | Direct Axis Subtransient Reactance, X"dv (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Direct Axis Transient Reactance, X'dv (saturated) | Direct Axis Transient Reactance, X'dv (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Positive Sequence Z (saturated) | Positive Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Positive Sequence Z (saturated) | Positive Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Negative Sequence Z (saturated) | Negative Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Negative Sequence Z (saturated) | Negative Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Z (saturated) | Zero Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Z (saturated) | Zero Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Resistance In P.u. (100 Mva Base) | Zero Sequence Resistance In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Reactance In P.u. (100 Mva Base) | Zero Sequence Reactance In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
GENERATOR AUXILIARY LOAD | GENERATOR AUXILIARY LOAD |  |  |  | TRUE
Average Amount Of Auxiliary Real Power | Average Amount Of Auxiliary Real Power |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Average Amount Of Auxiliary Reactive Power | Average Amount Of Auxiliary Reactive Power |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Auxiliary Load Power Factor | Auxiliary Load Power Factor |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
GENERATION AUXILIARY LOAD CHARACTERISTICS FOR MW LOAD | GENERATION AUXILIARY LOAD CHARACTERISTICS FOR MW LOAD |  |  |  | TRUE
Large Motor, Percent Of Total Mw Load | Large Motor, Percent Of Total Mw Load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Small Motor, Percent Of Total Mw Load | Small Motor, Percent Of Total Mw Load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resistive (heating) Load, Percent Of Total Mw Load | Resistive (heating) Load, Percent Of Total Mw Load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Discharge Lighting, Percent Of Total Mw Load | Discharge Lighting, Percent Of Total Mw Load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Other, Percent Of Total Mw Load | Other, Percent Of Total Mw Load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
GENERATION AUXILIARY LOAD CHARACTERISTICS FOR MVAR LOAD | GENERATION AUXILIARY LOAD CHARACTERISTICS FOR MVAR LOAD |  |  |  | TRUE
Large Motor, Percent Of Total MVAR Load | Large Motor, Percent Of Total MVAR Load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Small Motor, Percent Of Total MVAR Load | Small Motor, Percent Of Total MVAR Load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Discharge Lighting, Percent Of Total MVAR Load | Discharge Lighting, Percent Of Total MVAR Load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Other, Percent Of Total MVAR Load | Other, Percent Of Total MVAR Load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
TURBINE STEP-UP TRANSFORMER DATA | TURBINE STEP-UP TRANSFORMER DATA |  |  |  | TRUE
High Side Voltage Level (nominal) | High Side Voltage Level (nominal) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Low Side Voltage Level (nominal) | Low Side Voltage Level (nominal) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
High Side Voltage Connection | High Side Voltage Connection |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Low Side Voltage Connection | Low Side Voltage Connection |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Impedance Z | Impedance Z |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
X/R Ratio | X/R Ratio |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Z | Zero Sequence Z |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence X/R Ratio | Zero Sequence X/R Ratio |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Base Mva For Transformer Data | Base Mva For Transformer Data |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
PSSE MODELS : THE FOLLOWING FILES ARE REQUIRED TO BE SUBMITTED IF NOT LISTED IN THE WIND TURBINE DYNAMIC MODELS AVAILABLE AT ERCOT OR IF ADDITIONAL EQUIPMENT HAS BEEN ADDED TO THE SITE REQUIRING MODEL UPDATES. PLEASE INCLUDE ALL PSSE FILES IN A ZIP OR COMPRESSED FOLDER ALONG WITH YOUR RARF SUBMITTAL SERVICE REQUEST. | PSSE MODELS : THE FOLLOWING FILES ARE REQUIRED TO BE SUBMITTED IF NOT LISTED IN THE WIND TURBINE DYNAMIC MODELS AVAILABLE AT ERCOT OR IF ADDITIONAL EQUIPMENT HAS BEEN ADDED TO THE SITE REQUIRING MODEL UPDATES. PLEASE INCLUDE ALL PSSE FILES IN A ZIP OR COMPRESSED FOLDER ALONG WITH YOUR RARF SUBMITTAL SERVICE REQUEST. |  |  |  | TRUE
PSSE Compatible Wind Generator Models | PSSE Compatible Wind Generator Models |  |  |  | TRUE
Dynamic Reactive Device Form | Dynamic Reactive Device Form |  |  |  | TRUE
Private Network - Site - GEN | Private Network - Site - GEN |  |  |  | TRUE
SITE DETAILS | SITE DETAILS |  |  |  | TRUE
Private Network? | Private Network? |  |  |  | TRUE
PRIVATE NETWORK - SITE INFORMATION | PRIVATE NETWORK - SITE INFORMATION |  |  |  | TRUE
Average Amount Of Self-serve Private Load | Average Amount Of Self-serve Private Load |  |  |  | TRUE
Average Amount Of Self-serve Private Reactive Load | Average Amount Of Self-serve Private Reactive Load |  |  |  | TRUE
Expected Typical Private Network Net Interchange | Expected Typical Private Network Net Interchange |  |  |  | TRUE
Expected Typical Private Network Net Reactive Interchange | Expected Typical Private Network Net Reactive Interchange |  |  |  | TRUE
Private Network Gross Unit Capability | Private Network Gross Unit Capability |  |  |  | TRUE
Private Network Gross Unit Reactive Capability | Private Network Gross Unit Reactive Capability |  |  |  | TRUE
Load Characteristics For MW Load | Load Characteristics For MW Load |  |  |  | TRUE
Large Motor, Percent Of Total | Large Motor, Percent Of Total |  |  |  | TRUE
Small Motor, Percent Of Total | Small Motor, Percent Of Total |  |  |  | TRUE
Resistive (heating) Load, Percent Of Total MW Load | Resistive (heating) Load, Percent Of Total MW Load |  |  |  | TRUE
Discharge Lighting, Percent Of Total | Discharge Lighting, Percent Of Total |  |  |  | TRUE
Other, Percent Of Total MW Load | Other, Percent Of Total MW Load |  |  |  | TRUE
Load Characteristics for MVAR Load | Load Characteristics for MVAR Load |  |  |  | TRUE
Large Motor, Percent Of Total MVAR Load | Large Motor, Percent Of Total MVAR Load |  |  |  | TRUE
Small Motor, Percent Of Total MVAR Load | Small Motor, Percent Of Total MVAR Load |  |  |  | TRUE
Discharge Lighting, Percent Of Total MVAR Load | Discharge Lighting, Percent Of Total MVAR Load |  |  |  | TRUE
Other, Percent Of Total MVAR Load | Other, Percent Of Total MVAR Load |  |  |  | TRUE
Private Network - Unit - GEN | Private Network - Unit - GEN |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 | Do not show Message on Audit or Delta | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
SITE_CODE | SITE_CODE |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Private Network - Unit Information | Private Network - Unit Information |  |  |  | TRUE
Average Amount Of Self-serve Private Load | Average Amount Of Self-serve Private Load |  |  |  | TRUE
Average Amount Of Self-serve Private Reactive Load | Average Amount Of Self-serve Private Reactive Load |  |  |  | TRUE
Expected Typical Private Network Net Interchange | Expected Typical Private Network Net Interchange |  |  |  | TRUE
Expected Typical Private Network Net Reactive Interchange | Expected Typical Private Network Net Reactive Interchange |  |  |  | TRUE
Private Network Gross Unit Capability | Private Network Gross Unit Capability |  |  |  | TRUE
Private Network Gross Unit Reactive Capability | Private Network Gross Unit Reactive Capability |  |  |  | TRUE
If Unit trips, Does Load trip? | If Unit trips, Does Load trip? |  |  |  | TRUE
If yes, Approximate Percentage of Load That Will Trip? | If yes, Approximate Percentage of Load That Will Trip? |  |  |  | TRUE
Private Network - Site - CC | Private Network - Site - CC |  |  |  | TRUE
SITE DETAILS | SITE DETAILS |  |  |  | TRUE
Private Network? | Private Network? |  |  |  | TRUE
PRIVATE NETWORK - SITE INFORMATION | PRIVATE NETWORK - SITE INFORMATION |  |  |  | TRUE
Average Amount Of Self-serve Private Load | Average Amount Of Self-serve Private Load |  |  |  | TRUE
Average Amount Of Self-serve Private Reactive Load | Average Amount Of Self-serve Private Reactive Load |  |  |  | TRUE
Expected Typical Private Network Net Interchange | Expected Typical Private Network Net Interchange |  |  |  | TRUE
Expected Typical Private Network Net Reactive Interchange | Expected Typical Private Network Net Reactive Interchange |  |  |  | TRUE
Private Network Gross Unit Capability | Private Network Gross Unit Capability |  |  |  | TRUE
Private Network Gross Unit Reactive Capability | Private Network Gross Unit Reactive Capability |  |  |  | TRUE
Load Characteristics for MW Load | Load Characteristics for MW Load |  |  |  | TRUE
Large Motor, Percent Of Total | Large Motor, Percent Of Total |  |  |  | TRUE
Small Motor, Percent Of Total | Small Motor, Percent Of Total |  |  |  | TRUE
Resistive (heating) Load, Percent Of Total MW Load | Resistive (heating) Load, Percent Of Total MW Load |  |  |  | TRUE
Discharge Lighting, Percent Of Total | Discharge Lighting, Percent Of Total |  |  |  | TRUE
Other, Percent Of Total MW Load | Other, Percent Of Total MW Load |  |  |  | TRUE
Load Characteristics for MVAR Load | Load Characteristics for MVAR Load |  |  |  | TRUE
Large Motor, Percent Of Total MVAR Load | Large Motor, Percent Of Total MVAR Load |  |  |  | TRUE
Small Motor, Percent Of Total MVAR Load | Small Motor, Percent Of Total MVAR Load |  |  |  | TRUE
Discharge Lighting, Percent Of Total MVAR Load | Discharge Lighting, Percent Of Total MVAR Load |  |  |  | TRUE
Other, Percent Of Total MVAR Load | Other, Percent Of Total MVAR Load |  |  |  | TRUE
Private Network - Unit - CC | Private Network - Unit - CC |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta |  | Do not show Message on Audit or Delta | TRUE | Do not show Message on Audit or Delta
SITE CODE | SITE CODE |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
PRIVATE NETWORK - UNIT INFORMATION | PRIVATE NETWORK - UNIT INFORMATION |  |  |  | TRUE
Average Amount Of Self-serve Private Load | Average Amount Of Self-serve Private Load |  |  |  | TRUE
Average Amount Of Self-serve Private Reactive Load | Average Amount Of Self-serve Private Reactive Load |  |  |  | TRUE
Expected Typical Private Network Net Interchange | Expected Typical Private Network Net Interchange |  |  |  | TRUE
Expected Typical Private Network Net Reactive Interchange | Expected Typical Private Network Net Reactive Interchange |  |  |  | TRUE
Private Network Gross Unit Capability | Private Network Gross Unit Capability |  |  |  | TRUE
Private Network Gross Unit Reactive Capability | Private Network Gross Unit Reactive Capability |  |  |  | TRUE
If Unit Trips, Does Load Trip? | If Unit Trips, Does Load Trip? |  |  |  | TRUE
If Yes, Approximate Percentage Of Load That Will Trip? | If Yes, Approximate Percentage Of Load That Will Trip? |  |  |  | TRUE
Private Network - Site - Wind | Private Network - Site - Wind |  |  |  | TRUE
SITE DETAILS | SITE DETAILS |  |  |  | TRUE
Private Network? | Private Network? |  |  |  | TRUE
PRIVATE NETWORK - SITE INFORMATION | PRIVATE NETWORK - SITE INFORMATION |  |  |  | TRUE
Average Amount of Self-serve Private Load | Average Amount of Self-serve Private Load |  |  |  | TRUE
Average Amount of Self-serve Private Reactive Load | Average Amount of Self-serve Private Reactive Load |  |  |  | TRUE
Expected Typical Private Network Net Interchange | Expected Typical Private Network Net Interchange |  |  |  | TRUE
Expected Typical Private Network Net Reactive Interchange | Expected Typical Private Network Net Reactive Interchange |  |  |  | TRUE
Private Network Gross Unit Capability | Private Network Gross Unit Capability |  |  |  | TRUE
Private Network Gross Unit Reactive Capability | Private Network Gross Unit Reactive Capability |  |  |  | TRUE
Load Characteristics for MW Load | Load Characteristics for MW Load |  |  |  | TRUE
Large Motor, Percent Of Total MW Load | Large Motor, Percent Of Total MW Load |  |  |  | TRUE
Small Motor, Percent Of Total MW Load | Small Motor, Percent Of Total MW Load |  |  |  | TRUE
Resistive (Heating) Load, Percent Of Total MW Load | Resistive (Heating) Load, Percent Of Total MW Load |  |  |  | TRUE
Discharge Lighting, Percent Of Total MW Load | Discharge Lighting, Percent Of Total MW Load |  |  |  | TRUE
Other, Percent Of Total MW Load | Other, Percent Of Total MW Load |  |  |  | TRUE
Load Characteristics for MVAR Load | Load Characteristics for MVAR Load |  |  |  | TRUE
Large Motor, percent of total MVAR load | Large Motor, percent of total MVAR load |  |  |  | TRUE
Small Motor, Percent Of Total MVAR Load | Small Motor, Percent Of Total MVAR Load |  |  |  | TRUE
Discharge Lighting, Percent Of Total MVAR Load | Discharge Lighting, Percent Of Total MVAR Load |  |  |  | TRUE
Other, Percent Of Total MVAR Load | Other, Percent Of Total MVAR Load |  |  |  | TRUE
Private Network - Unit - Wind | Private Network - Unit - Wind |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 | Do not show Message on Audit or Delta | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
SITE CODE | SITE CODE |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
PRIVATE NETWORK - UNIT INFORMATION | PRIVATE NETWORK - UNIT INFORMATION |  |  |  | TRUE
Average Amount Of Self-Serve Private Load | Average Amount Of Self-Serve Private Load |  |  |  | TRUE
Average Amount Of Self-Serve Private Reactive Load | Average Amount Of Self-Serve Private Reactive Load |  |  |  | TRUE
Expected Typical Private Network Net Interchange | Expected Typical Private Network Net Interchange |  |  |  | TRUE
Expected Typical Private Network Net Reactive Interchange | Expected Typical Private Network Net Reactive Interchange |  |  |  | TRUE
Private Network Gross Unit Capability | Private Network Gross Unit Capability |  |  |  | TRUE
Private Network Gross Unit Reactive Capability | Private Network Gross Unit Reactive Capability |  |  |  | TRUE
If Unit trips, does Load trip? | If Unit trips, does Load trip? |  |  |  | TRUE
If yes, approximate percentage of Load that will trip? | If yes, approximate percentage of Load that will trip? |  |  |  | TRUE
General Information - LAAR | General Information - LAAR |  |  |  | TRUE
This submittal is for: | This submittal is for: | 03/09/2012 Already in form added to mapping document |  | 03/09/2012 Already in form added to mapping document | TRUE | 03/09/2012 Already in form added to mapping document
Submittal Information | Submittal Information |  |  |  | TRUE
Date Form Completed: | Date Form Completed: |  |  |  | TRUE
Resource Entity Submitting Form: | Resource Entity Submitting Form: | 03/09/2012 Updated Validation |  | 03/09/2012 Updated Validation | TRUE | 03/09/2012 Already in form added to mapping document
Resource Entity DUNS #: | Resource Entity DUNS #: |  |  |  | TRUE
Primary Contact (name of person ERCOT can contact with questions regarding this form) | Primary Contact (name of person ERCOT can contact with questions regarding this form) |  |  |  | TRUE
Printed Name: | Printed Name: |  |  |  | TRUE
Title: | Title: |  |  |  | TRUE
Phone Number: | Phone Number: |  |  |  | TRUE
E-mail Address: | E-mail Address: |  |  |  | TRUE
Fax Number: | Fax Number: |  |  |  | TRUE
Secondary Contact (if available) | Secondary Contact (if available) |  |  |  | TRUE
Printed Name: | Printed Name: |  |  |  | TRUE
Title: | Title: |  |  |  | TRUE
Phone Number: | Phone Number: |  |  |  | TRUE
E-mail Address: | E-mail Address: |  |  |  | TRUE
Fax Number: | Fax Number: |  |  |  | TRUE
Load Resource Information | Load Resource Information |  |  |  | TRUE
UNIT DETAILS | UNIT DETAILS |  |  |  | TRUE
Common Name for Load Resource | Common Name for Load Resource |  |  |  | TRUE
Dispatch Asset Code (provided by ERCOT) | Dispatch Asset Code (provided by ERCOT) |  |  |  | TRUE
Physical Street Address for Point Of Delivery (POD) | Physical Street Address for Point Of Delivery (POD) |  |  |  | TRUE
Name of City for Point of Delivery (POD) | Name of City for Point of Delivery (POD) |  |  |  | TRUE
Is Load Netted From Generation at ERCOT Read Gensite? | Is Load Netted From Generation at ERCOT Read Gensite? |  |  |  | TRUE
Is Load Behind a NOIE Settlement Meter Point? | Is Load Behind a NOIE Settlement Meter Point? |  |  |  | TRUE
Load Resource Type (CLR/UFR/Interruptible) | Load Resource Type (CLR/UFR/Interruptible) |  |  |  | TRUE
If CLR, will CLR be Dynamically Scheduling? | If CLR, will CLR be Dynamically Scheduling? |  |  |  | TRUE
Load Resource Effective Date | Load Resource Effective Date |  |  |  | TRUE
Load Resource Expiration Date | Load Resource Expiration Date |  |  |  | TRUE
Substation Name for POD | Substation Name for POD |  |  |  | TRUE
Substation Code for POD | Substation Code for POD |  |  |  | TRUE
Transmission Bus POD (PTI Bus No) | Transmission Bus POD (PTI Bus No) |  |  |  | TRUE
Transmission Station Voltage | Transmission Station Voltage |  |  |  | TRUE
Transmission Station Load Name in Network Operations Model | Transmission Station Load Name in Network Operations Model |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Meter Reading Entity (TDSP) | Meter Reading Entity (TDSP) |  |  |  | TRUE
Meter Reading Entity Duns Number | Meter Reading Entity Duns Number |  |  |  | TRUE
ESI-ID assigned to meter | ESI-ID assigned to meter |  |  |  | TRUE
Wholesale Delivery Point? | Wholesale Delivery Point? |  |  |  | TRUE
Load Resource Control Device | Load Resource Control Device |  |  |  | TRUE
ERCOT Load Zone | ERCOT Load Zone |  |  |  | TRUE
Maximum POD Total Load | Maximum POD Total Load |  |  |  | TRUE
Maximum Interruptible Load MW | Maximum Interruptible Load MW |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
High Reasonability Limit | High Reasonability Limit |  |  |  | TRUE
Low Reasonability Limit | Low Reasonability Limit |  |  |  | TRUE
CLR High Reasonability Ramp Rate Limit | CLR High Reasonability Ramp Rate Limit |  |  |  | TRUE
CLR Low Reasonability Ramp Rate Limit | CLR Low Reasonability Ramp Rate Limit |  |  |  | TRUE
Private Use Network? | Private Use Network? |  |  |  | TRUE
Load Resource Parameters | Load Resource Parameters |  |  |  | TRUE
Dispatch Asset Code | Dispatch Asset Code |  |  |  | TRUE
Non-CLR Resource Parameters | Non-CLR Resource Parameters |  |  |  | TRUE
Minimum Interruption Time | Minimum Interruption Time |  |  |  | TRUE
Minimum Restoration Time | Minimum Restoration Time |  |  |  | TRUE
Max WEEKLY Deployments | Max WEEKLY Deployments |  |  |  | TRUE
Max Interruption Time | Max Interruption Time |  |  |  | TRUE
Max DAILY Deployments | Max DAILY Deployments |  |  |  | TRUE
Max Weekly Energy | Max Weekly Energy |  |  |  | TRUE
Minimum Notice Time | Minimum Notice Time |  |  |  | TRUE
CLR Resource Parameters | CLR Resource Parameters |  |  |  | TRUE
Max Deployment Time | Max Deployment Time |  |  |  | TRUE
Max Weekly Energy | Max Weekly Energy |  |  |  | TRUE
CLR - NRRC | CLR - NRRC |  |  |  | TRUE
Dispatch Asset Code | Dispatch Asset Code |  |  |  | TRUE
NORMAL RAMP RATE CURVE | NORMAL RAMP RATE CURVE |  |  |  | TRUE
NRRC MW | NRRC MW |  |  |  | TRUE
Upward Ramprate | Upward Ramprate |  |  |  | TRUE
Downward Ramprate | Downward Ramprate |  |  |  | TRUE
CLR - ERRC | CLR - ERRC |  |  |  | TRUE
Dispatch Asset Code | Dispatch Asset Code |  |  |  | TRUE
EMERGENCY RAMP RATE CURVE | EMERGENCY RAMP RATE CURVE |  |  |  | TRUE
ERRC MW | ERRC MW |  |  |  | TRUE
Upward Ramprate | Upward Ramprate |  |  |  | TRUE
Downward Ramprate | Downward Ramprate |  |  |  | TRUE
Protection - GEN | Protection - GEN |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 | Do not show Message on Audit or Delta | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
PLANT VOLTAGE PROTECTION | PLANT VOLTAGE PROTECTION |  |  |  | TRUE
Breaker Interruption Time | Breaker Interruption Time |  |  |  | TRUE
Instantaneous Undervoltage Trip | Instantaneous Undervoltage Trip |  |  |  | TRUE
Instantaneous Under voltage Trip - Time 1 Time 2 Time 3 Time 4 | Instantaneous Under voltage Trip - Time 1 Time 2 Time 3 Time 4 |  |  |  | TRUE
Instantaneous Under voltage Trip - Undervoltage 1 Undervoltage 2 Undervoltage 3 Undervoltage 4 | Instantaneous Under voltage Trip - Undervoltage 1 Undervoltage 2 Undervoltage 3 Undervoltage 4 |  |  |  | TRUE
Instantaneous Overvoltage Trip | Instantaneous Overvoltage Trip |  |  |  | TRUE
Instantaneous Overvoltage Trip Time 1 Time 2 Time 3 Time 4 | Instantaneous Overvoltage Trip Time 1 Time 2 Time 3 Time 4 |  |  |  | TRUE
Instantaneous Overvoltage Trip - Overvoltage 1 Overvoltage 2 Overvoltage 3 Overvoltage 4 | Instantaneous Overvoltage Trip - Overvoltage 1 Overvoltage 2 Overvoltage 3 Overvoltage 4 |  |  |  | TRUE
PLANT FREQUENCY PROTECTION | PLANT FREQUENCY PROTECTION |  |  |  | TRUE
Instantaneous Underfrequency Trip | Instantaneous Underfrequency Trip |  |  |  | TRUE
Instantaneous Underfrequency Trip Time 1 Time 2 Time 3 Time 4 | Instantaneous Underfrequency Trip Time 1 Time 2 Time 3 Time 4 |  |  |  | TRUE
Instantaneous Underfrequency Trip - Underfrequency 1 Underfrequency 2 Underfrequency 3 Underfrequency 4 | Instantaneous Underfrequency Trip - Underfrequency 1 Underfrequency 2 Underfrequency 3 Underfrequency 4 |  |  |  | TRUE
Instantaneous Overfrequency Trip | Instantaneous Overfrequency Trip |  |  |  | TRUE
Instantaneous Overfrequency Trip Time 1 Time 2 Time 3 Time 4 | Instantaneous Overfrequency Trip Time 1 Time 2 Time 3 Time 4 |  |  |  | TRUE
Instantaneous Overfrequency Trip - Overfrequency 1 Overfrequency 2 Overfrequency 3 Overfrequency 4 | Instantaneous Overfrequency Trip - Overfrequency 1 Overfrequency 2 Overfrequency 3 Overfrequency 4 |  |  |  | TRUE
Protection - CC | Protection - CC |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 | Do not show Message on Audit or Delta | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
SITE_CODE | SITE_CODE |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Resource Name (Unit Code/mnemonic) | Resource Name (Unit Code/mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
PLANT VOLTAGE PROTECTION | PLANT VOLTAGE PROTECTION |  |  |  | TRUE
Breaker Interruption Time | Breaker Interruption Time |  |  |  | TRUE
Instantaneous Undervoltage Trip | Instantaneous Undervoltage Trip |  |  |  | TRUE
Instantaneous Undervoltage Trip - Time 1 Time 2 Time 3 Time 4 | Instantaneous Undervoltage Trip - Time 1 Time 2 Time 3 Time 4 |  |  |  | TRUE
Instantaneous Undervoltage Trip - Undervoltage 1 Undervoltage 2 Undervoltage 3 Undervoltage 4 | Instantaneous Undervoltage Trip - Undervoltage 1 Undervoltage 2 Undervoltage 3 Undervoltage 4 |  |  |  | TRUE
Instantaneous Overvoltage Trip | Instantaneous Overvoltage Trip |  |  |  | TRUE
Instantaneous Overvoltage Trip Time 1 Time 2 Time 3 Time 4 | Instantaneous Overvoltage Trip Time 1 Time 2 Time 3 Time 4 |  |  |  | TRUE
Instantaneous Overvoltage Trip - Overvoltage 1 Overvoltage 2 Overvoltage 3 Overvoltage 4 | Instantaneous Overvoltage Trip - Overvoltage 1 Overvoltage 2 Overvoltage 3 Overvoltage 4 |  |  |  | TRUE
PLANT FREQUENCY PROTECTION | PLANT FREQUENCY PROTECTION |  |  |  | TRUE
Instantaneous Underfrequency Trip | Instantaneous Underfrequency Trip |  |  |  | TRUE
Instantaneous Underfrequency Trip Time 1 Time 2 Time 3 Time 4 | Instantaneous Underfrequency Trip Time 1 Time 2 Time 3 Time 4 |  |  |  | TRUE
Instantaneous Underfrequency Trip - Underfrequency 1 Underfrequency 2 Underfrequency 3 Underfrequency 4 | Instantaneous Underfrequency Trip - Underfrequency 1 Underfrequency 2 Underfrequency 3 Underfrequency 4 |  |  |  | TRUE
Instantaneous Overfrequency Trip | Instantaneous Overfrequency Trip |  |  |  | TRUE
Instantaneous Overfrequency Trip Time 1 Time 2 Time 3 Time 4 | Instantaneous Overfrequency Trip Time 1 Time 2 Time 3 Time 4 |  |  |  | TRUE
Instantaneous Overfrequency Trip - Overfrequency 1 Overfrequency 2 Overfrequency 3 Overfrequency 4 | Instantaneous Overfrequency Trip - Overfrequency 1 Overfrequency 2 Overfrequency 3 Overfrequency 4 |  |  |  | TRUE
Protection - Wind | Protection - Wind |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 | Do not show Message on Audit or Delta | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
SITE CODE | SITE CODE |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
PLANT UNDERVOLTAGE PROTECTION | PLANT UNDERVOLTAGE PROTECTION |  |  |  | TRUE
Breaker Interruption Time | Breaker Interruption Time |  |  |  | TRUE
Instantaneous Undervoltage Trip | Instantaneous Undervoltage Trip |  |  |  | TRUE
Instantaneous Under voltage Trip - Time 1 Time 2 Time 3 Time 4 | Instantaneous Under voltage Trip - Time 1 Time 2 Time 3 Time 4 |  |  |  | TRUE
Instantaneous Undervoltage Trip - Under voltage 1 Under voltage 2 Under voltage 3 | Instantaneous Undervoltage Trip - Under voltage 1 Under voltage 2 Under voltage 3 |  |  |  | TRUE
Instantaneous Overvoltage Trip | Instantaneous Overvoltage Trip |  |  |  | TRUE
Instantaneous Overvoltage Trip Time 1 Time 2 Time 3 Time 4 | Instantaneous Overvoltage Trip Time 1 Time 2 Time 3 Time 4 |  |  |  | TRUE
Instantaneous Overvoltage Trip - Overvoltage 1 Overvoltage 2 Overvoltage 3 Overvoltage 4 | Instantaneous Overvoltage Trip - Overvoltage 1 Overvoltage 2 Overvoltage 3 Overvoltage 4 |  |  |  | TRUE
PLANT OVERFREQUENCY PROTECTION | PLANT OVERFREQUENCY PROTECTION |  |  |  | TRUE
Instantaneous Underfrequency Trip | Instantaneous Underfrequency Trip |  |  |  | TRUE
Instantaneous Underfrequency Trip Time 1 Time 2 Time 3 Time 4 | Instantaneous Underfrequency Trip Time 1 Time 2 Time 3 Time 4 |  |  |  | TRUE
Instantaneous Underfrequency Trip - Under frequency 1 Under frequency 2 Under frequency 3 Under frequency 4 | Instantaneous Underfrequency Trip - Under frequency 1 Under frequency 2 Under frequency 3 Under frequency 4 |  |  |  | TRUE
Instantaneous Overfrequency Trip | Instantaneous Overfrequency Trip |  |  |  | TRUE
Instantaneous Overfrequency Trip Time 1 Time 2 Time 3 Time 4 | Instantaneous Overfrequency Trip Time 1 Time 2 Time 3 Time 4 |  |  |  | TRUE
Instantaneous Overfrequency Trip - Overfrequency 1 Overfrequency 2 Overfrequency 3 Overfrequency 4 | Instantaneous Overfrequency Trip - Overfrequency 1 Overfrequency 2 Overfrequency 3 Overfrequency 4 |  |  |  | TRUE
TURBINE VRT CAPABILITY | TURBINE VRT CAPABILITY |  |  |  | TRUE
Does the Resource Have the Manufacturer's Technical Document / Simulation Results / Test Result, Etc. Describing The Turbine Technology & Vrt OPTIons Purchased With Turbine, If Any | Does the Resource Have the Manufacturer's Technical Document / Simulation Results / Test Result, Etc. Describing The Turbine Technology & Vrt OPTIons Purchased With Turbine, If Any |  |  |  | TRUE
Do Personnel (onsite Operator/engineer Etc.) Have Control To Enable/disable Or Change The Settings For Voltage Ride-through | Do Personnel (onsite Operator/engineer Etc.) Have Control To Enable/disable Or Change The Settings For Voltage Ride-through |  |  |  | TRUE
Does The Resource Use Dynamic Reactive Devices (svc/statcom, Etc.) At The Wind Farm? - (note: Capacitor Banks Used For Conventional Reactive Support Cannot Be Considered As Dynamic Reactive Devices) - If Yes, Please Provide Supporting Documentation. (manufacturer's Technical Document, Pss/e Model Etc.) | Does The Resource Use Dynamic Reactive Devices (svc/statcom, Etc.) At The Wind Farm? - (note: Capacitor Banks Used For Conventional Reactive Support Cannot Be Considered As Dynamic Reactive Devices) - If Yes, Please Provide Supporting Documentation. (manufacturer's Technical Document, Pss/e Model Etc.) |  |  |  | TRUE
Does the Resource Have the Turbine Voltage & Frequency Protection Settings As Per Manufacturer - Technical Document And/or Spec Sheet | Does the Resource Have the Turbine Voltage & Frequency Protection Settings As Per Manufacturer - Technical Document And/or Spec Sheet |  |  |  | TRUE
Does The Resource Have Plant Voltage Protection? If Yes, Please Provide Supporting Documentation. | Does The Resource Have Plant Voltage Protection? If Yes, Please Provide Supporting Documentation. |  |  |  | TRUE
Does The Resource Have Feeder Voltage Protection? If Yes, Please Provide Supporting Documentation. | Does The Resource Have Feeder Voltage Protection? If Yes, Please Provide Supporting Documentation. |  |  |  | TRUE
Collector System - WIND | Collector System - WIND | 03/13/2012 Updated |  |  | TRUE | Corrected Tab name 03/26/2012
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE | Corrected Tab name 03/26/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  |  |  | TRUE | Added field in form 03/26/2012
COLLECTION SYSTEM DETAILED MODEL | COLLECTION SYSTEM DETAILED MODEL | 03/13/2012 Updated |  |  | TRUE | Corrected Tab name 03/26/2012
Cable Type | Cable Type | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
Voltage Level kV | Voltage Level kV | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
POSITIVE SEQUENCE DATA | POSITIVE SEQUENCE DATA | 03/13/2012 Updated |  |  | TRUE | Corrected Tab name 03/26/2012
R/kft | R/kft | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
X/kft | X/kft | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
Charging Bc/kft | Charging Bc/kft | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
ZERO SEQUENCE DATA | ZERO SEQUENCE DATA | 03/13/2012 Updated |  |  | TRUE | Removed Wind from Tab in form 03/26/2012
R0/kft | R0/kft | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
X0/kft | X0/kft | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
Collector System-Wind Seg Data | Collector System-Wind Seg Data | 03/13/2012 Updated |  |  | TRUE | Corrected Tab name 03/26/2012
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE | Corrected Tab name 03/26/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  |  |  | TRUE | Added field in form 03/26/2012
Cable Type | Cable Type | 03/13/2012 Updated |  |  | TRUE | Corrected Tab name 03/26/2012
Cable Type | Cable Type | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
WIND SEGAMENT DETAILS | WIND SEGAMENT DETAILS | 03/13/2012 Updated |  |  | TRUE | Corrected Tab name 03/26/2012
From | From | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
To | To | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
Circuit Number | Circuit Number | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
Voltage Level | Voltage Level | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
Cable Segment Length | Cable Segment Length | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
Number of Turbines on cable segment | Number of Turbines on cable segment | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
Line Data | Line Data |  |  |  | TRUE
DESCRIPTION OF CHANGE | DESCRIPTION OF CHANGE |  |  |  | TRUE
LINE (ANY LENGTH) DETAILS | LINE (ANY LENGTH) DETAILS |  |  |  | TRUE
Line Name | Line Name |  |  |  | TRUE
Line Voltage Level | Line Voltage Level |  |  |  | TRUE
Resistance in P.U. (100 MVA Base) | Resistance in P.U. (100 MVA Base) |  |  |  | TRUE
Reactance in P.U. (100 MVA Base) | Reactance in P.U. (100 MVA Base) |  |  |  | TRUE
Charging Susceptance in PU (100 MVA Base) | Charging Susceptance in PU (100 MVA Base) |  |  |  | TRUE
Zero Sequence Line Resistance In P.u. (100mva Base) | Zero Sequence Line Resistance In P.u. (100mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Line Reactance In P.u. (100mva Base) | Zero Sequence Line Reactance In P.u. (100mva Base) | 03/08/2012 Removed Validation #3 per plaaning group. | ADD 04/2012 | 03/08/2012 Removed Validation #3 per plaaning group. | TRUE | 03/08/2012 Removed Validation #3 per plaaning group. | ADD 04/2012
Zero Sequence Charging Susceptance In P.u. (100mva Base) | Zero Sequence Charging Susceptance In P.u. (100mva Base) | 03/08/2012 Removed Validation #3 per plaaning group. | ADD 04/2012 | 03/08/2012 Removed Validation #3 per plaaning group. | TRUE | 03/08/2012 Removed Validation #3 per plaaning group. | ADD 04/2012
Type (overhead / underground) | Type (overhead / underground) |  |  |  | TRUE
Segment Length | Segment Length |  |  |  | TRUE
TO STATION | TO STATION |  |  |  | TRUE
EROCT STATION TO - Station Code Mnemonic | EROCT STATION TO - Station Code Mnemonic |  |  |  | TRUE
Internal Line | Internal Line |  |  |  | TRUE
TSP Name | TSP Name |  |  |  | TRUE
Connected Device 1 thru 10 | Connected Device 1 thru 10 |  |  |  | TRUE
Bus Number (PTI Bus Number) | Bus Number (PTI Bus Number) |  |  |  | TRUE
Weather Zone / Weather Station (used for Dynamic Ratings) | Weather Zone / Weather Station (used for Dynamic Ratings) |  |  |  | TRUE
FROM Station | FROM Station |  |  |  | TRUE
ERCOT FROM Station Code Mnemonic | ERCOT FROM Station Code Mnemonic |  |  |  | TRUE
Connected Device 1 thru 10 | Connected Device 1 thru 10 |  |  |  | TRUE
Bus Number (PTI Bus Number) | Bus Number (PTI Bus Number) |  |  |  | TRUE
Weather Zone / Weather Station (used for Dynamic Ratings) | Weather Zone / Weather Station (used for Dynamic Ratings) |  |  |  | TRUE
Line Code | Line Code |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
COMMENTS | COMMENTS |  |  |  | TRUE
EFFECTIVE DATE: | EFFECTIVE DATE: |  |  |  | TRUE
Line Temperture | Line Temperture |  |  |  | TRUE
DESCRIPTION OF CHANGE | DESCRIPTION OF CHANGE |  |  |  | TRUE | Added 03/26/2012
Line Name | Line Name |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Line Code | Line Code |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Line Rating | Line Rating |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Nominal | Nominal |  |  |  | TRUE
Continuous Rating | Continuous Rating |  |  |  | TRUE
2-hr Emergency Rating | 2-hr Emergency Rating |  |  |  | TRUE
15-min Rating | 15-min Rating |  |  |  | TRUE
Planning Rate C | Planning Rate C |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Line Temperture | Line Temperture |  |  |  | TRUE
20 °F - Continuous Rating - 115 °F Continuous Rating | 20 °F - Continuous Rating - 115 °F Continuous Rating |  |  |  | TRUE
20 °F - 2-hr Emergency Rating - 115 °F 2-hr Emergency Rating | 20 °F - 2-hr Emergency Rating - 115 °F 2-hr Emergency Rating |  |  |  | TRUE
20 °F - 15-min Rating - 115 °F 15-min Rating | 20 °F - 15-min Rating - 115 °F 15-min Rating |  |  |  | TRUE
Planning Rate C | Planning Rate C | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
Breaker_Switch Data | Breaker_Switch Data |  |  |  | TRUE
DESCRIPTION OF CHANGE | DESCRIPTION OF CHANGE |  |  |  | TRUE
BREAKER / SWITCH | BREAKER / SWITCH |  |  |  | TRUE
Switch Name | Switch Name |  |  |  | TRUE
ERCOT Station Code Mnemonic | ERCOT Station Code Mnemonic |  |  |  | TRUE
Switch Code | Switch Code |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Is this a Fault Isolating Device (e.g. Circuit Breaker) | Is this a Fault Isolating Device (e.g. Circuit Breaker) |  |  |  | TRUE
Normal Operating Status (when in-service) | Normal Operating Status (when in-service) |  |  |  | TRUE
Voltage Level | Voltage Level |  |  |  | TRUE
Static Ratings for Planning | Static Ratings for Planning |  |  |  | TRUE
Continuous Rating | Continuous Rating |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
2-hr Emergency Rating | 2-hr Emergency Rating |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
15 Min Rating | 15 Min Rating |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Side 1 / Side 2 - Directly connected device name(s) | Side 1 / Side 2 - Directly connected device name(s) |  |  |  | TRUE
COMMENTS | COMMENTS |  |  |  | TRUE
EFFECTIVE DATE: | EFFECTIVE DATE: |  |  |  | TRUE
Capacitor or Reactor Data | Capacitor or Reactor Data |  |  |  | TRUE
DESCRIPTION OF CHANGE | DESCRIPTION OF CHANGE |  |  |  | TRUE
Capacitor or Reactor | Capacitor or Reactor |  |  |  | TRUE
Device Name | Device Name |  |  |  | TRUE
ERCOT Station Code Mnemonic | ERCOT Station Code Mnemonic |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Device Code | Device Code |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Capacitor or Reactor | Capacitor or Reactor |  |  |  | TRUE
Nominal MvAR | Nominal MvAR |  |  |  | TRUE
Voltage Level Kv | Voltage Level Kv |  |  |  | TRUE
Bus Number (PTI Bus Number) | Bus Number (PTI Bus Number) |  |  |  | TRUE
Automatic Voltage Regulation | Automatic Voltage Regulation |  |  |  | TRUE
Voltage Level of Busbar being regulated | Voltage Level of Busbar being regulated |  |  |  | TRUE
Desired Regulating voltage | Desired Regulating voltage |  |  |  | TRUE
Minimum Regulating Voltage | Minimum Regulating Voltage |  |  |  | TRUE
Maximum Regulating Voltage | Maximum Regulating Voltage |  |  |  | TRUE
Zero Sequence Reactance Increment In p.u. | Zero Sequence Reactance Increment In p.u. | 03/08/2012 Removed Validation #3 per plaaning group. | ADD 04/2012 |  | TRUE | 03/08/2012 Removed Validation #3 per plaaning group. | ADD 04/2012
Device Name(s) - that this reactive device is directly connected to | Device Name(s) - that this reactive device is directly connected to |  |  |  | TRUE
COMMENTS | COMMENTS |  |  |  | TRUE
EFFECTIVE DATE: | EFFECTIVE DATE: |  |  |  | TRUE
Static Var Compensator Data | Static Var Compensator Data |  |  |  | TRUE
DESCRIPTION OF CHANGE | DESCRIPTION OF CHANGE |  |  |  | TRUE
STATIC VAR COMPENSATOR | STATIC VAR COMPENSATOR |  |  |  | TRUE
SVC Name | SVC Name |  |  |  | TRUE
ERCOT Station Name (Station Code or Station Mnemonic) | ERCOT Station Name (Station Code or Station Mnemonic) |  |  |  | TRUE
SVC CODE | SVC CODE |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
SVC Base Voltage Level | SVC Base Voltage Level |  |  |  | TRUE
Fixed Mvar (var injection At Nominal Voltage) | Fixed Mvar (var injection At Nominal Voltage) |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Minimum Admittance Limits (100 MVA Base) | Minimum Admittance Limits (100 MVA Base) |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Maximum Admittance Limits (100 MVA Base) | Maximum Admittance Limits (100 MVA Base) |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Minimum Steady State Reactive Power Limits | Minimum Steady State Reactive Power Limits |  |  |  | TRUE
Maximum Steady State Reactive Power Limits | Maximum Steady State Reactive Power Limits |  |  |  | TRUE
Minimum Threshold (post Contingency) Reactive Power Limits | Minimum Threshold (post Contingency) Reactive Power Limits |  |  |  | TRUE
Maximum Threshold (post Contingency) Reactive Power Limits | Maximum Threshold (post Contingency) Reactive Power Limits |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Minimum Voltage Threshold | Minimum Voltage Threshold |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Maximum Voltage Threshold | Maximum Voltage Threshold |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Device Name(s) - that this reactive device is directly connected to | Device Name(s) - that this reactive device is directly connected to |  |  |  | TRUE
COMMENTS | COMMENTS |  |  |  | TRUE
EFFECTIVE DATE: | EFFECTIVE DATE: |  |  |  | TRUE
Series Device Data | Series Device Data |  |  |  | TRUE
DESCRIPTION OF CHANGE | DESCRIPTION OF CHANGE |  |  |  | TRUE
SERIES DEVICE DATA | SERIES DEVICE DATA |  |  |  | TRUE
Series Device Name | Series Device Name |  |  |  | TRUE
Ercot Station Code Mnemonic | Ercot Station Code Mnemonic |  |  |  | TRUE
SD Code | SD Code |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Voltage Level | Voltage Level |  |  |  | TRUE
Resistance | Resistance |  |  |  | TRUE
Reactance | Reactance |  |  |  | TRUE
Continuous Rating | Continuous Rating |  |  |  | TRUE
2-hr Emergency Rating | 2-hr Emergency Rating |  |  |  | TRUE
15-min Rating | 15-min Rating |  |  |  | TRUE
Side 1 | Side 1 |  |  |  | TRUE
Side 1 - Connected Switching Device Name(s) | Side 1 - Connected Switching Device Name(s) |  |  |  | TRUE
Side 1 - Bus Number (PTI Bus Number) | Side 1 - Bus Number (PTI Bus Number) |  |  |  | TRUE
Side 2 | Side 2 |  |  |  | TRUE
Side 2 - Connected Switching Device Name(s) | Side 2 - Connected Switching Device Name(s) |  |  |  | TRUE
Side 2 - Bus Number (PTI Bus Number) | Side 2 - Bus Number (PTI Bus Number) |  |  |  | TRUE
COMMENTS | COMMENTS |  |  |  | TRUE
EFFECTIVE DATE: | EFFECTIVE DATE: |  |  |  | TRUE
Transformer Data | Transformer Data |  |  |  | TRUE
DESCRIPTION OF CHANGE | DESCRIPTION OF CHANGE |  |  |  | TRUE
TRANSFORMER DETAILS | TRANSFORMER DETAILS |  |  |  | TRUE
Transformer Name | Transformer Name |  |  |  | TRUE
ERCOT Station Name (Station Code or Station Mnemonic) | ERCOT Station Name (Station Code or Station Mnemonic) |  |  |  | TRUE
Transformer Code | Transformer Code |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Transformer Test Report Attached? | Transformer Test Report Attached? |  |  |  | TRUE
Is this transformer in Master / Follower of Current Balancing configuration? | Is this transformer in Master / Follower of Current Balancing configuration? |  |  |  | TRUE
Master Name (can be same as this transformer) | Master Name (can be same as this transformer) |  |  |  | TRUE
Follower Name (can be same as this transformer) | Follower Name (can be same as this transformer) |  |  |  | TRUE
Generation Step-Up Transformer? | Generation Step-Up Transformer? |  |  |  | TRUE
Zero Sequence Data - Winding Connection Code (1-8) | Zero Sequence Data - Winding Connection Code (1-8) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Grounding Resistance For An Impedance Grounded Transformer In P.u. (100 Mva Base) | Zero Sequence Grounding Resistance For An Impedance Grounded Transformer In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Grounding Reactance For An Impedance Grounded Transformer In P.u. (100 Mva Base) | Zero Sequence Grounding Reactance For An Impedance Grounded Transformer In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Resistance In P.u. (100 Mva Base) | Zero Sequence Resistance In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Reactance In P.u. (100 Mva Base) | Zero Sequence Reactance In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Positive Sequence Resistance (100 MVA Base) | Positive Sequence Resistance (100 MVA Base) |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Positive Sequence Reactance (100 MVA Base) | Positive Sequence Reactance (100 MVA Base) |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Continuous Rating | Continuous Rating |  |  |  | TRUE
2-hr Emergency Rating | 2-hr Emergency Rating |  |  |  | TRUE
15-min Rating | 15-min Rating |  |  |  | TRUE
Unit(s) associated with this transformer | Unit(s) associated with this transformer |  |  |  | TRUE
HIGH SIDE VOLTAGE INFORMATION | HIGH SIDE VOLTAGE INFORMATION |  |  |  | TRUE
High Side Voltage Level (no-load) | High Side Voltage Level (no-load) |  |  |  | TRUE
High Side Voltage Level (PTI) | High Side Voltage Level (PTI) |  |  |  | TRUE
High Side Voltage Connection - Wye or Delta | High Side Voltage Connection - Wye or Delta |  |  |  | TRUE
High Side Voltage Connected devices (list on separate lines) | High Side Voltage Connected devices (list on separate lines) |  |  |  | TRUE
High Side Manufactured Nominal Voltage | High Side Manufactured Nominal Voltage |  |  |  | TRUE
LOW SIDE VOLTAGE INFORMATION | LOW SIDE VOLTAGE INFORMATION |  |  |  | TRUE
Low Side Voltage Level (no-load) | Low Side Voltage Level (no-load) |  |  |  | TRUE
Low Side Voltage Level (PTI) | Low Side Voltage Level (PTI) |  |  |  | TRUE
Low Side Voltage Connection - Wye or Delta | Low Side Voltage Connection - Wye or Delta |  |  |  | TRUE
Low Side Voltage Connected device(s) (list on separate lines) | Low Side Voltage Connected device(s) (list on separate lines) |  |  |  | TRUE
Low Side Manufactured Nominal Voltage | Low Side Manufactured Nominal Voltage |  |  |  | TRUE
VOLTAGE REGULATION | VOLTAGE REGULATION |  |  |  | TRUE
Automatic Voltage Regulation | Automatic Voltage Regulation |  |  |  | TRUE
Does Transformer have a Load Tap Changer? | Does Transformer have a Load Tap Changer? |  |  |  | TRUE
Location of Tap Changer High or Low | Location of Tap Changer High or Low |  |  |  | TRUE
Base Kv of Regulated Side | Base Kv of Regulated Side |  |  |  | TRUE
Target Kv of Regulated Side | Target Kv of Regulated Side |  |  |  | TRUE
Acceptable Deviation of Target Voltage in Percent | Acceptable Deviation of Target Voltage in Percent |  |  |  | TRUE
COMMENTS | COMMENTS |  |  |  | TRUE
EFFECTIVE DATE: | EFFECTIVE DATE: |  |  |  | TRUE
Transformer Tap Settings | Transformer Tap Settings |  |  |  | TRUE
DESCRIPTION OF CHANGE | DESCRIPTION OF CHANGE |  |  |  | TRUE | Added 03/26/2012
Transformer Code | Transformer Code |  | Added to RARF Form for 02/2012 |  | TRUE |  | Added to RARF Form for 02/2012
High-Low Flag | High-Low Flag |  | Added to RARF Form for 02/2012 |  | TRUE |  | Added to RARF Form for 02/2012
TAP SETTINGS | TAP SETTINGS |  |  |  | TRUE
Tap position at Manufactured Nominal Voltage | Tap position at Manufactured Nominal Voltage |  |  |  | TRUE
Total Number of Tap Positions | Total Number of Tap Positions |  |  |  | TRUE
Normal Tap Position | Normal Tap Position |  |  |  | TRUE
Lowest Tap Position | Lowest Tap Position |  |  |  | TRUE
Voltage at Lowest Tap Position | Voltage at Lowest Tap Position |  |  |  | TRUE
Highest Tap Position | Highest Tap Position |  |  |  | TRUE
Voltage at Highest Tap Position | Voltage at Highest Tap Position |  |  |  | TRUE
Size of each Voltage Step | Size of each Voltage Step |  |  |  | TRUE
Load Data | Load Data |  |  |  | TRUE
DESCRIPTION OF CHANGE | DESCRIPTION OF CHANGE |  |  |  | TRUE
Load Data | Load Data |  |  |  | TRUE | Added 03/26/2012
Ercot Station Code Mnemonic | Ercot Station Code Mnemonic |  |  |  | TRUE
Load Name | Load Name |  |  |  | TRUE
Load Code | Load Code |  | UPDATE 02/2012 |  | TRUE |  | UPDATE 02/2012
Load Voltage Level | Load Voltage Level |  |  |  | TRUE
PTI Bus Number | PTI Bus Number |  |  |  | TRUE
Average Load Under Normal Operations | Average Load Under Normal Operations |  |  |  | TRUE
Average Mvar Under Normal Operations | Average Mvar Under Normal Operations |  |  |  | TRUE
Connected Devices | Connected Devices |  |  |  | TRUE
Device Name(s) - that this load is physically connected to | Device Name(s) - that this load is physically connected to |  |  |  | TRUE
Comments | Comments |  |  |  | TRUE
Effective Date: | Effective Date: |  |  |  | TRUE
SubSync - Gen | SubSync - Gen |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta |  |  | TRUE | Do not show Message on Audit or Delta
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  |  |  | TRUE
SUBSYNCHRONOUS RESONANCE | SUBSYNCHRONOUS RESONANCE |  |  |  | TRUE
Mass # | Mass # | Correction 02/28/2012 | NOT IN TABLE |  | TRUE | Correction 02/28/2012 | NOT IN TABLE
Mass Code | Mass Code | Correction |  |  | TRUE | Correction
Name | Name |  |  |  | TRUE
Mass Inertia | Mass Inertia |  |  |  | TRUE
Inertia Units | Inertia Units |  |  |  | TRUE
Associated Damping | Associated Damping |  |  |  | TRUE
Damping Units | Damping Units |  |  |  | TRUE
Stiffness Between Masses Previous and Current Masses | Stiffness Between Masses Previous and Current Masses |  |  |  | TRUE
Stiffness Units | Stiffness Units |  |  |  | TRUE
SubSync - CC | SubSync - CC |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta |  |  | TRUE | Do not show Message on Audit or Delta
SITE_CODE | SITE_CODE |  |  |  | TRUE
Resource Name (Unit Code/mnemonic) | Resource Name (Unit Code/mnemonic) |  |  |  | TRUE
SUBSYNCHRONOUS RESONANCE | SUBSYNCHRONOUS RESONANCE |  |  |  | TRUE
Mass # | Mass # | Correction 02/28/2012 | NOT IN TABLE |  | TRUE | Correction 02/28/2012 | NOT IN TABLE
Mass Code | Mass Code | Correction |  |  | TRUE | Correction
Mass Name | Mass Name |  |  |  | TRUE
Mass Inertia | Mass Inertia |  |  |  | TRUE
Inertia Units | Inertia Units |  |  |  | TRUE
Associated Damping | Associated Damping |  |  |  | TRUE
Damping Units | Damping Units |  |  |  | TRUE
Stiffness Between Masses Previous And Current Mass | Stiffness Between Masses Previous And Current Mass |  |  |  | TRUE
Stiffness Units | Stiffness Units |  |  |  | TRUE
PUN LOAD | PUN LOAD |  |  |  | TRUE
Station Details | Station Details |  |  |  | TRUE
Station Code | Station Code |  | ADD 04/2012 |  | TRUE | 03/27/2012 updated | ADD 04/2012
Load Name | Load Name |  | ADD 04/2012 |  | TRUE | 03/27/2012 updated | ADD 04/2012
Load Code | Load Code |  | ADD 04/2012 |  | TRUE | 03/27/2012 updated | ADD 04/2012
168 HR Data | 168 HR Data |  |  |  | TRUE
Hour Ending | Hour Ending |  | ADD 04/2012 |  | TRUE | 03/27/2012 updated | ADD 04/2012
Day of Week | Day of Week |  | ADD 04/2012 |  | TRUE | 03/27/2012 updated | ADD 04/2012
MW | MW |  | ADD 04/2012 |  | TRUE | 03/27/2012 updated | ADD 04/2012
General Information - ALL | General Information - ALL |  |  |  | TRUE
Reason for Submission | Reason for Submission | Updated 03/09/2012 validation rule to match view | ADD 04/2012 |  | TRUE | Updated 03/09/2012 validation rule to match view | ADD 04/2012
Date Form Completed: | Date Form Completed: |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resource Entity Submitting Form: | Resource Entity Submitting Form: | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
Resource Entity DUNS #: | Resource Entity DUNS #: |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Primary Contact | Primary Contact |  |  |  | TRUE
Printed Name: | Printed Name: |  |  |  | TRUE
Title: | Title: |  |  |  | TRUE
Phone Number: | Phone Number: |  |  |  | TRUE
E-mail Address: | E-mail Address: |  |  |  | TRUE
Fax Number: | Fax Number: |  |  |  | TRUE
Secondary Contact | Secondary Contact |  |  |  | TRUE
Printed Name: | Printed Name: |  |  |  | TRUE
Title: | Title: |  |  |  | TRUE
Phone Number: | Phone Number: |  |  |  | TRUE
E-mail Address: | E-mail Address: |  |  |  | TRUE
Fax Number: | Fax Number: |  |  |  | TRUE
Site Info - DG | Site Info - DG |  |  |  | TRUE
Generator Site Name | Generator Site Name |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Generator Site Code | Generator Site Code |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Address | Address |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
State | State |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
County | County |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Site In-Service Date | Site In-Service Date |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Site Stop Service Date | Site Stop Service Date |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Is generation behind a NOIE Settlement Meter Point? | Is generation behind a NOIE Settlement Meter Point? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
TDSP Providing Service To Gen Site | TDSP Providing Service To Gen Site |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
TDSP DUNS Number | TDSP DUNS Number | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
ESI-ID if H9 is "No" | ESI-ID if H9 is "No" |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
ERCOT Read | ERCOT Read |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Number of EPS Primary meters | Number of EPS Primary meters |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Is Resource claiming status as a Non-Modeled Generator as defined in ERCOT Protocol Section 2, Resource | Is Resource claiming status as a Non-Modeled Generator as defined in ERCOT Protocol Section 2, Resource |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Is Resource >10 MW? | Is Resource >10 MW? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Unit Info - DG | Unit Info - DG |  |  |  | TRUE
Generator Details | Generator Details |  |  |  | TRUE
Unit Name | Unit Name | 03/13/12 Updated Validation Rules | ADD 04/2012 |  | TRUE | 03/13/12 Updated Validation Rules | ADD 04/2012
Unit Code | Unit Code | 03/13/12 Updated Validation Rules | ADD 04/2012 |  | TRUE | 03/13/12 Updated Validation Rules | ADD 04/2012
Unit Dates | Unit Dates |  |  |  | TRUE
Unit Start Date | Unit Start Date | 03/13/12 Updated Validation Rules | ADD 04/2012 |  | TRUE | 03/13/12 Updated Validation Rules | ADD 04/2012
Unit End Date | Unit End Date | 03/13/12 Updated Validation Rules | ADD 04/2012 |  | TRUE | 03/13/12 Updated Validation Rules | ADD 04/2012
Fuel Information | Fuel Information |  |  |  | TRUE
Name Plate Rating | Name Plate Rating | 3/9/2012 Updated Validation and Added to form | ADD 04/2012 |  | TRUE | 3/9/2012 Updated Validation and Added to form | ADD 04/2012
Technology Type | Technology Type | 03/9/2012 Corrected Field name | ADD 04/2012 |  | TRUE | 03/9/2012 Corrected Field name | ADD 04/2012
Name Plate Rating | Name Plate Rating | 3/9/2012 Updated Validation and Added to form | ADD 04/2012 |  | TRUE | 3/9/2012 Updated Validation and Added to form | ADD 04/2012
Renewable | Renewable | 03/9/2012 Corrected Field name | ADD 04/2012 |  | TRUE | 03/9/2012 Corrected Field name | ADD 04/2012
Renewable/Offset | Renewable/Offset | 03/9/2012 Corrected Field name | ADD 04/2012 |  | TRUE | 03/9/2012 Corrected Field name | ADD 04/2012
If Wind, Number of Turbines | If Wind, Number of Turbines | 03/9/2012 Corrected Field name | ADD 04/2012 |  | TRUE | 03/9/2012 Corrected Field name | ADD 04/2012
Physical Unit Type | Physical Unit Type | 03/9/2012 Corrected Field name | ADD 04/2012 |  | TRUE | 03/9/2012 Corrected Field name | ADD 04/2012
Primary Fuel Type | Primary Fuel Type | 03/9/2012 Corrected Field name | ADD 04/2012 |  | TRUE | 03/9/2012 Corrected Field name | ADD 04/2012
Secondary Fuel Type | Secondary Fuel Type | 03/9/2012 Corrected Field name | ADD 04/2012 |  | TRUE | 03/9/2012 Corrected Field name | ADD 04/2012
Private Network Info | Private Network Info |  |  |  | TRUE
Private Network / Cogen | Private Network / Cogen | 03/9/2012 Corrected Field name | ADD 04/2012 |  | TRUE | 03/9/2012 Corrected Field name | ADD 04/2012
Amount of Self Serve for Cogen | Amount of Self Serve for Cogen | 03/9/2012 Corrected Field name | ADD 04/2012 |  | TRUE | 03/9/2012 Corrected Field name | ADD 04/2012
Private Network Net Interchange | Private Network Net Interchange | 03/9/2012 Corrected Field name | ADD 04/2012 |  | TRUE | 03/9/2012 Corrected Field name | ADD 04/2012
Private Network Gross Unit MW | Private Network Gross Unit MW | 03/9/2012 Corrected Field name | ADD 04/2012 |  | TRUE | 03/9/2012 Corrected Field name | ADD 04/2012
Private Network Gross Unit MVAR | Private Network Gross Unit MVAR | 03/9/2012 Corrected Field name | ADD 04/2012 |  | TRUE | 03/9/2012 Corrected Field name | ADD 04/2012
Generic Info | Generic Info |  |  |  | TRUE
Generic Fuel Category | Generic Fuel Category | 03/9/2012 Corrected Field name | ADD 04/2012 |  | TRUE | 03/9/2012 Corrected Field name | ADD 04/2012
Generic Start-up / Operating Category | Generic Start-up / Operating Category | 03/9/2012 Corrected Field name | ADD 04/2012 |  | TRUE | 03/9/2012 Corrected Field name | ADD 04/2012
Resource Owner Data | Resource Owner Data |  |  |  | TRUE
Resource Entity Name | Resource Entity Name | Update 03/13/2012 | ADD 04/2012 |  | TRUE | Update 03/13/2012 | ADD 04/2012
Resource Entity Duns Number | Resource Entity Duns Number | Updated 03/07/2012 | ADD 04/2012 |  | TRUE | Updated 03/07/2012 | ADD 04/2012
UNIT INFO - Solar | UNIT INFO - Solar |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Non Modeled Generation | Non Modeled Generation |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
PUC Registration Number (Docket Number) | PUC Registration Number (Docket Number) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
ERCOT Interconnection Project Number - Only new Units | ERCOT Interconnection Project Number - Only new Units |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
NERC Number (NERC ID#) | NERC Number (NERC ID#) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Qualifying facility | Qualifying facility |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
SITE AND UNIT DATES | SITE AND UNIT DATES |  |  |  | TRUE
Transmission Only Date (POI) | Transmission Only Date (POI) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Standard Generation Interconnection Agreement (SGIA) Signature Date | Standard Generation Interconnection Agreement (SGIA) Signature Date |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Unit Start Date (Model Ready Date) | Unit Start Date (Model Ready Date) | 03/13/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Unit Commercial Date | Unit Commercial Date |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Unit End Date | Unit End Date |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
POINT OF INTERCONNECTION | POINT OF INTERCONNECTION |  |  |  | TRUE
SubStation Code/SubStation Mnemonic | SubStation Code/SubStation Mnemonic |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Voltage Level | Voltage Level |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
PTI Bus Number | PTI Bus Number |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
FUEL INFORMATION | FUEL INFORMATION |  |  |  | TRUE
Primary Fuel Type | Primary Fuel Type |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Secondary Fuel Type | Secondary Fuel Type |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Fuel Transportation Type | Fuel Transportation Type |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resource Category | Resource Category |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
RATINGS AND DESIGNS | RATINGS AND DESIGNS |  |  |  | TRUE
Renewable | Renewable |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Renewable/Offset | Renewable/Offset |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Physical Unit Type | Physical Unit Type |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Name Plate Rating | Name Plate Rating |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Real Power Rating | Real Power Rating |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Reactive Power Rating | Reactive Power Rating |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Unit Generating Voltage | Unit Generating Voltage |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Governor Droop Setting | Governor Droop Setting |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Governor Dead-Band | Governor Dead-Band |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Design Max Ambient Temperature | Design Max Ambient Temperature |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Design Min Ambient Temperature | Design Min Ambient Temperature |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
GEOGRAPHIC LOCATION (CENTER OF PLANT) | GEOGRAPHIC LOCATION (CENTER OF PLANT) |  |  |  | TRUE
Latitude Of Center Of Plant | Latitude Of Center Of Plant |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Longitude Of Center Of Plant | Longitude Of Center Of Plant |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Unit Info - Solar Inverter | Unit Info - Solar Inverter |  |  |  | TRUE
GENERATOR Details | GENERATOR Details |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Total Number of Inverters | Total Number of Inverters |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
MODULE 1 - INVERTER DETAILS | MODULE 1 - INVERTER DETAILS |  |  |  | TRUE | Changed Data Field Name on RARF Form 03/26/2012
Module 1 - Type of INVERTER (Manufacturer/Model) | Module 1 - Type of INVERTER (Manufacturer/Model) |  | ADD 04/2012 |  | TRUE | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012
Module 1 - MW Rating for this model of INVERTER | Module 1 - MW Rating for this model of INVERTER |  | ADD 04/2012 |  | TRUE | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012
Module 1 - Number of this type of INVERTER | Module 1 - Number of this type of INVERTER |  | ADD 04/2012 |  | TRUE | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012
MODULE 2 - INVERTER DETAILS | MODULE 2 - INVERTER DETAILS |  |  |  | TRUE | Changed Data Field Name on RARF Form 03/26/2012
Module 2 - Type of INVERTER (Manufacturer/Model) | Module 2 - Type of INVERTER (Manufacturer/Model) |  | ADD 04/2012 |  | TRUE | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012
Module 2 - MW Rating for this model of INVERTER | Module 2 - MW Rating for this model of INVERTER |  | ADD 04/2012 |  | TRUE | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012
Module 2 - Number of this type of INVERTER | Module 2 - Number of this type of INVERTER |  | ADD 04/2012 |  | TRUE | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012
MODULE 3 - INVERTER DETAILS | MODULE 3 - INVERTER DETAILS |  |  |  | TRUE | Changed Data Field Name on RARF Form 03/26/2012
Module 3 - Type of INVERTER (Manufacturer/Model) | Module 3 - Type of INVERTER (Manufacturer/Model) |  | ADD 04/2012 |  | TRUE | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012
Module 3 - MW Rating for this model of INVERTER | Module 3 - MW Rating for this model of INVERTER |  | ADD 04/2012 |  | TRUE | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012
Module 3 - Number of this type of INVERTER | Module 3 - Number of this type of INVERTER |  | ADD 04/2012 |  | TRUE | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012
MODULE 4 - INVERTER DETAILS | MODULE 4 - INVERTER DETAILS |  |  |  | TRUE | Changed Data Field Name on RARF Form 03/26/2012
Module 4 - Type of INVERTER (Manufacturer/Model) | Module 4 - Type of INVERTER (Manufacturer/Model) |  | ADD 04/2012 |  | TRUE | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012
Module 4 - MW Rating for this model of INVERTER | Module 4 - MW Rating for this model of INVERTER |  | ADD 04/2012 |  | TRUE | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012
Module 4 - Number of this type of INVERTER | Module 4 - Number of this type of INVERTER |  | ADD 04/2012 |  | TRUE | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012
MODULE 5 - INVERTER DETAILS | MODULE 5 - INVERTER DETAILS |  |  |  | TRUE | Changed Data Field Name on RARF Form 03/26/2012
Module 5 - Type of INVERTER (Manufacturer/Model) | Module 5 - Type of INVERTER (Manufacturer/Model) |  | ADD 04/2012 |  | TRUE | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012
Module 5 - MW Rating for this model of INVERTER | Module 5 - MW Rating for this model of INVERTER |  | ADD 04/2012 |  | TRUE | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012
Module 5 - Number of this type of INVERTER | Module 5 - Number of this type of INVERTER |  | ADD 04/2012 |  | TRUE | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012
Site Information - ESG | Site Information - ESG |  |  |  | TRUE
Site Information for ESG Resource | Site Information for ESG Resource |  |  |  | TRUE
Dispatch Asset Code | Dispatch Asset Code |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resource Site Name: | Resource Site Name: |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
ESG Resource Site Code: | ESG Resource Site Code: |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Street Address: | Street Address: |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
City: | City: |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
State | State |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zipcode | Zipcode |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
County: | County: |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Congestion Management Zone for 2003: | Congestion Management Zone for 2003: |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Is Storage Netted From Generation at ERCOT Read Gensite? | Is Storage Netted From Generation at ERCOT Read Gensite? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Is Storage Behind a NOIE Settlement Meter Point? | Is Storage Behind a NOIE Settlement Meter Point? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Will site be acting as a CLR during Charging State? | Will site be acting as a CLR during Charging State? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Load Resource Type (CLR/UFR/Interruptible) | Load Resource Type (CLR/UFR/Interruptible) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
If CLR, will CLR be Dynamically Scheduling? | If CLR, will CLR be Dynamically Scheduling? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Storage Resource Effective Date | Storage Resource Effective Date |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Storage Resource Expiration Date | Storage Resource Expiration Date |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Substation Name for POD | Substation Name for POD |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Substation Code for POD | Substation Code for POD |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Transmission Bus POD (PTI Bus No) | Transmission Bus POD (PTI Bus No) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Voltage Level of Telemetered load(s) | Voltage Level of Telemetered load(s) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Meter Reading Entity (TDSP) | Meter Reading Entity (TDSP) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Meter Reading Entity Duns Number | Meter Reading Entity Duns Number |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
ESI-ID assigned to meter | ESI-ID assigned to meter |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Wholesale Delivery Point? | Wholesale Delivery Point? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Load Resource Control Device | Load Resource Control Device |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
ERCOT Load Zone | ERCOT Load Zone |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Private Use Network? | Private Use Network? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resource owned by NOIE? | Resource owned by NOIE? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Is Resource behind a NOIE Settlement Meter Point? | Is Resource behind a NOIE Settlement Meter Point? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Number of EPS Primary meters: | Number of EPS Primary meters: |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Unit Info - ESG | Unit Info - ESG |  |  |  | TRUE
GENERATOR Details | GENERATOR Details |  |  |  | TRUE
Unit Name | Unit Name |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Non Modeled Generation | Non Modeled Generation |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
PUC Registration Number (Docket Number) | PUC Registration Number (Docket Number) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
ERCOT Interconnection Project Number - only new units | ERCOT Interconnection Project Number - only new units |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
NERC Number (NERC ID#) | NERC Number (NERC ID#) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Qualifying facility | Qualifying facility |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
SITE AND UNIT DATES | SITE AND UNIT DATES |  |  |  | TRUE
Transmission Only Date (POI) | Transmission Only Date (POI) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Standard Generation Interconnection Agreement (SGIA) Signature Date | Standard Generation Interconnection Agreement (SGIA) Signature Date |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Unit Start Date (Model Ready Date) | Unit Start Date (Model Ready Date) | 03/13/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Unit Commercial Date | Unit Commercial Date |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Unit End Date | Unit End Date |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
POINT OF INTERCONNECTION | POINT OF INTERCONNECTION |  |  |  | TRUE
SubStation Code/SubStation Mnemonic | SubStation Code/SubStation Mnemonic |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Voltage Level | Voltage Level |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
PTI Bus Number | PTI Bus Number |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
FUEL INFORMATION | FUEL INFORMATION |  |  |  | TRUE
Energy Storage Technology Type | Energy Storage Technology Type | 03/08/2012 Updated List | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Primary Fuel Type | Primary Fuel Type | 03/08/2012 Updated List | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Secondary Fuel Type | Secondary Fuel Type | 03/08/2012 Updated List | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Fuel Transportation Type | Fuel Transportation Type | 03/08/2012 Updated List | ADD 04/2012 |  | TRUE |  | ADD 04/2012
RATINGS AND DESIGNS | RATINGS AND DESIGNS |  |  |  | TRUE
Renewable | Renewable |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Renewable/Offset | Renewable/Offset |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resource Category | Resource Category | 03/08/2012 Updated List | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Name Plate Rating | Name Plate Rating |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Real Power Rating | Real Power Rating |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Reactive Power Rating | Reactive Power Rating |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Turbine Rating | Turbine Rating |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Unit Generating Voltage | Unit Generating Voltage |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Governor (or equivalent) Droop Setting (%) | Governor (or equivalent) Droop Setting (%) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Governor (or equivalent) Dead-Band (Hz) | Governor (or equivalent) Dead-Band (Hz) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Is Resource Duration Limited (DLR) | Is Resource Duration Limited (DLR) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
DLR sustained energy output for 1 hour | DLR sustained energy output for 1 hour |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Maximum Energy Storage Capability | Maximum Energy Storage Capability |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
GEOGRAPHIC LOCATION (CENTER OF PLANT) | GEOGRAPHIC LOCATION (CENTER OF PLANT) |  |  |  | TRUE
Latitude Of Center Of Plant | Latitude Of Center Of Plant |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Longitude Of Center Of Plant | Longitude Of Center Of Plant |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
SubSync - ESG | SubSync - ESG |  |  |  | TRUE
GENERATOR Details | GENERATOR Details |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
SUBSYNCHRONOUS RESONANCE | SUBSYNCHRONOUS RESONANCE |  |  |  | TRUE
Mass # | Mass # | Correction 02/28/2012 | ADD 04/2012 NOT IN TABLE |  | TRUE | Correction 02/28/2012 | ADD 04/2012 NOT IN TABLE
Mass Name | Mass Name | Change | ADD 04/2012 |  | TRUE | Change | ADD 04/2012
Mass Code | Mass Code | Corrected | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Mass Inertia | Mass Inertia |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Inertia units | Inertia units |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Associated damping | Associated damping |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Damping units | Damping units |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Stiffness Between Masses Previous And Current Mass | Stiffness Between Masses Previous And Current Mass |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Stiffness units | Stiffness units |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Parameters - Solar | Parameters - Solar |  |  |  | TRUE
Generator Details | Generator Details |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Reasonability Limits | Reasonability Limits |  |  |  | TRUE
High Reasonability Limit | High Reasonability Limit |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Low Reasonability Limit | Low Reasonability Limit |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
High Reasonability Ramp Rate Limit | High Reasonability Ramp Rate Limit |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Low Reasonability Ramp Rate Limit | Low Reasonability Ramp Rate Limit |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Ratings Spring | Seasonal Ratings Spring |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Spring | Seasonal Net Max Sustainable Rating - Spring |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Sustainable Rating - Spring | Seasonal Net Min Sustainable Rating - Spring |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Max Emergency Rating - Spring | Seasonal Net Max Emergency Rating - Spring |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Emergency Rating - Spring | Seasonal Net Min Emergency Rating - Spring |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Ratings Summer | Seasonal Ratings Summer |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Summer | Seasonal Net Max Sustainable Rating - Summer |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Sustainable Rating - Summer | Seasonal Net Min Sustainable Rating - Summer |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Max Emergency Rating - Summer | Seasonal Net Max Emergency Rating - Summer |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Emergency Rating - Summer | Seasonal Net Min Emergency Rating - Summer |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Ratings Fall | Seasonal Ratings Fall |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Fall | Seasonal Net Max Sustainable Rating - Fall |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Sustainable Rating - Fall | Seasonal Net Min Sustainable Rating - Fall |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Max Emergency Rating - Fall | Seasonal Net Max Emergency Rating - Fall |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Emergency Rating - Fall | Seasonal Net Min Emergency Rating - Fall |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Ratings Winter | Seasonal Ratings Winter |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Winter | Seasonal Net Max Sustainable Rating - Winter |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Sustainable Rating - Winter | Seasonal Net Min Sustainable Rating - Winter |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Max Emergency Rating - Winter | Seasonal Net Max Emergency Rating - Winter |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Emergency Rating - Winter | Seasonal Net Min Emergency Rating - Winter |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES | UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES |  |  |  | TRUE
0°f | 0°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
5°f | 5°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
10°f | 10°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
15°f | 15°f |  | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
20°f | 20°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
25°f | 25°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
30°f | 30°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
35°f | 35°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
40°f | 40°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
45°f | 45°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
50°f | 50°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
55°f | 55°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
60°f | 60°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
65°f | 65°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
70°f | 70°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
75°f | 75°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
80°f | 80°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
85°f | 85°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
90°f | 90°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
95°f | 95°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
100°f | 100°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
105°f | 105°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
110°f | 110°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
115°f | 115°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
120°f | 120°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
Parameters - ESG Injections | Parameters - ESG Injections |  |  |  | TRUE
Generator Details | Generator Details |  |  |  | TRUE
Unit Name | Unit Name | 03/09/2012 Correct DB Field | ADD 04/2012 |  | TRUE | 03/09/2012 Correct DB Field | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
ESG Parameter Type | ESG Parameter Type |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Reasonability Limits | Reasonability Limits |  |  |  | TRUE
High Reasonability Limit | High Reasonability Limit |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Low Reasonability Limit | Low Reasonability Limit |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
High Reasonability Ramp Rate Limit | High Reasonability Ramp Rate Limit |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Low Reasonability Ramp Rate Limit | Low Reasonability Ramp Rate Limit |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Ratings Spring | Seasonal Ratings Spring |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Spring | Seasonal Net Max Sustainable Rating - Spring |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Sustainable Rating - Spring | Seasonal Net Min Sustainable Rating - Spring |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Max Emergency Rating - Spring | Seasonal Net Max Emergency Rating - Spring |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Emergency Rating - Spring | Seasonal Net Min Emergency Rating - Spring |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Ratings Summer | Seasonal Ratings Summer |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Summer | Seasonal Net Max Sustainable Rating - Summer |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Sustainable Rating - Summer | Seasonal Net Min Sustainable Rating - Summer |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Max Emergency Rating - Summer | Seasonal Net Max Emergency Rating - Summer |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Emergency Rating - Summer | Seasonal Net Min Emergency Rating - Summer |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Ratings Fall | Seasonal Ratings Fall |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Fall | Seasonal Net Max Sustainable Rating - Fall |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Sustainable Rating - Fall | Seasonal Net Min Sustainable Rating - Fall |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Max Emergency Rating - Fall | Seasonal Net Max Emergency Rating - Fall |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Emergency Rating - Fall | Seasonal Net Min Emergency Rating - Fall |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Ratings Winter | Seasonal Ratings Winter |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Winter | Seasonal Net Max Sustainable Rating - Winter |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Sustainable Rating - Winter | Seasonal Net Min Sustainable Rating - Winter |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Max Emergency Rating - Winter | Seasonal Net Max Emergency Rating - Winter |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Emergency Rating - Winter | Seasonal Net Min Emergency Rating - Winter |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES | UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES |  |  |  | TRUE
0°f | 0°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
5°f | 5°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
10°f | 10°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
15°f | 15°f |  | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
20°f | 20°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
25°f | 25°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
30°f | 30°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
35°f | 35°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
40°f | 40°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
45°f | 45°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
50°f | 50°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
55°f | 55°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
60°f | 60°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
65°f | 65°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
70°f | 70°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
75°f | 75°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
80°f | 80°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
85°f | 85°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
90°f | 90°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
95°f | 95°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
100°f | 100°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
105°f | 105°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
110°f | 110°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
115°f | 115°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
120°f | 120°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE | 03/09/2012 Updated Validation | ADD 04/2012
Parameters - ESG Withdrawing | Parameters - ESG Withdrawing |  |  |  | TRUE
Generator Details | Generator Details |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
ESG Parameter Type | ESG Parameter Type |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Reasonability Limits | Reasonability Limits |  |  |  | TRUE
High Reasonability Limit | High Reasonability Limit |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Low Reasonability Limit | Low Reasonability Limit |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
High Reasonability Ramp Rate Limit | High Reasonability Ramp Rate Limit |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Storage High Reasonability Ramp Rate Limit | Storage High Reasonability Ramp Rate Limit |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Low Reasonability Ramp Rate Limit | Low Reasonability Ramp Rate Limit |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
StorageLow Reasonability Ramp Rate Limit | StorageLow Reasonability Ramp Rate Limit |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Ratings Spring | Seasonal Ratings Spring |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Spring | Seasonal Net Max Sustainable Rating - Spring |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Sustainable Rating - Spring | Seasonal Net Min Sustainable Rating - Spring |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Max Emergency Rating - Spring | Seasonal Net Max Emergency Rating - Spring |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Emergency Rating - Spring | Seasonal Net Min Emergency Rating - Spring |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Ratings Summer | Seasonal Ratings Summer |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Summer | Seasonal Net Max Sustainable Rating - Summer |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Sustainable Rating - Summer | Seasonal Net Min Sustainable Rating - Summer |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Max Emergency Rating - Summer | Seasonal Net Max Emergency Rating - Summer |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Emergency Rating - Summer | Seasonal Net Min Emergency Rating - Summer |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Ratings Fall | Seasonal Ratings Fall |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Fall | Seasonal Net Max Sustainable Rating - Fall |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Sustainable Rating - Fall | Seasonal Net Min Sustainable Rating - Fall |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Max Emergency Rating - Fall | Seasonal Net Max Emergency Rating - Fall |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Emergency Rating - Fall | Seasonal Net Min Emergency Rating - Fall |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Ratings Winter | Seasonal Ratings Winter |  |  |  | TRUE
Seasonal Net Max Sustainable Rating - Winter | Seasonal Net Max Sustainable Rating - Winter |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Sustainable Rating - Winter | Seasonal Net Min Sustainable Rating - Winter |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Max Emergency Rating - Winter | Seasonal Net Max Emergency Rating - Winter |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Seasonal Net Min Emergency Rating - Winter | Seasonal Net Min Emergency Rating - Winter |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES | UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES |  |  |  | TRUE
0°f | 0°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
5°f | 5°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
10°f | 10°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
15°f | 15°f |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
20°f | 20°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
25°f | 25°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
30°f | 30°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
35°f | 35°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
40°f | 40°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
45°f | 45°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
50°f | 50°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
55°f | 55°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
60°f | 60°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
65°f | 65°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
70°f | 70°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
75°f | 75°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
80°f | 80°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
85°f | 85°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
90°f | 90°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
95°f | 95°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
100°f | 100°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
105°f | 105°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
110°f | 110°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
115°f | 115°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
120°f | 120°f | 03/09/2012 Updated Validation | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Operational Parameters - Solar | Operational Parameters - Solar |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
RESOURCE PARAMETERS | RESOURCE PARAMETERS |  |  |  | TRUE
Minimum On Line Time | Minimum On Line Time | Check | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Minimum Off Line Time | Minimum Off Line Time | Check | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Hot Start Time | Hot Start Time | Corrected | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Intermediate Start Time | Intermediate Start Time | Corrected | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Cold Start Time | Cold Start Time | Corrected | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Max Weekly Starts | Max Weekly Starts | Check | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Max On Line Time | Max On Line Time | Corrected | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Max Daily Starts | Max Daily Starts | Check | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Max Weekly Energy | Max Weekly Energy | Corrected | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Hot-to-Intermediate Time | Hot-to-Intermediate Time | Check | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Intermediate-to-Cold Time | Intermediate-to-Cold Time | Check | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Operational Parameters - Solar - NRRC | Operational Parameters - Solar - NRRC |  |  |  | TRUE
Generator Details | Generator Details |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Normal Ramp Rate Curve | Normal Ramp Rate Curve |  |  |  | TRUE
MW Number | MW Number |  |  |  | TRUE
NRRC Code | NRRC Code |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
NRRC MW | NRRC MW | PHASE II Updated 03/06/2012 Added Step 5 and 6 | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Upward Ramprate | Upward Ramprate | Check | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Downward Ramprate | Downward Ramprate | Check | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Operational Parameters - Solar - ERRC | Operational Parameters - Solar - ERRC |  |  |  | TRUE
Generator Details | Generator Details |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Emergency Ramp Rate Curve | Emergency Ramp Rate Curve |  |  |  | TRUE
ERRC MW | ERRC MW |  |  |  | TRUE
MW Number | MW Number |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
ERRC Code | ERRC Code | PHASE II Updated 03/06/2012 Added Step 5 and 6 | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Upward Ramprate | Upward Ramprate | Check | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Downward Ramprate | Downward Ramprate | Check | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Oper Parameters - ESG Injections | Oper Parameters - ESG Injections |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
ESG Parameter Type | ESG Parameter Type |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
RESOURCE PARAMETERS | RESOURCE PARAMETERS |  |  |  | TRUE
Minimum On Line Time | Minimum On Line Time | Check | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Minimum Off Line Time | Minimum Off Line Time | Check | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Hot Start Time | Hot Start Time | Corrected | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Intermediate Start Time | Intermediate Start Time | Corrected | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Cold Start Time | Cold Start Time | Corrected | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Max Weekly Starts | Max Weekly Starts | Check | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Max On Line Time | Max On Line Time | Corrected | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Max Daily Starts | Max Daily Starts | Check | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Max Weekly Energy | Max Weekly Energy | Corrected | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Hot-to-Intermediate Time | Hot-to-Intermediate Time | Check | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Intermediate-to-Cold Time | Intermediate-to-Cold Time | Check | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Operational Parameters - ESG Injections -NRRC | Operational Parameters - ESG Injections -NRRC |  |  |  | TRUE
Generator Details | Generator Details |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Dispatch Asset Code (Provided by ERCOT) | Dispatch Asset Code (Provided by ERCOT) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
ESG Parameter Type | ESG Parameter Type |  |  |  | TRUE
Normal Ramp Rate Curve | Normal Ramp Rate Curve |  |  |  | TRUE
MW Number | MW Number |  |  |  | TRUE
NRRC Code | NRRC Code |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
NRRC MW | NRRC MW | PHASE II Updated 03/06/2012 Added Step 5 and 6 | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Upward Ramprate | Upward Ramprate | Check | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Downward Ramprate | Downward Ramprate | Check | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Oper Parameters - ESG Injections - ERRC | Oper Parameters - ESG Injections - ERRC |  |  |  | TRUE
Generator Details | Generator Details |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Dispatch Asset Code (Provided by ERCOT) | Dispatch Asset Code (Provided by ERCOT) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
ESG Parameter Type | ESG Parameter Type |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Emergency Ramp Rate Curve | Emergency Ramp Rate Curve |  |  |  | TRUE
MW Number | MW Number |  |  |  | TRUE
ERRC Code | ERRC Code |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
ERRC MW | ERRC MW | PHASE II Updated 03/06/2012 Added Step 5 and 6 | ADD 04/2012 |  | TRUE | PHASE II Updated 03/06/2012 Added Step 5 and 6 | ADD 04/2012
Upward Ramprate | Upward Ramprate | Check | ADD 04/2012 |  | TRUE | Check | ADD 04/2012
Downward Ramprate | Downward Ramprate | Check | ADD 04/2012 |  | TRUE | Check | ADD 04/2012
Oper Parameters - ESG Withdrawing | Oper Parameters - ESG Withdrawing |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
ESG Parameter Type | ESG Parameter Type |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
RESOURCE PARAMETERS | RESOURCE PARAMETERS |  |  |  | TRUE
Minimum On Line Time | Minimum On Line Time | Check | ADD 04/2012 |  | TRUE | Check | ADD 04/2012
Minimum Off Line Time | Minimum Off Line Time | Check | ADD 04/2012 |  | TRUE | Check | ADD 04/2012
Hot Start Time | Hot Start Time | Corrected | ADD 04/2012 |  | TRUE | Corrected | ADD 04/2012
Intermediate Start Time | Intermediate Start Time | Corrected | ADD 04/2012 |  | TRUE | Corrected | ADD 04/2012
Cold Start Time | Cold Start Time | Corrected | ADD 04/2012 |  | TRUE | Corrected | ADD 04/2012
Max Weekly Starts | Max Weekly Starts | Check | ADD 04/2012 |  | TRUE | Check | ADD 04/2012
Max On Line Time | Max On Line Time | Corrected | ADD 04/2012 |  | TRUE | Corrected | ADD 04/2012
Max Daily Starts | Max Daily Starts | Check | ADD 04/2012 |  | TRUE | Check | ADD 04/2012
Max Weekly Energy | Max Weekly Energy | Corrected | ADD 04/2012 |  | TRUE | Corrected | ADD 04/2012
Hot-to-Intermediate Time | Hot-to-Intermediate Time | Check | ADD 04/2012 |  | TRUE | Check | ADD 04/2012
Intermediate-to-Cold Time | Intermediate-to-Cold Time | Check | ADD 04/2012 |  | TRUE | Check | ADD 04/2012
Oper Parameters - ESG Withdrawing - NRRC | Oper Parameters - ESG Withdrawing - NRRC |  |  |  | TRUE
Generator Details | Generator Details |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 04/2012
Dispatch Asset Code (Provided by ERCOT) | Dispatch Asset Code (Provided by ERCOT) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
ESG Parameter Type | ESG Parameter Type |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Normal Ramp Rate Curve | Normal Ramp Rate Curve |  |  |  | TRUE
MW Number | MW Number |  |  |  | TRUE
NRRC Code | NRRC Code |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
NRRC MW | NRRC MW | PHASE II Updated 03/06/2012 Added Step 5 and 6 | ADD 04/2012 |  | TRUE | PHASE II Updated 03/06/2012 Added Step 5 and 6 | ADD 04/2012
Upward Ramprate | Upward Ramprate | Check | ADD 04/2012 |  | TRUE | Check | ADD 04/2012
Downward Ramprate | Downward Ramprate | Check | ADD 04/2012 |  | TRUE | Check | ADD 04/2012
Oper Parameters - ESG Withdrawing - ERRC | Oper Parameters - ESG Withdrawing - ERRC |  |  |  | TRUE
Generator Details | Generator Details |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
Dispatch Asset Code (Provided by ERCOT) | Dispatch Asset Code (Provided by ERCOT) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
ESG Parameter Type | ESG Parameter Type |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Emergency Ramp Rate Curve | Emergency Ramp Rate Curve |  |  |  | TRUE
MW Number | MW Number |  |  |  | TRUE
ERRC Code | ERRC Code |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
ERRC MW | ERRC MW | PHASE II Updated 03/06/2012 Added Step 5 and 6 | ADD 04/2012 |  | TRUE | PHASE II Updated 03/06/2012 Added Step 5 and 6 | ADD 04/2012
Upward Ramprate | Upward Ramprate | Check | ADD 04/2012 |  | TRUE | Check | ADD 04/2012
Downward Ramprate | Downward Ramprate | Check | ADD 04/2012 |  | TRUE | Check | ADD 04/2012
Reactive Capability - Solar | Reactive Capability - Solar |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Module # | Module # |  |  |  | TRUE | Added 03/26/2012
Module_Code | Module_Code |  |  |  | TRUE | Added 03/26/2012 Hidded column on form
REACTIVE CAPABILITY CURVES DETAILS | REACTIVE CAPABILITY CURVES DETAILS |  |  |  | TRUE
Reactive Capability Data Provided Below is Gross/Net Values? | Reactive Capability Data Provided Below is Gross/Net Values? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Reactive Capability Data Provided Below is from NDCRC Test Data? | Reactive Capability Data Provided Below is from NDCRC Test Data? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
If Reactive Capability Data Provided Below Is From Ndcrc Test Data Then Enter The Date On Which The Test Was Performed. | If Reactive Capability Data Provided Below Is From Ndcrc Test Data Then Enter The Date On Which The Test Was Performed. |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
MW1 | MW1 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Lagging MVAR limit associated with MW1 output | Lagging MVAR limit associated with MW1 output |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Leading MVAR limit associated with MW1 output | Leading MVAR limit associated with MW1 output |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
MW2 | MW2 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Lagging MVAR limit associated with MW2 output | Lagging MVAR limit associated with MW2 output |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Leading MVAR limit associated with MW2 output | Leading MVAR limit associated with MW2 output |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
MW3 | MW3 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Lagging MVAR limit associated with MW3 output | Lagging MVAR limit associated with MW3 output |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Leading MVAR limit associated with MW3 output | Leading MVAR limit associated with MW3 output |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
MW4 | MW4 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Lagging MVAR limit associated with MW4 output | Lagging MVAR limit associated with MW4 output |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Leading MVAR limit associated with MW4 output | Leading MVAR limit associated with MW4 output |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
MW5 - Unity Power Factor | MW5 - Unity Power Factor |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
If hydrogen cooled, indicate hydrogen pressure (psi) associated with your Reactive Curve submitted for ERCOT studies | If hydrogen cooled, indicate hydrogen pressure (psi) associated with your Reactive Curve submitted for ERCOT studies |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Net Maximum Leading Operating Capability | Net Maximum Leading Operating Capability |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Net Maximum Lagging Operating Capability | Net Maximum Lagging Operating Capability |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Has the Manufacturer's Capability Curve submitted? | Has the Manufacturer's Capability Curve submitted? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Reactive Capability -ESG | Reactive Capability -ESG |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
REACTIVE CAPABILITY CURVES DETAILS | REACTIVE CAPABILITY CURVES DETAILS |  |  |  | TRUE
Reactive Capability Data Provided Below is Gross/Net Values? | Reactive Capability Data Provided Below is Gross/Net Values? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Reactive Capability Data Provided Below is from NDCRC Test Data? | Reactive Capability Data Provided Below is from NDCRC Test Data? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
If Reactive Capability Data Provided Below Is From Ndcrc Test Data Then Enter The Date On Which The Test Was Performed. | If Reactive Capability Data Provided Below Is From Ndcrc Test Data Then Enter The Date On Which The Test Was Performed. |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
MW1 | MW1 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Lagging MVAR limit associated with MW1 output | Lagging MVAR limit associated with MW1 output |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Leading MVAR limit associated with MW1 output | Leading MVAR limit associated with MW1 output |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
MW2 | MW2 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Lagging MVAR limit associated with MW2 output | Lagging MVAR limit associated with MW2 output |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Leading MVAR limit associated with MW2 output | Leading MVAR limit associated with MW2 output |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
MW3 | MW3 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Lagging MVAR limit associated with MW3 output | Lagging MVAR limit associated with MW3 output |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Leading MVAR limit associated with MW3 output | Leading MVAR limit associated with MW3 output |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
MW4 | MW4 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Lagging MVAR limit associated with MW4 output | Lagging MVAR limit associated with MW4 output |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Leading MVAR limit associated with MW4 output | Leading MVAR limit associated with MW4 output |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Maximum Leading Operating Capability | Maximum Leading Operating Capability |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Maximum Lagging Operating Capability | Maximum Lagging Operating Capability |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Has the Manufacturer's Capability Curve submitted? | Has the Manufacturer's Capability Curve submitted? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Ownership - Solar | Ownership - Solar |  |  |  | TRUE
Generator Detail | Generator Detail |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Ownership Percentages | Ownership Percentages |  |  |  | TRUE
Joint Ownership Code | Joint Ownership Code |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resource Entity Name | Resource Entity Name | Update 03/13/2012 | ADD 04/2012 |  | TRUE | Update 03/13/2012 | ADD 04/2012
Resource Duns Number | Resource Duns Number |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Fixed Ownership | Fixed Ownership |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Master Owner (Y or N) | Master Owner (Y or N) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Ownership Start Date | Ownership Start Date | 03/07/2012 Updated with Business Rule | ADD 04/2012 |  | TRUE | 03/07/2012 Updated with Business Rule | ADD 04/2012
Ownership Start Date | Ownership Start Date | 03/07/2012 Updated with Business Rule | ADD 04/2012 |  | TRUE | 03/07/2012 Updated with Business Rule | ADD 04/2012
Ownership - ESG | Ownership - ESG |  |  |  | TRUE
Generator Detail | Generator Detail |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Ownership Percentages | Ownership Percentages |  |  |  | TRUE
Joint Ownership | Joint Ownership |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resource Entity Name | Resource Entity Name | Update 03/13/2012 | ADD 04/2012 |  | FALSE | Update 03/13/2012 | ADD 04/2012
Resource Duns Number | Resource Duns Number |  | ADD 04/2012 |  | FALSE |  | ADD 04/2012
Fixed Ownership | Fixed Ownership |  | ADD 04/2012 |  | FALSE |  | ADD 04/2012
Master Owner (Y or N) | Master Owner (Y or N) |  | ADD 04/2012 |  | FALSE |  | ADD 04/2012
Ownership Start Date | Ownership Start Date | 03/07/2012 Updated with Business Rule | ADD 04/2012 |  | TRUE | 03/07/2012 Updated with Business Rule | ADD 04/2012
Ownership Start Date | Ownership Start Date | 03/07/2012 Updated with Business Rule | ADD 04/2012 |  | TRUE | 03/07/2012 Updated with Business Rule | ADD 04/2012
Planning - Solar | Planning - Solar |  |  |  | TRUE
GENERATION DETAILS | GENERATION DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
INVERTER TYPE | INVERTER TYPE |  | ADD 04/2012 |  | TRUE | Added Validation 03/27/2012 | ADD 04/2012
PLANNING DETAILS | PLANNING DETAILS |  |  |  | TRUE
What is the MVA base that the following data is based on? | What is the MVA base that the following data is based on? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
What is the kV base that the following data is based on? | What is the kV base that the following data is based on? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Direct Axis Subtransient reactance, X"di (unsaturated) | Direct Axis Subtransient reactance, X"di (unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Direct Axis Transient reactance, X'di (unsaturated) | Direct Axis Transient reactance, X'di (unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Positive Sequence Z (unsaturated) | Positive Sequence Z (unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Positive Sequence Z (unsaturated) | Positive Sequence Z (unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Negative Sequence Z (unsaturated) | Negative Sequence Z (unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Negative Sequence Z (unsaturated) | Negative Sequence Z (unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Does Zero Sequence Z exist? | Does Zero Sequence Z exist? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Z (unsaturated) | Zero Sequence Z (unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Z (unsaturated) | Zero Sequence Z (unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Direct Axis Subtransient reactance, X"dv (saturated) | Direct Axis Subtransient reactance, X"dv (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Direct Axis Transient reactance, X'dv (saturated) | Direct Axis Transient reactance, X'dv (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Positive Sequence Z (saturated) | Positive Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Positive Sequence Z (saturated) | Positive Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Negative Sequence Z (saturated) | Negative Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Negative Sequence Z (saturated) | Negative Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Z (saturated) | Zero Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Z (saturated) | Zero Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Resistance In P.u. (100 Mva Base) | Zero Sequence Resistance In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Reactance In P.u. (100 Mva Base) | Zero Sequence Reactance In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Generator Auxiliary Load | Generator Auxiliary Load |  |  |  | TRUE
Average Amount of Auxiliary Real Power | Average Amount of Auxiliary Real Power |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Average Amount of Auxiliary Reactive Power | Average Amount of Auxiliary Reactive Power |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Auxiliary Load Power Factor | Auxiliary Load Power Factor |  | ADD 04/2012 |  | TRUE | Added Validation 03/27/2012 | ADD 04/2012
Generation Auxiliary Load Characteristics for MW Load | Generation Auxiliary Load Characteristics for MW Load |  |  |  | TRUE
Large Motor, percent of total MW load | Large Motor, percent of total MW load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Small Motor, percent of total MW load | Small Motor, percent of total MW load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resistive (Heating) Load, percent of total MW load | Resistive (Heating) Load, percent of total MW load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Discharge Lighting, percent of total MW load | Discharge Lighting, percent of total MW load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Other, percent of total MW load | Other, percent of total MW load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Generation Auxiliary Load Characteristics for MVAR Load | Generation Auxiliary Load Characteristics for MVAR Load |  |  |  | TRUE
Large Motor, percent of total MVAR load | Large Motor, percent of total MVAR load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Small Motor, percent of total MVAR load | Small Motor, percent of total MVAR load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Discharge Lighting, percent of total MVAR load | Discharge Lighting, percent of total MVAR load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Other, percent of total MVAR load | Other, percent of total MVAR load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
INVERTER STEP-UP TRANSFORMER DATA | INVERTER STEP-UP TRANSFORMER DATA |  |  |  | TRUE
High Side Voltage Level (nominal) | High Side Voltage Level (nominal) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Low Side Voltage Level (nominal) | Low Side Voltage Level (nominal) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
High Side Voltage Connection - Wye / Wye - Grounded / Delta | High Side Voltage Connection - Wye / Wye - Grounded / Delta |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Low Side Voltage Connection - Wye / Wye - Grounded / Delta | Low Side Voltage Connection - Wye / Wye - Grounded / Delta |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Impedance Z | Impedance Z |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
X/r Ratio | X/r Ratio |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Z | Zero Sequence Z |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence X/r Ratio | Zero Sequence X/r Ratio |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Base Mva For Transformer Data | Base Mva For Transformer Data |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Inverter Limits In P.u. Of Nominal Output For Fault Duty Studies | Inverter Limits In P.u. Of Nominal Output For Fault Duty Studies |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
VOLTAGE REGULATION | VOLTAGE REGULATION |  |  |  | TRUE
Automatic Voltage Regulation | Automatic Voltage Regulation |  | ADD 04/2012 |  | TRUE | Added Validation 03/27/2012 | ADD 04/2012
Does Transformer Have A Load Tap Changer? | Does Transformer Have A Load Tap Changer? |  | ADD 04/2012 |  | TRUE | Added Validation 03/27/2012 | ADD 04/2012
Location of Tap Changer High or Low | Location Of Load Tap Changer - High Or Low |  | ADD 04/2012 |  | FALSE | 03/28/2012 Removed High or Low from Field Name and removed validation Rule #3. Added Validation 03/27/2012 | ADD 04/2012
Base Kv Of Regulated Side | Base Kv Of Regulated Side |  | ADD 04/2012 |  | TRUE | Added Validation 03/27/2012 | ADD 04/2012
Target Kv Of Regulated Side | Target Kv Of Regulated Side |  | ADD 04/2012 |  | TRUE | Added Validation 03/27/2012 | ADD 04/2012
Acceptable Deviation Of Target Voltage | Acceptable Deviation Of Target Voltage |  | ADD 04/2012 |  | TRUE | Added Validation 03/27/2012 | ADD 04/2012
ONLY IF HIGH SIDE TAP EXISTS | ONLY IF HIGH SIDE TAP EXISTS |  |  |  | TRUE
Tap Position At Manufactured Nominal Voltage | Tap Position At Manufactured Nominal Voltage |  | ADD 04/2012 |  | TRUE | Added Validation 03/27/2012 | ADD 04/2012
Total Number Of Tap Positions | Total Number Of Tap Positions |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Normal Tap Position | Normal Tap Position |  | ADD 04/2012 |  | TRUE | Added Validation 03/27/2012 | ADD 04/2012
Lowest Tap Position | Lowest Tap Position |  | ADD 04/2012 |  | TRUE | Added Validation 03/27/2012 | ADD 04/2012
Voltage At Lowest Tap Position | Voltage At Lowest Tap Position |  | ADD 04/2012 |  | TRUE | Added Validation 03/27/2012 | ADD 04/2012
Highest Tap Position | Highest Tap Position |  | ADD 04/2012 |  | TRUE | Added Validation 03/27/2012 | ADD 04/2012
Voltage At Highest Tap Position | Voltage At Highest Tap Position |  | ADD 04/2012 |  | TRUE | Added Validation 03/27/2012 | ADD 04/2012
Size Of Each Voltage Level Step | Size Of Each Voltage Level Step |  | ADD 04/2012 |  | TRUE | Added Validation 03/27/2012 | ADD 04/2012
PSSE MODEL : THE FOLLOWING LIST OF FILES ARE REQUIRED TO BE SUBMITTED IF THIS IS AN INITIAL REGISTRATION OR IF THERE ARE CHANGES MODIFYING PREVIOUSLY SUBMITTED PSSE FILES. PLEASE INCLUDE ALL PSSE FILES IN A ZIP OR COMPRESSED FOLDER FILE ALONG WITH YOUR RARF SUBMITTAL IN THE SAME SERVICE REQUEST | PSSE MODEL : THE FOLLOWING LIST OF FILES ARE REQUIRED TO BE SUBMITTED IF THIS IS AN INITIAL REGISTRATION OR IF THERE ARE CHANGES MODIFYING PREVIOUSLY SUBMITTED PSSE FILES. PLEASE INCLUDE ALL PSSE FILES IN A ZIP OR COMPRESSED FOLDER FILE ALONG WITH YOUR RARF SUBMITTAL IN THE SAME SERVICE REQUEST |  |  |  | TRUE
Psse Compatible Solar Pv Generator Models | Psse Compatible Solar Pv Generator Models |  |  |  | TRUE
Dynamic Reactive Device Form/models | Dynamic Reactive Device Form/models |  |  |  | TRUE
Planning - ESG | Planning - ESG |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
PLANNING DETAILS | PLANNING DETAILS |  |  |  | TRUE
What is the MVA base that the following data is based on? | What is the MVA base that the following data is based on? |  | ADD 04/2012 |  | TRUE | Added Validation 03/27/2012 | ADD 04/2012
What is the kV base that the following data is based on? | What is the kV base that the following data is based on? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Direct Axis Subtransient reactance, X"di (unsaturated) | Direct Axis Subtransient reactance, X"di (unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Direct Axis Transient reactance, X'di (unsaturated) | Direct Axis Transient reactance, X'di (unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Positive Sequence Z (unsaturated) | Positive Sequence Z (unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Positive Sequence Z (unsaturated) | Positive Sequence Z (unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Negative Sequence Z (unsaturated) | Negative Sequence Z (unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Negative Sequence Z (unsaturated) | Negative Sequence Z (unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Does Zero Sequence Z exist? | Does Zero Sequence Z exist? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Z (unsaturated) | Zero Sequence Z (unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Z (unsaturated) | Zero Sequence Z (unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Direct Axis Subtransient reactance, X"dv (saturated) | Direct Axis Subtransient reactance, X"dv (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Direct Axis Transient reactance, X'dv (saturated) | Direct Axis Transient reactance, X'dv (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Positive Sequence Z (saturated) | Positive Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Positive Sequence Z (saturated) | Positive Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Negative Sequence Z (saturated) | Negative Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Negative Sequence Z (saturated) | Negative Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Z (saturated) | Zero Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Z (saturated) | Zero Sequence Z (saturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE | Added Validation 03/27/2012 | ADD 04/2012
Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE | Added Validation 03/27/2012 | ADD 04/2012
Zero Sequence Resistance In P.u. (100 Mva Base) | Zero Sequence Resistance In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE | Added Validation 03/27/2012 | ADD 04/2012
Zero Sequence Reactance In P.u. (100 Mva Base) | Zero Sequence Reactance In P.u. (100 Mva Base) |  | ADD 04/2012 |  | TRUE | Added Validation 03/27/2012 | ADD 04/2012
Generator Auxiliary Load | Generator Auxiliary Load |  |  |  | TRUE
Average Amount of Auxiliary Real Power | Average Amount of Auxiliary Real Power |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Average Amount of Auxiliary Reactive Power | Average Amount of Auxiliary Reactive Power |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Auxiliary Load Power Factor | Auxiliary Load Power Factor |  | ADD 04/2012 |  | TRUE | Added Validation 03/27/2012 | ADD 04/2012
Generation Auxiliary Load Characteristics for MW Load | Generation Auxiliary Load Characteristics for MW Load |  |  |  | TRUE
Large Motor, percent of total MW load | Large Motor, percent of total MW load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Small Motor, percent of total MW load | Small Motor, percent of total MW load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resistive (Heating) Load, percent of total MW load | Resistive (Heating) Load, percent of total MW load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Discharge Lighting, percent of total MW load | Discharge Lighting, percent of total MW load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Other, percent of total MW load | Other, percent of total MW load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Generation Auxiliary Load Characteristics for MVAR Load | Generation Auxiliary Load Characteristics for MVAR Load |  |  |  | TRUE
Large Motor, percent of total MVAR load | Large Motor, percent of total MVAR load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Small Motor, percent of total MVAR load | Small Motor, percent of total MVAR load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Discharge Lighting, percent of total MVAR load | Discharge Lighting, percent of total MVAR load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Other, percent of total MVAR load | Other, percent of total MVAR load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Voltage Regulation | Voltage Regulation |  |  |  | TRUE
Automatic Voltage Regulation | Automatic Voltage Regulation |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Does Transformer have a Load Tap Changer? | Does Transformer have a Load Tap Changer? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Location of Tap Changer High or Low | Location of Tap Changer High or Low |  | ADD 04/2012 |  | TRUE | 03/28/2012 Removed High or Low from Field Name and removed validation Rule #3. Added Validation 03/27/2012 | ADD 04/2012
Base kV of Regulated Side | Base kV of Regulated Side |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Target kV of Regulated Side | Target kV of Regulated Side |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Acceptable Deviation of Target Voltage | Acceptable Deviation of Target Voltage |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Only if High Side Tap Exists | Only if High Side Tap Exists |  |  |  | TRUE
Tap position at Manufactured Nominal Voltage | Tap position at Manufactured Nominal Voltage |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Total Number of Tap Positions | Total Number of Tap Positions |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Normal Tap Position | Normal Tap Position |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Lowest Tap Position | Lowest Tap Position |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Voltage at Lowest Tap Position | Voltage at Lowest Tap Position |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Highest Tap Position | Highest Tap Position |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Voltage at Highest Tap Position | Voltage at Highest Tap Position |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Size of each Voltage Level Step | Size of each Voltage Level Step |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Only if Low Side Tap Exists | Only if Low Side Tap Exists |  |  |  | TRUE
Tap position at Manufactured Nominal Voltage | Tap position at Manufactured Nominal Voltage |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Total Number of Tap Positions | Total Number of Tap Positions |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Normal Tap Position | Normal Tap Position |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Lowest Tap Position | Lowest Tap Position |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Voltage at Lowest Tap Position | Voltage at Lowest Tap Position |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Highest Tap Position | Highest Tap Position |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Voltage at Highest Tap Position | Voltage at Highest Tap Position |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Size of each Voltage Level Step | Size of each Voltage Level Step |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Inverter Data (if applicable) | Inverter Data (if applicable) |  |  |  | TRUE
What is the MVA base that the following data is based on? | What is the MVA base that the following data is based on? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
What is the kV base that the following data is based on? | What is the kV base that the following data is based on? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Direct Axis Subtransient reactance, X"di | Direct Axis Subtransient reactance, X"di |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Direct Axis Transient reactance, X'di | Direct Axis Transient reactance, X'di |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Positive Sequence Z (Unsaturated) | Positive Sequence Z (Unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Positive Sequence Z (Unsaturated) | Positive Sequence Z (Unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Negative Sequence Z (Unsaturated) | Negative Sequence Z (Unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Negative Sequence Z (Unsaturated) | Negative Sequence Z (Unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Z (Unsaturated) | Zero Sequence Z (Unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Zero Sequence Z (Unsaturated) | Zero Sequence Z (Unsaturated) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
PSSE Models : The following files are required to be submitted if not listed in the Wind Turbine Dynamic Models available at ERCOT or if additional equipment has been added to the site requiring Model updates. Please include all PSSE files in a ZIP or Compressed Folder along with your RARF submittal Service Request. | PSSE Models : The following files are required to be submitted if not listed in the Wind Turbine Dynamic Models available at ERCOT or if additional equipment has been added to the site requiring Model updates. Please include all PSSE files in a ZIP or Compressed Folder along with your RARF submittal Service Request. |  |  |  | TRUE
PSSE Compatible Solar Pv Generator Models | PSSE Compatible Solar Pv Generator Models |  |  |  | TRUE
Dynamic Reactive Device Form/models | Dynamic Reactive Device Form/models |  |  |  | TRUE
Protection - Solar | Protection - Solar |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Breaker Interruption Time | Breaker Interruption Time |  |  |  | TRUE
Breaker Interruption Time | Breaker Interruption Time |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
PLANT VOLTAGE PROTECTION | PLANT VOLTAGE PROTECTION |  |  |  | TRUE
Instantaneous Undervoltage Trip | Instantaneous Undervoltage Trip |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Undervoltage 1 | Undervoltage 1 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 1 | Time 1 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Undervoltage 2 | Undervoltage 2 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 2 | Time 2 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Undervoltage 3 | Undervoltage 3 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 3 | Time 3 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Undervoltage 4 | Undervoltage 4 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 4 | Time 4 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Instantaneous Overvoltage Trip | Instantaneous Overvoltage Trip |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Overvoltage 1 | Overvoltage 1 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 1 | Time 1 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Overvoltage 2 | Overvoltage 2 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 2 | Time 2 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Overvoltage 3 | Overvoltage 3 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 3 | Time 3 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Overvoltage 4 | Overvoltage 4 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 4 | Time 4 |  | ADD 04/2012 |  | FALSE |  | ADD 04/2012
PLANT FREQUENCY PROTECTION | PLANT FREQUENCY PROTECTION |  |  |  | TRUE
Instantaneous Underfrequency Trip | Instantaneous Underfrequency Trip |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Underfrequency 1 | Underfrequency 1 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 1 | Time 1 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Underfrequency 2 | Underfrequency 2 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 2 | Time 2 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Underfrequency 3 | Underfrequency 3 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 3 | Time 3 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Underfrequency 4 | Underfrequency 4 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 4 | Time 4 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Instantaneous Overfrequency Trip | Instantaneous Overfrequency Trip |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Overfrequency 1 | Overfrequency 1 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 1 | Time 1 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Overfrequency 2 | Overfrequency 2 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 2 | Time 2 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Overfrequency 3 | Overfrequency 3 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 3 | Time 3 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Overfrequency 4 | Overfrequency 4 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 4 | Time 4 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
PV INVERTER VRT CAPABILITY | PV INVERTER VRT CAPABILITY |  |  |  | TRUE
Provide Manufacturer's Technical Document / Simulation Results / Test Result, Etc. Describing The Solar Technology & Vrt OPTIons Purchased With Inverter, If Any | Provide Manufacturer's Technical Document / Simulation Results / Test Result, Etc. Describing The Solar Technology & Vrt OPTIons Purchased With Inverter, If Any |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Do Personnel (onsite Operator/engineer Etc.) Have Control To Enable/disable Or Change The Settings For Voltage Ride-through | Do Personnel (onsite Operator/engineer Etc.) Have Control To Enable/disable Or Change The Settings For Voltage Ride-through |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Does The Resource Use Dynamic Reactive Devices (SVC/statcom, Etc.) At Solar Plant Facility? - (note: Capacitor Banks Used For Conventional Reactive Support Cannot Be Considered As Dynamic Reactive Devices) - If Yes, Please Provide Supporting Documentation. (manufacturer's Technical Document, Pss/e Model Etc.) | Does The Resource Use Dynamic Reactive Devices (SVC/statcom, Etc.) At Solar Plant Facility? - (note: Capacitor Banks Used For Conventional Reactive Support Cannot Be Considered As Dynamic Reactive Devices) - If Yes, Please Provide Supporting Documentation. (manufacturer's Technical Document, Pss/e Model Etc.) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Provide Inverter Voltage & Frequency Protection Settings As Per Manufacturer - Technical Document And/or Spec Sheet | Provide Inverter Voltage & Frequency Protection Settings As Per Manufacturer - Technical Document And/or Spec Sheet |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Does The Resource Have Plant Voltage Protection? If Yes, Please Provide Supporting Documentation. | Does The Resource Have Plant Voltage Protection? If Yes, Please Provide Supporting Documentation. |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Does The Resource Have Feeder Voltage Protection? If Yes, Please Provide Supporting Documentation. | Does The Resource Have Feeder Voltage Protection? If Yes, Please Provide Supporting Documentation. |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Protection - ESG | Protection - ESG |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 | Do not show Message on Audit or Delta | TRUE | Do not show Message on Audit or Delta | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Breaker Interruption Time | Breaker Interruption Time |  |  |  | TRUE
Breaker Interruption Time | Breaker Interruption Time |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
PLANT VOLTAGE PROTECTION | PLANT VOLTAGE PROTECTION |  |  |  | TRUE
Instantaneous Undervoltage Trip | Instantaneous Undervoltage Trip |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Undervoltage 1 | Undervoltage 1 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 1 | Time 1 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Undervoltage 2 | Undervoltage 2 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 2 | Time 2 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Undervoltage 3 | Undervoltage 3 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 3 | Time 3 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Undervoltage 4 | Undervoltage 4 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 4 | Time 4 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Instantaneous Overvoltage Trip | Instantaneous Overvoltage Trip |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Overvoltage 1 | Overvoltage 1 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 1 | Time 1 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Overvoltage 2 | Overvoltage 2 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 2 | Time 2 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Overvoltage 3 | Overvoltage 3 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 3 | Time 3 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Overvoltage 4 | Overvoltage 4 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 4 | Time 4 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
PLANT FREQUENCY PROTECTION | PLANT FREQUENCY PROTECTION |  |  |  | TRUE
Instantaneous Underfrequency Trip | Instantaneous Underfrequency Trip |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Underfrequency 1 | Underfrequency 1 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 1 | Time 1 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Underfrequency 2 | Underfrequency 2 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 2 | Time 2 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Underfrequency 3 | Underfrequency 3 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 3 | Time 3 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Underfrequency 4 | Underfrequency 4 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 4 | Time 4 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Instantaneous Overfrequency Trip | Instantaneous Overfrequency Trip |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Overfrequency 1 | Overfrequency 1 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 1 | Time 1 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Overfrequency 2 | Overfrequency 2 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 2 | Time 2 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Overfrequency 3 | Overfrequency 3 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 3 | Time 3 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Overfrequency 4 | Overfrequency 4 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Time 4 | Time 4 |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Collector System - Solar | Collector System - Solar | 03/13/2012 Updated |  |  | TRUE | Corrected Tab name 03/26/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  |  |  | TRUE | Added 03/26/2012
COLLECTION SYSTEM DETAILED MODEL | COLLECTION SYSTEM DETAILED MODEL | 03/13/2012 Updated |  |  | TRUE | Corrected Tab name 03/26/2012
Cable Type | Cable Type | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
Voltage Level kV | Voltage Level kV | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
POSITIVE SEQUENCE DATA | POSITIVE SEQUENCE DATA | 03/13/2012 Updated |  |  | TRUE | Corrected Tab name 03/26/2012
R/kft | R/kft | 03/09/2012 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
X/kft | X/kft | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
Charging Bc/kft | Charging Bc/kft | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
ZERO SEQUENCE DATA | ZERO SEQUENCE DATA | 03/13/2012 Updated |  |  | TRUE | Corrected Tab name 03/26/2012
R0/kft | R0/kft | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
X0/kft | X0/kft | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
Collector System-Solar Seg Data | Collector System-Solar Seg Data | 03/13/2012 Updated |  |  | TRUE | Corrected Tab name 03/26/2012
CABLE TYPE | CABLE TYPE | 03/13/2012 Updated |  |  | TRUE | Corrected Tab name 03/26/2012
Cable Type | Cable Type | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) |  |  |  | TRUE | Added 03/26/2012
CABLE SEGAMENT DATA | CABLE SEGAMENT DATA | 03/13/2012 Updated |  |  | TRUE | Corrected Tab name 03/26/2012
From | From | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
To | To | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
Circuit Number | Circuit Number | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
Voltage Level | Voltage Level | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
Cable Segment Length | Cable Segment Length | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
Number of Turbines On Cable Segment | Number of Turbines On Cable Segment | 03/13/12 Updated | ADD 04/2012 |  | TRUE | Corrected Tab name 03/26/2012 | ADD 04/2012
Private Network - Site - ESG | Private Network - Site - ESG |  |  |  | TRUE
SITE DETAILS | SITE DETAILS |  |  |  | TRUE
Private Network? | Private Network? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
PRIVATE NETWORK - SITE INFORMATION | PRIVATE NETWORK - SITE INFORMATION |  |  |  | TRUE
Average Amount of Self-Serve private load | Average Amount of Self-Serve private load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Average Amount of Self-Serve private reactive load | Average Amount of Self-Serve private reactive load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Expected Typical Private Network Net Interchange | Expected Typical Private Network Net Interchange |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Expected Typical Private Network Net Reactive Interchange | Expected Typical Private Network Net Reactive Interchange |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Private Network Gross Unit Capability | Private Network Gross Unit Capability |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Private Network Gross Unit Reactive Capability | Private Network Gross Unit Reactive Capability |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Load Characteristics for MW Load | Load Characteristics for MW Load |  |  |  | TRUE
Large Motor, percent of total MW load | Large Motor, percent of total MW load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Small Motor, percent of total MW load | Small Motor, percent of total MW load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resistive (Heating) Load, percent of total MW load | Resistive (Heating) Load, percent of total MW load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Discharge Lighting, percent of total MW load | Discharge Lighting, percent of total MW load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Other, percent of total MW load | Other, percent of total MW load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Load Characteristics for MVAR Load | Load Characteristics for MVAR Load |  |  |  | TRUE
Large Motor, percent of total MVAR load | Large Motor, percent of total MVAR load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Small Motor, percent of total MVAR load | Small Motor, percent of total MVAR load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Discharge Lighting, percent of total MVAR load | Discharge Lighting, percent of total MVAR load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Other, percent of total MVAR load | Other, percent of total MVAR load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Private Network - Unit - ESG | Private Network - Unit - ESG |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
SITE_CODE | SITE_CODE |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) | Do not show Message on Audit or Delta | ADD 02/2012 |  | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
PRIVATE NETWORK - UNIT INFORMATION | PRIVATE NETWORK - UNIT INFORMATION |  |  |  | TRUE
Average Amount of Self-Serve private load | Average Amount of Self-Serve private load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Average Amount of Self-Serve private reactive load | Average Amount of Self-Serve private reactive load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Expected Typical Private Network Net Interchange | Expected Typical Private Network Net Interchange |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Expected Typical Private Network Net Reactive Interchange | Expected Typical Private Network Net Reactive Interchange |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Private Network Gross Unit Capability | Private Network Gross Unit Capability |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Private Network Gross Unit Reactive Capability | Private Network Gross Unit Reactive Capability |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
If Unit trips, does Load trip? | If Unit trips, does Load trip? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
If yes, approximate percentage of Load that will trip? | If yes, approximate percentage of Load that will trip? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Private Network - Site - Solar | Private Network - Site - Solar |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Private Network? | Private Network? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
PRIVATE NETWORK - SITE INFORMATION | PRIVATE NETWORK - SITE INFORMATION |  |  |  | TRUE
Average Amount of Self-Serve private load | Average Amount of Self-Serve private load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Average Amount of Self-Serve private reactive load | Average Amount of Self-Serve private reactive load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Expected Typical Private Network Net Interchange | Expected Typical Private Network Net Interchange |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Expected Typical Private Network Net Reactive Interchange | Expected Typical Private Network Net Reactive Interchange |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Private Network Gross Unit Capability | Private Network Gross Unit Capability |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Private Network Gross Unit Reactive Capability | Private Network Gross Unit Reactive Capability |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Load Characteristics for MW Load | Load Characteristics for MW Load |  |  |  | TRUE
Large Motor, percent of total MW load | Large Motor, percent of total MW load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Small Motor, percent of total MW load | Small Motor, percent of total MW load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Resistive (Heating) Load, percent of total MW load | Resistive (Heating) Load, percent of total MW load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Discharge Lighting, percent of total MW load | Discharge Lighting, percent of total MW load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Other, percent of total MW load | Other, percent of total MW load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Load Characteristics for MVAR Load | Load Characteristics for MVAR Load |  |  |  | TRUE
Large Motor, percent of total MVAR load | Large Motor, percent of total MVAR load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Small Motor, percent of total MVAR load | Small Motor, percent of total MVAR load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Discharge Lighting, percent of total MVAR load | Discharge Lighting, percent of total MVAR load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Other, percent of total MVAR load | Other, percent of total MVAR load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Private Network - Unit - Solar | Private Network - Unit - Solar |  |  |  | TRUE
GENERATOR DETAILS | GENERATOR DETAILS |  |  |  | TRUE
Unit Name | Unit Name | Do not show Message on Audit or Delta | ADD 02/2012 | Do not show Message on Audit or Delta | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
SITE_CODE | SITE_CODE |  | ADD 02/2012 |  | TRUE |  | ADD 02/2012
Resource Name (Unit Code/Mnemonic) | Resource Name (Unit Code/Mnemonic) | Do not show Message on Audit or Delta | ADD 02/2012 | Do not show Message on Audit or Delta | TRUE | Do not show Message on Audit or Delta | ADD 02/2012
PRIVATE NETWORK - Unit Information | PRIVATE NETWORK - Unit Information |  |  |  | TRUE
Average Amount of Self-Serve private load | Average Amount of Self-Serve private load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Average Amount of Self-Serve private reactive load | Average Amount of Self-Serve private reactive load |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Expected Typical Private Network Net Interchange | Expected Typical Private Network Net Interchange |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Expected Typical Private Network Net Reactive Interchange | Expected Typical Private Network Net Reactive Interchange |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Private Network Gross Unit Capability | Private Network Gross Unit Capability |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
Private Network Gross Unit Reactive Capability | Private Network Gross Unit Reactive Capability |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
If Unit trips, does Load trip? | If Unit trips, does Load trip? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012
If yes, approximate percentage of Load that will trip? | If yes, approximate percentage of Load that will trip? |  | ADD 04/2012 |  | TRUE |  | ADD 04/2012

## Sheet8 (hidden)
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Private Network - Site |  | Private Network - Site |  | Not in table | Not in table
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | SITE DETAILS |  | Private Network - Site |  | Not in table | Not in table
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Private Network? | 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. | Private Network - Site | Y/N | SITECODES | PRIVATE_NTWK_SITE_FLG | Select from Y or N. Private Network Flag is not null | R | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms/Kittiepong | EMS
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | PRIVATE NETWORK - SITE INFORMATION |  | Private Network - Site |  | Not in table | Not in table | This tab is conditional : Required for all Private Use Networks |  | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Average Amount Of Self-serve Private Load | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. | Private Network - Site | MW | SITECODES | AVG_LD_MW_UNIT | This field is conditional. Required if Private Network flag is 'Y' | C | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms | EMS
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Average Amount Of Self-serve Private Reactive Load | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. | Private Network - Site | MVAR | SITECODES | AVG_LD_MVAR_UNIT | This field is conditional. Required if Private Network flag is 'Y' | C | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Expected Typical Private Network Net Interchange | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. | Private Network - Site | MW | SITECODES | NET_INTERCHNG_MW_UNIT | This field is conditional. Required if Private Network flag is 'Y' | C | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms | EMS
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Expected Typical Private Network Net Reactive Interchange | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. | Private Network - Site | MVAR | SITECODES | NET_INTERCHNG_MVAR_UNIT | This field is conditional. Required if Private Network flag is 'Y' | C | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Private Network Gross Unit Capability | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. | Private Network - Site | MW | SITECODES | GROSS_CAPBLTY_MW_UNIT | This field is conditional. Required if Private Network flag is 'Y' | C | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Private Network Gross Unit Reactive Capability | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. | Private Network - Site | MVAR | SITECODES | GROSS_CAPBLTY_MVAR_UNIT | This field is conditional. Required if Private Network flag is 'Y' | C | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Load Characteristics For MW Load |  | Private Network - Site |  | Not in table | Not in table | This tab is conditional : Required for all Private Use Networks |  | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Large Motor, Percent Of Total | 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. | Private Network - Site | % | SITECODES | PUN_MW_LARGEMTR_PCT | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu | MMS
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Small Motor, Percent Of Total | 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. | Private Network - Site | % | SITECODES | PUN_MW_SMALLMTR_PCT | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu | MMS
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Resistive (heating) Load, Percent Of Total MW Load | 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. | Private Network - Site | % | SITECODES | PUN_MW_RESISTIVE_PCT | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu | MMS
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Discharge Lighting, Percent Of Total | 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. | Private Network - Site | % | SITECODES | PUN_MW_DISCHARGE_PCT | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu | MMS
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Other, Percent Of Total MW Load | 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. | Private Network - Site | % | SITECODES | PUN_MW_OTHER_PCT | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu | MMS
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Load Characteristics for MVAR Load |  | Private Network - Site |  | Not in table | Not in table | This tab is conditional : Required for all Private Use Networks
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Large Motor, Percent Of Total MVAR Load | 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. | Private Network - Site | % | SITECODES | PUN_MVAR_LARGEMTR_PCT | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu | MMS
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Small Motor, Percent Of Total MVAR Load | 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. | Private Network - Site | % | SITECODES | PUN_MVAR_SMALLMTR_PCT | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | R | Lin Xu | MMS
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Discharge Lighting, Percent Of Total MVAR Load | 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. | Private Network - Site | % | SITECODES | PUN_MVAR_DISCHARGE_PCT | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu | MMS
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Other, Percent Of Total MVAR Load | 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. | Private Network - Site | % | SITECODES | PUN_MVAR_OTHER_PCT | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu | MMS

## Sheet1 (hidden)
Wind | Non_Modeled Generator | Passed for flag not checked error on audit |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | Y/N | WIND | NON_MOD_GEN | 1.Select from the list: Y or N 2.Not Null | Select from the list: Y or N | R | Error! Resource claiming status as a Non-Modeled Generator Flag is Blank |  | DONE | Passed all Validations
Wind | Transmission Only Date (POI) |  |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | mm/dd/yyyy | WIND | TRANS_ONLY_DT | 1. Optional. 2. Format should be: MM/DD/YYYY | This field is optional. Format should be: MM/DD/YYYY | O | Passed - Format OK Form Does not allow |  | Done | Passed all Validations
Wind | Standard Generation Interconnection Agreement (SGIA) Signature Date | Passed for flag not checked error on audit |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | mm/dd/yyyy | WIND | SGIA_SIG_DT | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date. | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date. | R | Passed - Format OK 1. Generated Error for field being blank 2. Form Does not allow 3. Warning! SGIA Signature Date (05/28/2012) is greater than Current Date |  | DOne | Passed all Validations
Wind | Unit Start Date (Model Ready Date) |  | 03/13/2012 Updated Validation | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | mm/dd/yyyy | WIND | UNIT_MRD_ST_DT | 1.This field is not null. Format should be: MM/DD/YYYY 2.Date should be Vaild Data Base Load Date 3.Unit Start Date should be >= Site Start Date ( Site-Information Tab) | This field is optional. Format should be: MM/DD/YYYY |  | Passed - Format OK 1. Generated Error for field being blank Form Does not allow |  | Done | Passed all Validations
Wind | SubStation Code/SubStation Mnemonic | Passed for flag not checked error on audit |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | All caps | Wind | SUBSTAT_CODE_SUB_MNEMONIC | 1) This field is not null (required). Data type must be Character. 2) Must match ERCOT records (unless new). Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" . 4) Must be <= 8 characters. Warning! Substation Code should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) Substation code should be in Upper case letters. Generate an error if the rule fails. | 1) This field is not null (required). Data type must be Character. 2) Must match ERCOT records (unless new). Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" . 4) Must be <= 8 characters. Warning! Substation Code should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) Substation code should be in Upper case letters. Generate an error if the rule fails. | R | 1. Generated Error for field being blank 2. 3. |  | DONE | Passed all Validations
Wind | Voltage Level | Passed for flag not checked error on audit | 03/13/12 Updated | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | kV | Wind | VOL_LEV | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0. | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0. | R | 1. Generated Error for field being blank 2.Error! Voltage Level (75) should be either 69, 138 or 345 when Voltage Level >= 69 3. Error! Voltage Level (-5) should be a numeric value, which is > 0 and <= 345 |  | DOne | Passed all Validations
Wind | PTI Bus Number | Passed for flag not checked error on audit |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | # | Wind | PTI_BUS_NUM | 1) This field isnot null (required). Data type must be Integer. 2) The value must be > 0. | 1) This field isnot null (required). Data type must be Integer. 2) The value must be > 0. | R | FORMAT OK ! 1. Passed for flag not checked error on audit 2. Error! PTI Bus Number (0) must be > 0 |  | Done | Passed all Validations
Wind | Governor Droop Setting | Passed for flag not checked error on audit | 05/03/2012 removed percent from label on form | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View |  | Wind | GOV_DROOP |  | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if it is not between 0 and 25. Generate Warning if > 5 (protocol requirement). | R | Format OK 1. Generated Error for field being blankError! 2. Error! Governor Droop Setting (-5) must be a numeric value between 0 and 25 3.Error! Governor Droop Setting (30) must be a numeric value between 0 and 25 |  | Done | Passed all Validations | 2 passed
Wind | Governor Dead-Band | Passed for Validation Rule 1 and 3 |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | Hz | Wind | GOV_DEAD_BND |  | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if > 0.1. Generate Warning if > 0.03. | R | 1. PASSED - for Field Required 2.Error! Governor Dead-band (-5) must be a positive value 3. Error! Governor Dead-band (25.00) is > 0.1 |  | Done | Passed all Validations | 3. passed
Wind | Design Max Ambient Temperature |  |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | Degree F | Wind | DESIGN_MAX_AMB_TEMP |  | >100 <150 |  | Passed - Format OK Form Does not allow |  | DOne | Passed all Validations | Passed - Format OK Form Does not allow | Checked for -1
Wind | Design Min Ambient Temperature |  |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | Degree F | Wind | DESIGN_MIN_AMB_TEMP |  | >-100 <32 |  | Passed - Format OK Form Does not allow |  | DOne | Passed all Validations | Passed - Format OK Form Does not allow | Checked for -5
Wind | Height of Meteorological Instrumentation - Wind Speed | Passed for flag not checked error on audit |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | Meters | Wind | HGT_MET_TWR_WND_SPD |  | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Error! Height of Meteorological Instrumentation - Wind Speed (-5) must be > 0 Error! Height of Meteorological Instrumentation - Wind Speed (what) should be a numeric valuePassed - Format |  | DOne | Passed all Validations |  | 90 | Error
Wind | Height of Meteorological Instrumentation - Wind Direction | Passed for flag not checked error on audit |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | Meters | Wind | HGT_MET_TWR_WND_DIRT |  | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Format OK Error! Height of Meteorological Instrumentation - Wind Direction (time) should be a numeric value Passed for flag not checked error on audit |  | DOne | Passed all Validations
Wind | Height of Meteorological Instrumentation - Barometric Pressure | Passed for flag not checked error on audit |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | Meters | Wind | HGT_MET_TWR_BAR_PRES |  | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Format OK Error! Height of Meteorological Instrumentation - Barometric Pressure (-7) must be > 0 Error! Height of Meteorological Instrumentation - Wind Direction (-6) must be > 0 Error! Height of Meteorological Instrumentation - Barometric Pressure (eat) should be a numeric value Passed for flag not checked error on audit |  |  | Passed all Validations
Wind | Height of Meteorological Instrumentation - Temperature | Passed for flag not checked error on audit |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | Meters | Wind | HGT_MET_TWR_TEMP |  | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Passed - Format OK Error! Height of Meteorological Instrumentation - Temp (-12) must be > 0 Error! Height of Meteorological Instrumentation - Temp (lunch) should be a numeric value Passed for flag not checked error on audit |  |  | Passed all Validations
Wind | Joint Ownership? |  |  | ADD 04/2012 | Ownership - WIND | WIND_Ownership.View | Y/N | OWNERSHIP | J0CODE |  | 1. Select from the list: Y or N 2. If N then Fixed Ownership 100% | R
Wind | Ownership Start Date |  | 04/09/2012 Changed Validation to be an Optional | ADD 04/2012 | Ownership - Wind | WIND_Ownership.View | mm/dd/yyyy | OWNERSHIP | OWNR_START_DT |  | Format should be: MM/DD/YYYY | R O | Passed - Format OK Form Does not allow |  |  | Passed all Validations
Wind | Ownership Stop Date |  |  | ADD 04/2012 | Ownership - Wind | WIND_Ownership.View | mm/dd/yyyy | OWNERSHIP | OWNR_END_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Passed - Format OK Form Does not allow |  |  | Passed all Validations
Wind | 0°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 5°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Form Does not allow Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 10°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 15°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 20°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 25°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 30°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 35°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 40°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 45°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 50°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 55°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 60°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 65°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 70°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 75°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 80°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 85°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 90°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 95°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 100°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 105°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 110°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 115°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | 120°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R | Passed for value not being entered. error on audit |  | Done | Passed all Validations
Wind | Reactive Capability Data Provided Below Is Gross/Net Values? | Passed for flag not checked error on audit | 04/02/2012 - Updated RARF Field Name, DB Field and removed Net from Drop down List in data Validation | ADD 04/2012 | Reactive Capability - Wind | Wind_ReactiveCapability.View | List | REACT_CAP_WIND | REACT_CAPB_DATA_GROSS_NET_VAL |  | Select from the list: GROSS |  | Passed for flag not checked error on audit |  |  | Passed all Validations
Wind | Reactive Capability Data Provided is from NDCRC Test Data? | Passed for flag not checked error on audit |  | ADD 04/2012 | Reactive Capability - Wind | Wind_ReactiveCapability.View | Y/N | REACT_CAP_WIND | REACT_CAPB_NDCRC_TEST_DATA |  | Select from the list: Y or N |  | Passed for flag not checked error on audit |  |  | Passed all Validations
Wind | If Reactive Capability Data Provided Is From NDCRC test Data Then Enter The Date On Which The Test Was Performed. |  |  | ADD 04/2012 | Reactive Capability - Wind | Wind_ReactiveCapability.View | mm/dd/yyyy | REACT_CAP_WIND | REACT_CAPB_NDCRC_TEST_DATA_DT |  | This field is optional. Format should be: MM/DD/YYYY | O |  |  |  | Passed all Validations
Wind | Does Zero Sequence Z exist? | Passed for flag not checked error on audit |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | Y/N | Wind | DOES_ZERO_SEQ_EXIST |  | Drop down list select Y/N | R | Passed for flag not checked error on audit |  |  | Passed all Validations
Wind | Direct Axis Subtransient Reactance, X"dv (saturated) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Passed 1. Generated Error for field being blank Error! Value (stop) is not a numeric, enter a numeric value 2.Error! Value (-2.0) is < -1, enter a numeric value which is >=-1 and <=1 and Error! Value (2.0) is > 1, enter a numeric value which is >=-1 and <=1 3. Warning! Reactance Value (0.26) should be within calculated typical lower (15.8886) and upper (113.49) reactance limits |  |  | Passed all Validations
Wind | Direct Axis Transient Reactance, X'dv (saturated) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Passed 1. Generated Error for field being blank Error! Value (stop) is not a numeric, enter a numeric value Error! Value (-2.0) is < 0, enter a numeric value which is >=0 and <=2 3. Warning! Reactance Value (0.26) should be within calculated typical lower (27.2376) and upper (136.188) reactance limits |  |  | Passed all Validations
Wind | Positive Sequence Z (saturated) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | R in p.u. | WIND | POSITIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Passed 1. Generated Error for field being blank 2.Error! Value (2.0) is > 1, enter a numeric value which is >=0 and <=1 | NMMS |  | Passed all Validations
Wind | Positive Sequence Z (saturated) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | X in p.u. | WIND | POSITIVE_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | 1. Generated Error for field being blank Error! Value (stop) is not a numeric, enter a numeric value 2. 3. Warning! Reactance Value (0.26) should be within calculated typical lower (15.889) and upper (113.49) reactance limits | NMMS |  | Passed all Validations
Wind | Negative Sequence Z (saturated) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | R in p.u. | WIND | NEGATIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Passed 1. Generated Error for field being blank Error! Value (stop) is not a numeric, enter a numeric value 2. Error! Value (2.0) is > 1, enter a numeric value which is >=0 and <=1 |  |  | Passed all Validations
Wind | Negative Sequence Z (saturated) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | X in p.u. | WIND | NEGATIVE_SEQ_Z_X-SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | 1. Generated Error for field being blank Error! Value (look) is not a numeric, enter a numeric value 2. Warning! Reactance Value (0.26) should be within calculated typical lower (15.889) and upper (147.537) reactance limits |  |  | Passed all Validations
Wind | Zero Sequence Z (saturated) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | R in p.u. | WIND | ZERO_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U | R | Passed 1. Generated Error for field being blank Error! Value (stop) is not a numeric, enter a numeric value 2. Error! Value (2.0) is > 1, enter a numeric value which is >=0 and <=1 | NMMS |  | Passed all Validations
Wind | Zero Sequence Z (saturated) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | X in p.u. | WIND | ZERO_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | 1. Generated Error for field being blank 2. Warning! Reactance Value (0.26) should be within calculated typical lower (2.27) and upper (54.475) reactance limits | NMMS |  | Passed all Validations
Wind | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | 1. Generated Error for field being blank Error! Value (stop) is not a numeric, enter a numeric value 2. 3. Warning! Reactance Value (0.26) should be within calculated typical lower (15.889) and upper (113.49) reactance limits |  |  | Passed all Validations
Wind | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | 1. Generated Error for field being blank Error! Value (stop) is not a numeric, enter a numeric value 2. 3.Warning! Reactance Value (0.26) should be within calculated typical lower (15.889) and upper (113.49) reactance limits |  |  | Passed all Validations
Wind | Zero Sequence Resistance In P.u. (100 Mva Base) |  | 04/24/2012 Remove field from database and form. No validation. | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | ZERO_SEQ_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | REMOVED
Wind | Zero Sequence Reactance In P.u. (100 Mva Base) |  | 04/24/2012 Remove field from database and form. No validation. | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | ZERO_SEQ_Reactance_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | REMOVED
Wind | Average Amount Of Auxiliary Real Power |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | MW | WIND | AUX_MWTOTAL |  | 1) This field is optional 2) Data type is float 3) Value must be < Parameters - GEN - High Reasonability Limit 4) Warn if value > (High Reasonability Limit) * .75 5) Error if value > (High Reasonability Limit) * .66 | R | 1. Generated Error for field being blank 2.Error! Voltage Level (HOW) should be a numeric value, which is > 0 and <= 345 3..Error! Value (34.50) must be < High Reasonability Limit (15.87) 4. Warning! Value (74.) is > 75% of High Reasonability Limit (97.5) 5.Error! Value (65.) must be < 66% of High Reasonability Limit (97.5) |  |  | Passed all Validations
Wind | Average Amount Of Auxiliary Reactive Power |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | MWAR | WIND | AUX_MVARTOTAL |  | 1) This field is optional 2) Data type is Float 3) Value must be < Reactive Capability - GEN - Maximum Lagging Operating Capability (MVAR) 4) Warn if value > ( Maximum Lagging Operating Capability) * .75 5) Error if value > ( Maximum Lagging Operating Capability) * .66 | R | 1. Generated Error for field being blank Error! Value (STOP) is not a numeric, enter a numeric value 2. 3.Error! Value (65.) must be < Max Lagging Operating Capability (47.19) 4 Warning! Value (2.0) is > 75% of Max Lagging Operating Capability (2.3) 5.Error! Value (32.) must be < 66% of Max Lagging Operating Capability (47.19) |  |  | Passed all Validations
Wind | Auxiliary Load Power Factor |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | AUX_LOAD_PWR_FACT |  | Between .8 and 1.0 |  | 1. Generated Error for field being Error! Value (STOP) is not a numeric, enter a numeric value 2. Error! Value (3.00) must be between .8 and 1.0 |  |  | Passed all Validations
Wind | Large Motor, Percent Of Total Mw Load |  | 05/03/2012 removed percent from label on form | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | LRG_MTR_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Passed for correct values 1. Generated Error for field being blank 2. Generated Error if TOTAL % does not = 100% 3. Generated all Errors if Private Network flag is 'Y' |  | Done | Passed all Validations
Wind | Small Motor, Percent Of Total Mw Load |  | 05/03/2012 removed percent from label on form | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | SML_MTR_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Passed for correct values 1. Generated Error for field being blank 2. Generated Error if TOTAL % does not = 100% 3. Generated all Errors if Private Network flag is 'Y' |  | Done | Passed all Validations
Wind | Resistive (heating) Load, Percent Of Total Mw Load |  | 05/03/2012 removed percent from label on form | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | RESISTIVE_LOAD_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Passed for correct values 1. Generated Error for field being blank 2. Generated Error if TOTAL % does not = 100% 3. Generated all Errors if Private Network flag is 'Y' |  | Done | Passed all Validations
Wind | Discharge Lighting, Percent Of Total Mw Load |  | 05/03/2012 removed percent from label on form | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | DISCHARGE LIGHT_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Passed for correct values 1. Generated Error for field being blank 2. Generated Error if TOTAL % does not = 100% 3. Generated all Errors if Private Network flag is 'Y' |  | Done | Passed all Validations
Wind | Other, Percent Of Total Mw Load |  | 05/03/2012 removed percent from label on form | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | OTH_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Passed for correct values 1. Generated Error for field being blank 2. Generated Error if TOTAL % does not = 100% 3. Generated all Errors if Private Network flag is 'Y' |  | Done | Passed all Validations
Wind | Large Motor, Percent Of Total MVAR Load |  | 05/03/2012 removed percent from label on form | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | LRG_MTR_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Passed for correct values 1. Generated Error for field being blank 2. Generated Error if TOTAL % does not = 100% 3. Generated all Errors if Private Network flag is 'Y' |  | Done | Passed all Validations
Wind | Small Motor, Percent Of Total MVAR Load |  | 05/03/2012 removed percent from label on form | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | SML_MTR_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | R | Passed for correct values 1. Generated Error for field being blank 2. Generated Error if TOTAL % does not = 100% 3. Generated all Errors if Private Network flag is 'Y' |  | Done | Passed all Validations
Wind | Discharge Lighting, Percent Of Total MVAR Load |  | 05/03/2012 removed percent from label on form | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | DISCHARGE LIGHT_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Passed for correct values 1. Generated Error for field being blank 2. Generated Error if TOTAL % does not = 100% 3. Generated all Errors if Private Network flag is 'Y' |  | Done | Passed all Validations
Wind | Other, Percent Of Total MVAR Load |  | 05/03/2012 removed percent from label on form | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | OTH_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Passed for correct values 1. Generated Error for field being blank 2. Generated Error if TOTAL % does not = 100% 3. Generated all Errors if Private Network flag is 'Y' |  | Done | Passed all Validations
Wind | High Side Voltage Level (nominal) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | Kv | WIND | HIGH_SIDE_VT_LEVL |  | 1) This field is required 2) Data type must be real 3) Generate an Error if not between 345 and 69 | R | 1. Generated Error for field being blank 2. 3.Error! Value (25) is must be >= 69 | Test 2 | Test 2 | Passed all Validations
Wind | Low Side Voltage Level (nominal) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | KV | WIND | LOW_SIDE_VT_LEVL |  | 1) This field is required 2) Data type must be real 3) Generate an Error if not < 69 | R | 1. Generated Error for field being blank 2. 3.Error! Value (69) is must be < 69 | Test 2 | Test 2 | Passed all Validations
Wind | High Side Voltage Connection |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | List | WIND | HIGH_SIDE_VT_CONNT |  | 1) This field is required 2) Data type must be from list 3) Generate an Error if blank | R | 1 and 3. Generated Error for field being blank | retest 2 | retest 2 | Passed all Validations
Wind | Low Side Voltage Connection |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | List | WIND | LOW_SIDE_VT_CONNT |  | 1) This field is required 2) Data type must be from list 3) Generate an Error if blank | R | 1 and 3. Generated Error for field being blank | retest 2 | retest 2 | Passed all Validations
Wind | Impedance Z |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | IMPEDANCE_Z |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0 | R | 1. Generated Error for field being blank 2. Error! Value (1.0A) is not a numeric, enter a numeric value 3. Error! Value (-1) is must be >= 0 |  | Done | Passed all Validations
Wind | X/R Ratio |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | X_R_RATIO |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 1 | R | 1. Generated Error for field being blank 2. Error! Value (1e10) is not a numeric, enter a numeric value 3. Error! Value (-1) is must be >= 1 |  | Done | Passed all Validations
Wind | Zero Sequence Z |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | ZERO_SEQ_Z |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0 | R | 1. Generated Error for field being blank 2.Error! Value (1.0D) is not a numeric, enter a numeric value 3.Error! Value (-1) is must be >= 0 |  | Done | Passed all Validations
Wind | Zero Sequence X/R Ratio |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | ZERO_SEQ_X_R_RATIO |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 1 | R | 1. Generated Error for field being blank 2.Error! Value (1e10) is not a numeric, enter a numeric value 3.Error! Value (.005) is must be >= 1 |  | Done | Passed all Validations
Wind | Base Mva For Transformer Data |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | MVA | WIND | BASE_MVA_TRANSFORMER_DATA |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank, Generate Warning if > 2000 | R | 1. Generated Error for field being blank 2.Error! Value (1e10) is not a numeric, enter a numeric value 3. Generated Error for field being blank Warning! Value (2050) is must be <= 2000 |  | Done | Passed all Validations
Wind | Cable Type |  | 05/15/2012 changed validation #3 to an ERROR message. Corrected Tab name 03/26/2012 | ADD 04/2012 | Collector System - Wind | CollectorSystem.View |  | COLLECTOR_SYS | CABLE_TYPE |  | 1) This field is required 2) Data type must string 3) Generate an error if blank | R |  |  |  | Passed all Validations
Wind | Voltage Level kV |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System - Wind | CollectorSystem.View | kv | COLLECTOR_SYS | VT_LEVEL_KV |  | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | T |  |  |  | Passed all Validations
Wind | R/kft |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System - Wind | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_R_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank | R |  |  |  | Passed all Validations
Wind | X/kft |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System - Wind | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_X_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank | R |  |  |  | Passed all Validations
Wind | Charging Bc/kft |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System - Wind | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_CHRG_BC_KFT |  | 1) This field is required 2) Data type must float 3) Generate an error if blank | R |  |  |  | Passed all Validations
Wind | R0/kft |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System - Wind | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | ZERO_R0_KFT |  | 1) This field is required 2) Data type must float 3) Generate an errorif blank | R |  |  |  | Passed all Validations
Wind | X0/kft |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System - Wind | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | ZERO_X0_KFT |  | 1) This field is required 2) Data type must float 3) Generate an error if blank | R |  |  |  | Passed all Validations
Wind | Cable Type |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System-Wind Seg Data | CollectorSystem_SegData.View | List | CABLE_SEG_DATA | CABLE_TYPE |  | 1) This field is required 2) Data type must string 3) Generate an error if blank | R |  |  |  | Passed all Validations
Wind | From |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System-Wind Seg Data | CollectorSystem_SegData.View | Integer | CABLE_SEG_DATA | CABLE_SEG_DATA_FROM |  | 1) This field is required 2) Data type must integer 3) Generate an error if blank | R |  |  |  | Passed all Validations
Wind | To |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System-Wind Seg Data | CollectorSystem_SegData.View | Integer | CABLE_SEG_DATA | CABLE_SEG_DATA_TO |  | 1) This field is required 2) Data type must integer 3) Generate an error if blank | R |  |  |  | Passed all Validations
Wind | Circuit Number |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System-Wind Seg Data | CollectorSystem_SegData.View | Integer | CABLE_SEG_DATA | CIRCT_NUM |  | 1) This field is required 2) Data type must integer 3) Generate an error if blank | R |  |  |  | Passed all Validations
Wind | Voltage Level |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System-Wind Seg Data | CollectorSystem_SegData.View | kV | CABLE_SEG_DATA | VT_LEVL |  | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0. | T |  |  |  | Passed all Validations
Wind | Cable Segment Length |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System-Wind Seg Data | CollectorSystem_SegData.View | in kft | CABLE_SEG_DATA | CABLE_SEG_LENTH |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank | R |  |  |  | Passed all Validations
Wind | Number of Turbines on cable segment |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System-Wind Seg Data | CollectorSystem_SegData.View | Integer | CABLE_SEG_DATA | NUM_TURBIN_ON_CABLE_SEG |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank | R |  |  |  | Passed all Validations
Transmission | Zero Sequence Line Resistance In P.u. (100mva Base) |  |  | ADD 04/2012 | Line Data | Line_Information.View | p.u. | LINE | ZERO_SEQ_LINE_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  | Error -1 and left blank | Passed all Validations
Transmission | Zero Sequence Line Reactance In P.u. (100mva Base) |  |  | ADD 04/2012 | Line Data | Line_Information.View | p.u. | LINE | ZERO_SEQ_LINE_REACTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 | R |  | Error -1 and left blank | Passed all Validations
Transmission | Zero Sequence Charging Susceptance In P.u. (100mva Base) |  | 2012-03-08 | ADD 04/2012 | Line Data | Line_Information.View | p.u. | LINE | ZERO_ SEQ_ CHRG_ SUSECPTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  | Error -1 and left blank | Passed all Validations
Transmission | DESCRIPTION OF CHANGE |  | Added 03/26/2012 | Add 04/2012 | Line Temperture | Line_TempDetails.View | List | LINE_TEMP | CHANGE_DESCRIPTION |  | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Joel Koepke
Transmission | Planning Rate C |  | 05/03/2012 Add new field to Line Table also needs to be mapped. Field already existed in form. 03/09/2012 Updated Validation | ADD 04/2012 | Line Temperture | Line_TempDetails.View | MVA | Line | PLANNING_RATE_C |  | This field is required Numeric value Must be >= Nominal Emergency Rating (2HR Rating) | R |  | Error required field Error >= 1400 | Passed all Validations
Transmission | Planning Rate C |  | 05/03/2012 Updated validation rule 03/09/2012 Updated Validation | ADD 04/2012 | Line Temperture | Line_TempDetails.View | MVA | LINE_TEMP | PLANNING_RATE_C |  | 1)Numeric value 2) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be >=Tempature Emergency Rating (2HR Rating) else (if Line Rating (Static or Dynamic) = Static, this field must be blank). | R | Model Adminstration | Test for Ddynamic Line | 1 passed | Defect
Transmission | Continuous Rating |  |  | ADD 04/2012 | Breaker Switch Data | Breaker_Switch.View | MVA | BREAKER_SWITCH | CONTINUOUS_RTG |  | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be <= Nominal (Static) - 2-hr Emergency Rating 3) Value must be <= Nominal (Static) - 15-min Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - Continuous Rating AND value must be >= 115 °F Continuous Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Model Adminstration | Error if Blank Error if 9999 | Passed all Validations
Transmission | 2-hr Emergency Rating |  |  | ADD 04/2012 | Breaker Switch Data | Breaker_Switch.View | MVA | BREAKER_SWITCH | EMGCY_RTG_2HR |  | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be >= Nominal (Static) - Continuous Rating 3) Value must be <= Nominal (Static) - 15-min Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 2-hr Emergency Rating AND value must be >= 115 °F 2-hr Emergency Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Model Adminstration | Error if Blank Error if 9999 | Passed all Validations
Transmission | 15 Min Rating |  |  | ADD 04/2012 | Breaker Switch Data | Breaker_Switch.View | MVA | BREAKER_SWITCH | RTG_15MIN |  | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be >= Nominal (Static) - Continuous Rating 3) Value must be >= Nominal (Static) - 2-hr Emergency Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 15-min Rating AND value must be >= 115 °F 15-min Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Model Adminstration | Error if Blank Error if 9999 | Passed all Validations
Transmission | Zero Sequence Reactance Increment In p.u. |  | 03/08/2012 Removed Validation #3 per plaaning group. | ADD 04/2012 | Capacitor and Reactor Data | Capacitor_Reactor.View | p.u. | CAPREACT | ZERO_SEQ_REACTANCE_INCRMENT_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 | R | Model Adminstration | Error -1 and 220 | Passed all Validations
Transmission | Zero Sequence Data - Winding Connection Code (1-9) |  | 05/15/2012 Updated Validation to Required. 04/24/2012 Change Column name on RARF Form and removed p.u. lable | ADD 04/2012 | Transformer Data | Transformer_Info.View | p.u. | TRANSFORMER | ZERO_SEQ_DATA_WINDING_CON_CODE |  | 1) This field is Required 2) Data type must be string | R | Model Adminstration | Done Error if blank | Passed all Validations
Transmission | Zero Sequence Grounding Resistance For An Impedance Grounded Transformer In P.u. (100 Mva Base) |  |  | ADD 04/2012 | Transformer Data | Transformer_Info.View | p.u. | TRANSFORMER | ZERO_SEQ_GRUND_RESISTANCE_IMPEDANCE_GRUND_TRANS_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Model Adminstration | ERROR -1 and 225 and 22 | Passed all Validations
Transmission | Zero Sequence Grounding Reactance For An Impedance Grounded Transformer In P.u. (100 Mva Base) |  |  | ADD 04/2012 | Transformer Data | Transformer_Info.View | p.u. | TRANSFORMER | ZERO_SEQ_GRUND_REACTANCE_IMPEDANCE_GRUND_TRANS_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Model Adminstration | ERROR -1 and 200 | Passed all Validations
Transmission | Zero Sequence Resistance In P.u. (100 Mva Base) |  |  | ADD 04/2012 | Transformer Data | Transformer_Info.View | p.u. | TRANSFORMER | ZERO_SEQ_TRANS_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Model Adminstration | Blank | Passed all Validations
Transmission | Zero Sequence Reactance In P.u. (100 Mva Base) |  |  | ADD 04/2012 | Transformer Data | Transformer_Info.View | p.u. | TRANSFORMER | ZERO_SEQ_TRANS_REACTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Model Adminstration | ERROR 500 and -12 | Passed all Validations
Transmission | DESCRIPTION OF CHANGE |  | Added 03/26/2012 | Add 04/2012 | Transformer Tap Settings | Transformer_HighTaps.View and Transformer_LowTaps.View | List | TRANSFORMER_TAP_SETTINGS | CHANGE_DESCRIPTION |  | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Joel Koepke |  | Passed all Validations
Transmission | Station Code |  | 03/27/2012 updated | ADD 04/2012 | PUN Load | PUN_LOAD.View | enter all caps | PUN_LOAD | SUBSTATION_CODE |  | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Not null 3) All caps |  |  | ERROR if Y | Passed all Validations
Transmission | Load Name |  | 03/27/2012 updated | ADD 04/2012 | PUN Load | PUN_LOAD.View | List | PUN_LOAD | PUN_LOAD_NAME |  | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Value should following the following convention SiteCode_LoadName. Load Name (Load Name) should be as it appears in the ERCOT Model 3) Not Null | L |  | ERROR if Y | Passed all Validations
Transmission | Load Code |  | 03/27/2012 updated | ADD 04/2012 | PUN Load | PUN_LOAD.View | Automatic | PUN_LOAD | PUN_LOAD_CODE |  | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Not null |  |  | ERROR if Y | Passed all Validations
Transmission | Hour Ending |  | 03/27/2012 updated | ADD 04/2012 | PUN Load | PUN_LOAD.View | Automatic | PUN_LOAD | HOUR_ENDING |  | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Not null |  |  | ERROR if Y | Passed all Validations
Transmission | Day of Week |  | 03/27/2012 updated | ADD 04/2012 | PUN Load | PUN_LOAD.View | Automatic | PUN_LOAD | DAY |  | 1) These fields are conditionally required if "Private Network - Private Network?" = 'Y' and for each Load identified 2) Not Null |  |  | ERROR if Y | Passed all Validations
Transmission | MW |  | 03/27/2012 updated | ADD 04/2012 | PUN Load | PUN_LOAD.View |  | PUN_LOAD | MW |  | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Not null. Must be numeric. 3) Value must be >= 0 (for zero load, place a 0 in that space) |  |  | ERROR if Y | Passed all Validations

## ESG and SOLAR Fields (hidden)
Field/Section Type: R- Required( Not null),O= Optional ,C =Conditional
Validation Type: B = Basic Validation , DVB = Data Validation based on Business Rules , DVE = Data Validation with the existing record in ERCOT
Format /Data type: Numeric, Integer , Character, Date, Dropdown List
Source--> Represents the source of the Validation Rules
RARF FORM TYPE | RARF DATA FIELD | Field Updates | Change Description |  | RARF Tab | Source Report Name | Label | TABLE | DB Field | EXCEL | Business Rules/Basic UI validations | Field/ Tab Type | Source | Destination Application
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | General and Site Information |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | This tab is Required for all Resource Entities (Load and Generation Resources) | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | This submittal is for | Updated 03/09/2012 validation rule to match view |  |  | General and Site Information |  |  | SITECODES | SUBMIT_REASON | Not null. Select from the list: New Site, Revision, Addition of Units, Deletion of Units | Not null. Select from the list: New Site, Revision, Addition of Unit(s), Deletion of Unit(s)* | R
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Submittal Information |  |  |  | General and Site Information |  |  | Not in table | Not in table | Not null. Select from the list: New Site, Revision, Addition of Units, Deletion of Units | Not null. Select from the list: New Site, Revision, Addition of Units, Deletion of Units | R | RARF Glossary Version 4.0 4/RARF Guide version 4.0/ Angela Moy
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Date Form Completed: |  |  |  | General and Site Information |  |  | SITECODES | FORM_COMP_DT | Optional | Not null. Equal to the System Date. Date Format should be mm/dd/yyyy | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Resource Entity Submitting Form: | 03/09/2012 Updated Validation | ADD 04/2012 |  | General and Site Information | GeneralInformation.View |  | RE_RARF | RE_NAME | 1. Not null. 2. Name must match ERCOT records (SIEBEL) | 1.This field is not null. 2. All should be capital letters 3.No Special characters except spaces and dashes. | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Resource Entity DUNS #: |  |  |  | General and Site Information |  |  | SITECODES & RE_RARF | RE_DUNS | 1. Not null. 2. DUNS number must match ERCOT records (SIEBEL) | Not null. Data type should be varchar (as sometimes the value contains # with a leading zero). Duns# is either 9 digit or 13 digit .Should match with RE Duns# IN Siebel | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Site Information |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | This tab is Conditional: Required if the Generation Type is ' WIND or CC or GEN' , where GEN is non-cc non-wind generation resources. This tab is not required for Load Resources. | C | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,MMS,Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Resource Site Name: |  |  |  | General and Site Information |  |  | SITECODES | SITE_NAME | 1. Not null. 2. Validate with ERCOT records (Lodestar). 3. All should be capital letters | 1.This field is not null. Validate with the existing record in ERCOT?? 2. All should be capital letters | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | EMS,Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Resource Site Code: | 05/02/2012 Updated Table that this field is mapped to, adding SITE_LOAD_SPLIT. |  |  | General and Site Information |  |  | SITECODES & SITE_LOAD_SPLIT | SITE_CODE | 1. Not null. 2. Validate with ERCOT records (Lodestar). 3. All should be capital letters | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Street Address: |  |  |  | General and Site Information |  |  | SITECODES | STREET_ADDRESS | Not null | Not null | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | City: |  |  |  | General and Site Information |  |  | SITECODES | CITY | Not null | Not null | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | State |  |  |  | General and Site Information |  |  | SITECODES | STATE | Not null | This is Required field (can not be null) Data type should be character, no numbers or commas are allowed. | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Zip Code |  |  |  | General and Site Information |  |  | SITECODES | ZIPCODE | Not null | This is a Required field and can not be null. Only numbers are allowed | R |  | Siebel
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | County: |  |  |  | General and Site Information |  |  | SITECODES | COUNTY | Not null | Not null | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Site In-Service Date: |  |  |  | General and Site Information |  |  | SITECODES | SITE_IN_SRVC_DT | 1. Must be earlier than Site-Stop Service Date. 2. mm/dd/yy format. 3. Not null. | Site-In Service Date is earlier than Site-Stop Service Date. Enter the date in mm/dd/yy format. This field is not null. | R | Lin Xu | Lodestar,MMS
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Site Stop Service Date: |  |  |  | General and Site Information |  |  | SITECODES | SITE_STOP_SRVC_DT | 1. Must be later than Site In-Service Date. 2. mm/dd/yy format. 3. Not null. | Site Stop Service Date should be later than Site-In Service Date. Format is mm/dd/yyy. This field is optional. NA is not valid , Leave it blank if not applicable. | O | Lin Xu | Lodestar,MMS
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Congestion Management Zone for 2003: |  |  |  | General and Site Information |  |  | SITECODES | CMZ_2003 | 1. Select from the list: North,South,Houston,West. 2. Not Null | Select from the list: North,South,Houston,West. This field is Required | O | RARF Glossary Version 4.0/ Angela Moy
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Resource owned by NOIE? |  |  |  | General and Site Information |  |  | SITECODES | RE_OWNED_NOIE_FLG | 1. Select from the list: Y or N 2. Not Null | Select from the list: Y or N | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Is Resource behind a NOIE Settlement Meter Point? |  |  |  | General and Site Information |  |  | SITECODES | RE_BHND_NOIE_SMP_FLG | 1. Select from the list: Y or N 2. Not Null | Select from the list: Y or N | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Number of EPS Primary meters: |  |  |  | General and Site Information |  |  | SITECODES | NUM_EPS_METERS | Not null | This field is required and it should be an integer | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Is Resource claiming status as a Non-Modeled Generator as defined in ERCOT Protocol Section 2, Resource | 05/23/2012 Updated validation Rule 04/12/2012 Updated RARF TAB | ADD 04/2012 |  | Site Info - DG General Information - DG | DG_SiteInfo.View | Y/N | SITECODES | RE_CLAIM_NONMOD_STATUS |  | 1. If Site_Code is in NON_MODELED then If RE_CLAIM_NONMOD_STATUS is null then Error Else if RE_CLAIM_NONMOD_STATUS not Y or N, Error If Site_Code is NOT in NON_MODELED then do not validate | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Is Resource >10 MW? | 05/23/2012 Updated validation Rule 04/12/2012 Updated RARF TAB | ADD 04/2012 |  | Site Info - DG General Information - DG | DG_SiteInfo.View | Y/N | SITECODES | RES_GREAT_TEN_MW |  | 1.If Site_Code is in NON_MODELED then If RE_CLAIM_NONMOD_STATUS is null then Error Else if RE_CLAIM_NONMOD_STATUS not Y or N, Error If Site_Code is NOT in NON_MODELED then do not validate . | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Primary Contact (name of person ERCOT can contact with questions regarding this form) |  |  |  | General and Site Information |  |  | Not in table | Not in table
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Printed Name: |  |  |  | General and Site Information |  |  | SITECODES | NAME_PC | Not null | Not null. Validate that the Authorized rep has valid digital certificate to access the User Interface | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Title: |  |  |  | General and Site Information |  |  | SITECODES | TITLE_PC | Not null | Not null | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Phone Number: |  |  |  | General and Site Information |  |  | SITECODES | PHONE_PC | Not null | Not null | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | E-mail Address: |  |  |  | General and Site Information |  |  | SITECODES | EMAIL_PC | Not null | Not null | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Fax Number: |  |  |  | General and Site Information |  |  | SITECODES | FAX_PC | Optional | Optional | O | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Secondary Contact (if available) |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | Optional
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Printed Name: |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | Optional
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Title: |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | Optional
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Phone Number: |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | Optional
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | E-mail Address: |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | Optional
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Fax Number: |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | Optional
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | GEN Load Split -ESIID |  |  |  | GEN Load Split -ESIID |  |  | Not in table | Not in table
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | GENERATION SITE LOAD DETAILS |  |  |  | GEN Load Split -ESIID |  |  | Not in table | Not in table
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | ESIID_NUMBER |  | ADD 02/2012 to RARF FORM |  | GEN Load Split - ESIID |  |  | SITE_LOAD_SPLIT | ESIID_NUMBER | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2. Must have minimum of 2 ESI ID's entered 3. Data type is character | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Generate ESIID Number + 1 (ex. ESIID_1, ESIID_2, ESIID_3)
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | SITECODE_ESIID |  | ADD 02/2012 to RARF FORM |  | GEN Load Split - ESIID |  |  | SITE_LOAD_SPLIT | SITECODE_ESIID | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2.Concantanate SITE_CODE and ESIID_NUMBER | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Concantanate SITECODE_ESIID_Number
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Generation Load Split? | Corrected 02/29/2012 |  |  | GEN Load Split - ESIID |  | Y/N | SITECODES | GEN_LOAD_SPLIT_FLG | 1.This field is conditional. Required only if Generation Load Split is 'N'. 2. Not Required of Resource Behind NOIE Settlement point is 'Y' 2. Data type is character | Select from the list: Y or N | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | ERCOT Read Meter? |  |  |  | GEN Load Split - ESIID |  | Y/N | SITECODES | ERCOT_READ_FLG | 1. Select from the list: Y or N 2. Not Null | Select from the list: Y or N | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | SITECODE | 05/02/2012 Removed from form, column remains but data will now be populated from SITECODE tab | ADD 02/2012 |  | GEN Load Split - ESIID |  | Automatic | SITECODES & SITE_LOAD_SPLIT | SITE_CODE | 1. Not null. 2. Validate with ERCOT records (Lodestar). 3. All should be capital letters | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | ESI ID: | 05/02/2012 Updated Validation Rule | UPDATE 02/2012 |  | GEN Load Split - ESIID |  |  | SITE_LOAD_SPLIT | ESI_ID |  | 1.Data type is character 2.If Generation Load Split is 'N', ESIID is required. 3. If Generation Load Split is 'Y' then If RE_BHND_NOIE_SMP_FLG is 'Y' and Site_Code is in NON_MODELED, then no ESIID is required else ESIID is required | C | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | TDSP Providing Service To Resource: | Corrected |  |  | GEN Load Split - ESIID |  | List | SITE_LOAD_SPLIT | TDSP_PROVIDING_SVC | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Select From drop down list provided. | This field is conditional. Required only if If the Generation Load Split question is answered as 'N' . Validate with the existing record in ERCOT?? | C | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | TDSP DUNS Number: | 03/09/2012 Updated Validation |  |  | GEN Load Split - ESIID |  | Automatic | SITE_LOAD_SPLIT | TDSP_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Prepopulated with DUNS of TDSP provided in cell above | 1. Not null 2. Must match with the data existing in Siebel 3. Data type: varchar (as sometimes the value contains # with a leading zero) 4. Either a 9 or 13 digit DUNS number | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Fixed Load Splitting % | 05/03/2012 removed percent from label on form |  |  | GEN Load Split - ESIID |  |  | SITE_LOAD_SPLIT | FIXED_LD_SPLIT | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2. Must have minimum of 2 ESI ID's entered | 1.This field is optional/conditional. Required only if Gen Site is split among multiple ESI Id's.If entered, cross check the data with Lodestar. 2. Sum of the Fixed Load Splitting % (corresponding to each ESIID) should be 100. Generate an error if the rule fails | C/O | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Load Serving Entity |  |  |  | GEN Load Split - ESIID |  | List | SITE_LOAD_SPLIT | COMP_RETAILER | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Select From drop down list provided. | This field is optional/conditional. Required only if Gen Site is split among multiple ESI Id's. | C | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Load Serving Entity Duns# |  |  |  | GEN Load Split - ESIID |  | Automatic | SITE_LOAD_SPLIT | COMP_RETAILER_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Prepopulated with DUNS of Competitive Retailer provided in cell above | This field is optional/conditional. Required only if Gen Site is split among multiple ESI Id's. If entered it should be either 9 or 13 digit number AND should match with the existing record in Lodestar? | C | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Private Network - Site |  |  |  | Private Network - Site |  |  | Not in table | Not in table
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | SITE DETAILS |  |  |  | Private Network - Site |  |  | Not in table | Not in table
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Private Network? | 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  | Y/N | SITECODES | PRIVATE_NTWK_SITE_FLG |  | Select from Y or N. Private Network Flag is not null | R
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | PRIVATE NETWORK - SITE INFORMATION |  |  |  | Private Network - Site |  |  | Not in table | Not in table |  | This tab is conditional : Required for all Private Use Networks
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Average Amount Of Self-serve Private Load | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  | MW | SITECODES | AVG_LD_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Average Amount Of Self-serve Private Reactive Load | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  | MVAR | SITECODES | AVG_LD_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Expected Typical Private Network Net Interchange | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  | MW | SITECODES | NET_INTERCHNG_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Expected Typical Private Network Net Reactive Interchange | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  | MVAR | SITECODES | NET_INTERCHNG_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Private Network Gross Unit Capability | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  | MW | SITECODES | GROSS_CAPBLTY_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Private Network Gross Unit Reactive Capability | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  | MVAR | SITECODES | GROSS_CAPBLTY_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Load Characteristics For MW Load |  |  |  | Private Network - Site |  |  | Not in table | Not in table |  | This tab is conditional : Required for all Private Use Networks
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Large Motor, Percent Of Total | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  |  | SITECODES | PUN_MW_LARGEMTR_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Small Motor, Percent Of Total | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  |  | SITECODES | PUN_MW_SMALLMTR_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Resistive (heating) Load, Percent Of Total MW Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  |  | SITECODES | PUN_MW_RESISTIVE_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Discharge Lighting, Percent Of Total | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  |  | SITECODES | PUN_MW_DISCHARGE_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Other, Percent Of Total MW Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  |  | SITECODES | PUN_MW_OTHER_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Load Characteristics for MVAR Load |  |  |  | Private Network - Site |  |  | Not in table | Not in table |  | This tab is conditional : Required for all Private Use Networks
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Large Motor, Percent Of Total MVAR Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  |  | SITECODES | PUN_MVAR_LARGEMTR_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Small Motor, Percent Of Total MVAR Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  |  | SITECODES | PUN_MVAR_SMALLMTR_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | R
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Discharge Lighting, Percent Of Total MVAR Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  |  | SITECODES | PUN_MVAR_DISCHARGE_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Other, Percent Of Total MVAR Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  |  | SITECODES | PUN_MVAR_OTHER_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C
Solar | UNIT INFO - Solar |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View |  | Not in table | Not in table
Solar | GENERATOR DETAILS |  |  |  | UNIT INFO - Solar |  |  | Not in table | Not in table
Solar | Unit Name |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | all caps | SOLAR | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R
Solar | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | Automatic | SOLAR | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C
Solar | Non Modeled Generation |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | Y/N | SOLAR | NON_MOD_GEN |  | 1.Select from the list: Y or N 2.Not Null
Solar | PUC Registration Number (Docket Number) |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View |  | SOLAR | PUC_NUM |  | This field is optional and it should be a number. NA is not valid , Leave it blank if not applicable.
Solar | ERCOT Interconnection Project Number - Only new Units |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View |  | SOLAR | ERCOT_INTRCONN_PROJ_NUM |  | 1.This field is optional. Required only for new units. Enter a Valid Number or leave it blank if not applicable 2. Cross check with the data entered in the field 'This submittal is for' in General Information Tab. If the value is 'New Site' then only this field is required.
Solar | NERC Number (NERC ID#) |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View |  | SOLAR | NERC_NUM |  | This field is optional. NA is not valid , Leave it blank if not applicable.
Solar | Qualifying facility |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | Y/N | SOLAR | QUAL_FACILITY_FLG |  | QF flag is not null. Select from the list: Y or N
Solar | SITE AND UNIT DATES |  |  |  | UNIT INFO - Solar |  |  | Not in table | Not in table
Solar | Transmission Only Date (POI) |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | mm/dd/yyyy | SOLAR | TRANS_ONLY_DT |  | 1.This field is optional. Format should be: MM/DD/YYYY 2. Data type must be Date.
Solar | Standard Generation Interconnection Agreement (SGIA) Signature Date |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | mm/dd/yyyy | SOLAR | SGIA_SIG_DT |  | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date.
Solar | Unit Start Date (Model Ready Date) | 03/13/2012 Updated Validation | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | mm/dd/yyyy | SOLAR | UNIT_MRD_ST_DT |  | This field is optional. Format should be: MM/DD/YYYY
Solar | Unit Commercial Date |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | mm/dd/yyyy | SOLAR | UNIT_START_DT |  | This field is not null. Format should be: MM/DD/YYYY Unit Start Date should be >= Site Start Date ( Site-Information Tab)
Solar | Unit End Date |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | mm/dd/yyyy | SOLAR | UNIT_END_DT |  | This field is optional. Format should be: MM/DD/YYYY
Solar | POINT OF INTERCONNECTION |  |  |  | UNIT INFO - Solar |  |  | Not in table | Not in table
Solar | SubStation Code/SubStation Mnemonic |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | all caps | SOLAR | SUBSTAT_CODE_SUB_MNEMONIC |  | 1) This field is not null (required). Data type must be Character. 2) Must match ERCOT records (unless new). Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" . 4) Must be <= 8 characters. Warning! Substation Code should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) Substation code should be in Upper case letters. Generate an error if the rule fails.
Solar | Voltage Level |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | kV | SOLAR | VOL_LEV |  | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0.
Solar | PTI Bus Number |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | # | SOLAR | PTI_BUS_NUM |  | 1) This field isnot null (required). Data type must be Integer. 2) The value must be > 0.
Solar | FUEL INFORMATION |  |  |  | UNIT INFO - Solar |  |  | Not in table | Not in table
Solar | Primary Fuel Type |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | List | SOLAR | PRIM_FUELTYPE |  | 1)Resource Category is not null. 2)Select from the list: SUN,NA,NG and OT
Solar | Secondary Fuel Type |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | List | SOLAR | SEC_FUELTYPE |  | 1)Resource Category is not null. 2)Select from the list: SUN,NA,NG and OT
Solar | Fuel Transportation Type |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | List | SOLAR | FUEL_TRANSTYPE |  | NA
Solar | Resource Category |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | List | SOLAR | RES_CATG |  | 1)Resource Category is not null. 2)Select from the list: Solar
Solar | RATINGS AND DESIGNS |  |  |  | UNIT INFO - Solar |  |  | Not in table | Not in table
Solar | Renewable |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | Y/N | SOLAR | RENEWABLE_FLG |  | Renewable Flag is not null. Select from the list: Y or N
Solar | Renewable/Offset |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | List | SOLAR | RENEWABLE_OFFSET |  | Select from the list : RN, OS, NA. This field is not null.
Solar | Physical Unit Type |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | List | SOLAR | PHYS_UNIT_TYPE |  | Select from the list:CA, CC, CE, CS, CT, FC, GT, HY, IC, NA, OT, PS, PV, ST, WT. This field is not null.
Solar | Name Plate Rating |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | MVA | SOLAR | NAME_PLT_RTG |  | Name Plate Rating should be >= Real Power Rating
Solar | Real Power Rating |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | MW | SOLAR | RTG_MW |  | Real Power Rating should be > Reactive Power Rating
Solar | Reactive Power Rating |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | MVAR | SOLAR | RTG_MVAR |  | Name Plate Rating should be >= Reactive Power Rating
Solar | Unit Generating Voltage |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | kV | SOLAR | UNIT_KV |  | 1. This field is not null and it should be a number 2. Unit Generating voltage can not be below 4.16 KV
Solar | Governor Droop Setting | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View |  | SOLAR | GOV_DROOP |  | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if it is not between 0 and 25. Generate Warning if > 5 (protocol requirement).
Solar | Governor Dead-Band |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | Hz | SOLAR | GOV_DEAD_BND |  | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if > 0.1. Generate Warning if > 0.03.
Solar | Design Max Ambient Temperature |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | degree F | SOLAR | DESIGN_MAX_AMB_TEMP |  | >100 <150
Solar | Design Min Ambient Temperature |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | degree F | SOLAR | DESIGN_MIN_AMB_TEMP |  | >-100 <32
Solar | GEOGRAPHIC LOCATION (CENTER OF PLANT) |  |  |  | UNIT INFO - Solar |  |  | Not in table | Not in table
Solar | Latitude Of Center Of Plant |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | decimal degrees (N) | SOLAR | LAT_CENTER_PLT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if Latitude < 25.0 or > 37.0.
Solar | Longitude Of Center Of Plant |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | decimal degrees (W) | SOLAR | LONG_CENTER_PLT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if <93 or > 107 .
Solar | Unit Info - Solar Inverter |  |  |  | Unit Info - Solar Inverter |  |  | Not in table | Not in table
Solar | GENERATOR Details |  |  |  | Unit Info - Solar Inverter |  |  | Not in table | Not in table
Solar | Unit Name |  | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | List | SOLAR_INVERTER | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R
Solar | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | Automatic | SOLAR_INVERTER | UNIT_CODE |  | .This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C
Solar | Total Number of Inverters |  | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | # | SOLAR_INVERTER | TOTNUM_INVERTERS |  | 1.This is not null and it should be an Integer 2. Not null.
Solar | MODULE 1 - INVERTER DETAILS | Changed Data Field Name on RARF Form 03/26/2012 |  |  | Unit Info - Solar Inverter |  |  | Not in table | Not in table
Solar | Module 1 - Type of INVERTER (Manufacturer/Model) | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | all caps | SOLAR_INVERTER | GRP1_INV_TYPE |  | This field is not null and the Data type should be character.
Solar | Module 1 - MW Rating for this model of INVERTER | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | MW | SOLAR_INVERTER | GRP1_INV_MW_MDL_RTG |  | This field is not null and it should be an integer
Solar | Module 1 - Number of this type of INVERTER | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | # | SOLAR_INVERTER | GRP1_INV_NUM |  | 1. This field is optional. If entered it should be a character. If the data is entered for Group2, then reactive capability- Solar Tab should have values for this group. 2. Inverter groups of Inverters within a unit must be of the same type and size. RARF Audit report should generate a warning if this rule fails
Solar | MODULE 2 - INVERTER DETAILS | Changed Data Field Name on RARF Form 03/26/2012 |  |  | Unit Info - Solar Inverter |  |  | Not in table | Not in table
Solar | Module 2 - Type of INVERTER (Manufacturer/Model) | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | all caps | SOLAR_INVERTER | GRP2_INV_TYPE |  | This field is optional/conditional. Required if Type of Inverter info is entered for Group2 otherwise it is optional. Data type should be Integer. If the data is entered for Group2, then reactive capability-Solar Tab should have values for this group.
Solar | Module 2 - MW Rating for this model of INVERTER | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | MW | SOLAR_INVERTER | GRP2_INV_MW_MDL_RTG |  | 1. This field is optional. If entered it should be a character. If the data is entered for Group3, then reactive capability-Solar Tab should have values for this group. 2. Wind groups of Inverters within a unit must be of the same type and size. RARF Audit report should generate a warning if this rule fails
Solar | Module 2 - Number of this type of INVERTER | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | # | SOLAR_INVERTER | GRP2_INV_NUM |  | 1. Conditional required if Type of Inverter info is entered for Group2 2. Data type should be numeric.
Solar | MODULE 3 - INVERTER DETAILS | Changed Data Field Name on RARF Form 03/26/2012 |  |  | Unit Info - Solar Inverter |  |  | Not in table | Not in table
Solar | Module 3 - Type of INVERTER (Manufacturer/Model) | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | all caps | SOLAR_INVERTER | GRP3_INV_TYPE |  | 1. Conditional required if Type of Inverter info is entered for Group3 2. Data type should be numeric.
Solar | Group 3 - MW Rating for this model of INVERTER | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | MW | SOLAR_INVERTER | GRP3_INV_MW_MDL_RTG |  | This field is optional/conditional. Required if Type of Inverter info is entered for Group5 otherwise it is optional. Data type should be Integer. If the data is entered for Group5, then reactive capability-Solar Tab should have values for this group.
Solar | Group 3 - Number of this type of INVERTER | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | # | SOLAR_INVERTER | GRP3_INV_NUM |  | This field is optional/conditional. Required if Type of Inverter info is entered for Group4 otherwise it is optional. Data type should be Integer. If the data is entered for Group4, then reactive capability-Solar Tab should have values for this group.
Solar | MODULE 4 - INVERTER DETAILS | Changed Data Field Name on RARF Form 03/26/2012 |  |  | Unit Info - Solar Inverter |  |  | Not in table | Not in table
Solar | Module 4 - Type of INVERTER (Manufacturer/Model) | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | all caps | SOLAR_INVERTER | GRP4_INV_TYPE |  | 1. Optional. 2. Group4 reactive capability-Solar Tab should have values for this group.
Solar | Module 4 - MW Rating for this model of INVERTER | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | MW | SOLAR_INVERTER | GRP4_INV_MW_MDL_RTG |  | This field is optional/conditional. Required if Type of Inverter info is entered for Group5 otherwise it is optional. Data type should be Integer. If the data is entered for Group5, then reactive capability-Solar Tab should have values for this group.
Solar | Module 4 - Number of this type of INVERTER | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | # | SOLAR_INVERTER | GRP4_INV_NUM |  | 1. Conditional required if Type of Inverter info is entered for Group3 2. Data type should be numeric.
Solar | MODULE 5 - INVERTER DETAILS | Changed Data Field Name on RARF Form 03/26/2012 |  |  | Unit Info - Solar Inverter |  |  | Not in table | Not in table
Solar | Module 5 - Type of INVERTER (Manufacturer/Model) | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | all caps | SOLAR_INVERTER | GRP5_INV_TYPE
Solar | Module 5 - MW Rating for this model of INVERTER | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | MW | SOLAR_INVERTER | GRP5_INV_MW_MDL_RTG
Solar | Module 5 - Number of this type of INVERTER | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | # | SOLAR_INVERTER | GRP5_INV_NUM
ESG | Site Information - ESG |  |  |  | Site Information - ESG |  |  | Not in table | Not in table
ESG | Site Information for ESG Resource |  |  |  | Site Information - ESG |  |  | Not in table | Not in table
ESG | Dispatch Asset Code (Provided by ERCOT) | 04/04/2012 removed from RARF Form but needed for Reports | ADD 04/2012 | NOT IN RARF FORM | Site Information - ESG | ESG_SiteInfo.View | all caps | ESGUNIT | DISPATCH_ASSET_CODE
ESG | Resource Site Name: |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | all caps | SITECODES | SITE_NAME
ESG | ESG Resource Site Code: |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | all caps | SITECODES | SITE_CODE
ESG | Street Address: |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View |  | SITECODES | STREET_ADDRESS
ESG | City: |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View |  | SITECODES | CITY
ESG | State |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View |  | SITECODES | STATE
ESG | Zipcode |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View |  | SITECODES | ZIPCODE
ESG | County: |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View |  | SITECODES | COUNTY
ESG | Congestion Management Zone for 2003: |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | List | SITECODES | CMZ_2003 |  | 1. Select from the list: North,South,Houston,West. 2. Not Null
ESG | Is Storage Netted From Generation at ERCOT Read Gensite? |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | Y/N | SITECODES | RE_OWNED_NOIE_FLG |  | 1. Select from the list: Y or N 2. Not Null
ESG | Is Storage Behind a NOIE Settlement Meter Point? |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | Y/N | SITECODES | RE_BHND_NOIE_SMP_FLG |  | 1. Select from the list: Y or N 2. Not Null
ESG | Will site be acting as a CLR during Charging State? |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | Y/N | ESGUNIT | CLR_CHARGING_STATE_FLG
ESG | Load Resource Type (CLR/UFR/Interruptible) |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | List | ESGUNIT | LR_TYPE_CLR_UFR_FLG
ESG | If CLR, will CLR be Dynamically Scheduling? |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | Y/N | ESGUNIT | CLR_DS_FLG
ESG | Storage Resource Effective Date |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | mm/dd/yyyy | ESGUNIT | STORAGE_RE_START_DT |  | 1. Must be earlier than Site-Stop Service Date. 2. mm/dd/yy format. 3. Not null.
ESG | Storage Resource Expiration Date |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | mm/dd/yyyy | ESGUNIT | STORAGE_RE_STOP_DT |  | 1. Must be later than Site In-Service Date. 2. mm/dd/yy format. 3. Not null.
ESG | Substation Name for POD |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | all caps | ESGUNIT | SUBSTATION_NAME_POD
ESG | Substation Code for POD |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | all caps | ESGUNIT | SUBSTATION_NAME_POD
ESG | Transmission Bus POD (PTI Bus No) |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | # | ESGUNIT | TRANSMISSION_BUS_POD_PTI_BUS_NO
ESG | Voltage Level of Telemetered load(s) |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | kV | ESGUNIT | VOLTAGE_LEVEL_TELEMETERED_LOAD
ESG | Meter Reading Entity (TDSP) |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | List | ESGUNIT | METER_READING_ENTITY
ESG | Meter Reading Entity Duns Number |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | Automatic | ESGUNIT | METER_READING_ENTITY_DUNS_NO
ESG | ESI-ID assigned to meter |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View |  | ESGUNIT | ESIID_ASSIGNED_METER
ESG | Wholesale Delivery Point? |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | Y/N | ESGUNIT | WHOLESALE_DELIVERY_PT
ESG | Load Resource Control Device |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | List | ESGUNIT | LR_CONTROL_DEVICE
ESG | ERCOT Load Zone |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | List | ESGUNIT | ERCOT_LOAD_ZONE
ESG | Private Use Network? |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | Y/N | ESGUNIT | PUN_FLG
ESG | Resource owned by NOIE? |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | Y/N | ESGUNIT | NOIE_FLG |  | Select from the list: Y or N
ESG | Is Resource behind a NOIE Settlement Meter Point? |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | Y/N | ESGUNIT | RE_NOIE_SETTLEMENT_METER_POINT_FLG |  | Select from the list: Y or N
ESG | Number of EPS Primary meters: |  | ADD 04/2012 |  | Site Information - ESG | ESG_SiteInfo.View | Integer | SITECODES | NUM_EPS_METERS |  | This field is required and it should be an integer
ESG | Unit Info - ESG |  |  |  | Unit Info - ESG |  |  | Not in table | Not in table
ESG | GENERATOR Details |  |  |  | Unit Info - ESG |  |  | Not in table | Not in table
ESG | Unit Name |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | all caps | ESGUNIT | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Lodestar,NMMS | Lodestar,NMMS
ESG | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | Automatic | ESGUNIT | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Lodestar,NMMS | Lodestar,NMMS
ESG | Dispatch Asset Code (Provided by ERCOT) | 04/04/2012 Add to form and ESGUNIT Table also added validation | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View |  | ESGUNIT | DISPATCH_ASSET_CODE |  | Required if DB Field = Withdrawing in ESGUNIT Table
ESG | Non Modeled Generation |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | Y/N | ESGUNIT | NON_MOD_GEN |  | Select from the list: Y or N | R
ESG | PUC Registration Number (Docket Number) |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View |  | ESGUNIT | PUC_NUM |  | This field is optional. Enter a Valid Number or leave it blank if not applicable | O
ESG | ERCOT Interconnection Project Number - only new units |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View |  | ESGUNIT | ERCOT_INTRCONN_PROJ_NUM |  | 1.This field is optional. Required only for new units. Enter a Valid Number or leave it blank if not applicable 2. Cross check with the data entered in the field 'This submittal is for' in General Information Tab. If the value is 'New Site' then only this field is required. | O
ESG | NERC Number (NERC ID#) |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View |  | ESGUNIT | NERC_NUM |  | This field is optional. Enter a Valid Number or leave it blank if not applicable | O
ESG | Qualifying facility |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | Y/N | ESGUNIT | QUAL_FACILITY_FLG |  | QF flag is not null. Select from the list: Y or N | R
ESG | SITE AND UNIT DATES |  |  |  | Unit Info - ESG |  |  | Not in table | Not in table
ESG | Transmission Only Date (POI) |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | mm/dd/yyyy | ESGUNIT | TRANS_ONLY_DT |  | This field is optional. Format should be: MM/DD/YYYY | O
ESG | Standard Generation Interconnection Agreement (SGIA) Signature Date |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | mm/dd/yyyy | ESGUNIT | SGIA_SIG_DT |  | 1) This field is required 2) Data type must be date 3) Generate an Error if blank. Generate Warning if > current date | R
ESG | Unit Start Date (Model Ready Date) | 03/13/2012 Updated Validation | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | mm/dd/yyyy | ESGUNIT | UNIT_MRD_ST_DT |  | This field is optional. Format should be: MM/DD/YYYY | R
ESG | Unit Commercial Date |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | mm/dd/yyyy | ESGUNIT | UNIT_START_DT |  | This field is not null. Format should be: MM/DD/YYYY Unit Start Date should be >= Site Start Date ( Site-Information Tab) | R
ESG | Unit End Date |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | mm/dd/yyyy | ESGUNIT | UNIT_END_DT |  | This field is optional. Format should be: MM/DD/YYYY | O
ESG | POINT OF INTERCONNECTION |  |  |  | Unit Info - ESG |  |  | Not in table | Not in table
ESG | SubStation Code/SubStation Mnemonic |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | all caps | ESGUNIT | SUBSTAT_CODE_SUB_MNEMONIC |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital. 3. Should not allow spaces. 4. Can not exceed 13 characters for split gen resources | R
ESG | Voltage Level |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | kV | ESGUNIT | VOL_LEV |  | 1) This field is not null (required). Data type must be a numeric. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0. | T
ESG | PTI Bus Number |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View |  | ESGUNIT | PTI_BUS_NUM |  | 1) This field isnot null (required). Data type must be Integer. 2) The value must be > 0. | T
ESG | FUEL INFORMATION |  |  |  | Unit Info - ESG |  |  | Not in table | Not in table
ESG | Energy Storage Technology Type |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | List | ESGUNIT | PHYS_UNIT_TYPE |  | 1) This field is required 2) Data type must be one from a list of possibilities FC,NA,OT | R
ESG | Primary Fuel Type | 03/08/2012 Updated List | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | List | ESGUNIT | PRIM_FUELTYPE |  | Select from the list: OTH, NA | R
ESG | Secondary Fuel Type | 03/08/2012 Updated List | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | List | ESGUNIT | SEC_FUELTYPE |  | Select from the list: OTH, NA | R
ESG | Fuel Transportation Type | 03/08/2012 Updated List | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | List | ESGUNIT | FUEL_TRANSTYPE |  | Select from the list: NA | R
ESG | RATINGS AND DESIGNS |  |  |  | Unit Info - ESG |  |  | Not in table | Not in table
ESG | Renewable |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | Y/N | ESGUNIT | RENEWABLE_FLG |  | Renewable Flag is not null. Select from the list: Y or N | R
ESG | Renewable/Offset |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | List | ESGUNIT | RENEWABLE_OFFSET |  | Select from the list : RN, OS, NA. This field is not null. | R
ESG | Resource Category | 03/08/2012 Updated List | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | List | ESGUNIT | RES_CATG |  | Select from the list: Energy Storage | R
ESG | Name Plate Rating |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | MVA | ESGUNIT | NAME_PLT_RTG |  | Name Plate Rating should be >= Real Power Rating | R
ESG | Real Power Rating |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | MW | ESGUNIT | RTG_MW |  | Real Power Rating should be > Reactive Power Rating | R
ESG | Reactive Power Rating |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | MVAR | ESGUNIT | RTG_MVAR |  | Name Plate Rating should be >= Reactive Power Rating | R
ESG | Turbine Rating |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | MW | ESGUNIT | TURBINE_RTG |  | This field is optional. Enter Numeric value or leave it blank if not applicable. | O
ESG | Unit Generating Voltage |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | kV | ESGUNIT | UNIT_KV |  | 1. This field is not null and it should be a number 2. Unit Generating voltage can not be below 4.16 KV | R
ESG | Governor (or equivalent) Droop Setting (%) | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View |  | ESGUNIT | GOV_DROOP |  | 1) This field is required 2) Data type must be Numeric, Positive Value. 3) Generate an Error if it is not between 0 and 25. Generate Warning if > 5 (protocol requirement). | R
ESG | Governor (or equivalent) Dead-Band (Hz) |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | Hz | ESGUNIT | GOV_DEAD_BND |  | 1) This field is required 2) Data type must be Numeric, Positive Value. 3) Generate an Error if > 0.1. Generate Warning if > 0.03. | R
ESG | Is Resource Duration Limited (DLR) |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | Y/N | ESGUNIT | DLR_LIMITED |  | 1) This field is required 2) Data type must be 'Y' or 'N' 3) Generate an Error if blank | R
ESG | DLR sustained energy output for 1 hour |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | MWh | ESGUNIT | DLR_ENRGY_OUTPUT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if > 1000. | R
ESG | Maximum Energy Storage Capability |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | MWh | ESGUNIT | MAX_ENRGY_STORG_CAPB |  | 1. This field is not null and it should be a number | R
ESG | GEOGRAPHIC LOCATION (CENTER OF PLANT) |  |  |  | Unit Info - ESG |  |  | Not in table | Not in table
ESG | Latitude Of Center Of Plant |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | decimals degrees (N) | ESGUNIT | LAT_CENTER_PLT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if Latitude < 25.0 or > 37.0. | R
ESG | Longitude Of Center Of Plant |  | ADD 04/2012 |  | Unit Info - ESG | Audit - ESG_UnitInfo.View Delta - ESGUNIT_UnitInfo.View | decimals degrees (W) | ESGUNIT | LONG_CENTER_PLT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if <93 or > 107 . | R
ESG | SubSync - ESG |  |  |  | Unit Info - ESG |  |  | Not in table | Not in table
ESG | GENERATOR Details |  |  |  | SubSync |  |  | Not in table | Not in table
ESG | Unit Name |  | ADD 04/2012 |  | SubSync | SUBSYNC.View | List | SUBSYNC | UNIT_NAME |  | 1.This field is not null. Data type: Character. | R
ESG | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | SubSync | SUBSYNC.View | Automatic | SUBSYNC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C
ESG | SUBSYNCHRONOUS RESONANCE |  |  |  | SubSync |  |  | Not in table | Not in table |  | 2.All letters should be capital
ESG | Mass # | Correction 02/28/2012 | Update 02/2012 | SubSync | SubSync |  | List | SUBSYNC | MASS_NUMBER |  | 3. Should not allow spaces
ESG | Mass Name | Change | ADD 04/2012 |  | SubSync | SUBSYNC.View |  | SUBSYNC | NAME |  | 4. Can not exceed 13 characters for split gen resources
ESG | Mass Code | Corrected | ADD 04/2012 |  | SubSync | SUBSYNC.View | Automatic | SUBSYNC | MASS |  | CONCATENATE Unit_CODE_MASS
ESG | Mass Inertia |  | ADD 04/2012 |  | SubSync | SUBSYNC.View |  | SUBSYNC | MASS_INERTIA
ESG | Inertia units |  | ADD 04/2012 |  | SubSync | SUBSYNC.View |  | SUBSYNC | INERTIA_UNITS
ESG | Associated damping |  | ADD 04/2012 |  | SubSync | SUBSYNC.View |  | SUBSYNC | ASST_DMPG
ESG | Damping units |  | ADD 04/2012 |  | SubSync | SUBSYNC.View |  | SUBSYNC | DMPG_UNITS
ESG | Stiffness Between Masses Previous And Current Mass |  | ADD 04/2012 |  | SubSync | SUBSYNC.View |  | SUBSYNC | STFNS_BTWN_MASSES
ESG | Stiffness units |  | ADD 04/2012 |  | SubSync | SUBSYNC.View |  | SUBSYNC | STFNS_UNITS
Solar | Parameters - Solar |  |  |  | Parameters - Solar |  |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type Selected is 'GEN' where GEN is non-CC non-wind Generation Resources. | C | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,MMS,NMMS
Solar | Generator Details |  |  |  | Parameters - Solar |  |  | Not in table | Not in table
Solar | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | List | SOLAR | UNIT_NAME | 1. Not Null. 2. Must not exceed 4 characters for Jointly Owned Units 3. Maximum of 8 character allowed | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Solar | Resource Name (Unit Code/Mnemonic) | 04/23/2012 Updated Table to DERATING_SOLAR | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | Automatic | SOLAR & DERATING_SOLAR | UNIT_CODE | 1. Not Null. 2. Enter Site Code and Unit Name for this field (Sitecode_Unit Name) 3. All letters must be capital | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Solar | Reasonability Limits |  |  |  | Parameters - Solar |  |  | Not in table | Not in table
Solar | High Reasonability Limit |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | HR_LMT | 1. High Reasonability Limit >0 2. HighReasonabilityLimit >= LowReasonablityLimit 3. Not Null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit | R | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Solar | Low Reasonability Limit |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | LR_LMT | 1. Low Reasonability Limit >0 for Non PUN sites 2. Low ReasonabilityLimit <= High ReasonablityLimit 3. PUN (Private Use Network) Sites LRL should equal zero or produce a Warning 4. Not Null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Solar | High Reasonability Ramp Rate Limit |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW/min | SOLAR | HR_RAMPRATE_LMT | 1. High Reasonability Ramp Rate Limit >= Low Reasonability Ramp Rate Limit. 2. Not null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS
Solar | Low Reasonability Ramp Rate Limit |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW/min | SOLAR | LR_RAMP_RATE_LMT | 1. Low Reasonability Ramp Rate Limit >=0. 2. Not null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS
Solar | Seasonal Ratings Spring |  |  |  | Parameters - Solar |  |  | Not in table | Not in table
Solar | Seasonal Net Max Sustainable Rating - Spring |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MAX_SUST_RTG_SP | 1.Seasonal Net Max Sustainable Rating - Spring >= Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Spring > Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Lin Xu/Weihui | MMS,NMMS
Solar | Seasonal Net Min Sustainable Rating - Spring |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MIN_SUST_RTG_SP | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS,NMMS
Solar | Seasonal Net Max Emergency Rating - Spring |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MAX_EMGY_RTG_SP | 1.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Lin Xu/Weihui | MMS,NMMS
Solar | Seasonal Net Min Emergency Rating - Spring |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MIN_EMGY_RTG_SP | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit 2. Not Null | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS,NMMS
Solar | Seasonal Ratings Summer |  |  |  | Parameters - Solar |  |  | Not in table | Not in table
Solar | Seasonal Net Max Sustainable Rating - Summer |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MAX_SUST_RTG_SM | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Summer > Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | Seasonal Net Min Sustainable Rating - Summer |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MIN_SUST_RTG_SM | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit | R | Lin Xu | MMS
Solar | Seasonal Net Max Emergency Rating - Summer |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MAX_EMGY_RTG_SM | 1.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Summer > Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | Seasonal Net Min Emergency Rating - Summer |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MIN_EMGY_RTG_SM | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | Seasonal Ratings Fall |  |  |  | Parameters - Solar |  |  | Not in table | Not in table
Solar | Seasonal Net Max Sustainable Rating - Fall |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MAX_SUST_RTG_FL | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | Seasonal Net Min Sustainable Rating - Fall |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MIN_SUST_RTG_FL | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall. >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | Seasonal Net Max Emergency Rating - Fall |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MAX_EMGY_RTG_FL | 1.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Fall > Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | Seasonal Net Min Emergency Rating - Fall |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MIN_EMGY_RTG_FL | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | Seasonal Ratings Winter |  |  |  | Parameters - Solar |  |  | Not in table | Not in table
Solar | Seasonal Net Max Sustainable Rating - Winter |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MAX_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | Seasonal Net Min Sustainable Rating - Winter |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MIN_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | Seasonal Net Max Emergency Rating - Winter |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MAX_EMGY_RTG_WT | 1.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Winter > Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | Seasonal Net Min Emergency Rating - Winter |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MIN_EMGY_RTG_WT | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES |  |  |  | Parameters - Solar |  |  | Not in table | Not in table
Solar | 0°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 5°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 10°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 15°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Solar | 20°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 25°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 30°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 35°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 40°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 45°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 50°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 55°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 60°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 65°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 70°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 75°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 80°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 85°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 90°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 95°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 100°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 105°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 110°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 115°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 120°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | Parameters - ESG Injections |  |  |  | Parameters - ESG Injections |  |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type Selected is 'GEN' where GEN is non-CC non-wind Generation Resources. | C | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,MMS,NMMS
ESG | Generator Details |  |  |  | Parameters - ESG Injections |  |  | Not in table | Not in table
ESG | Unit Name | 03/09/2012 Correct DB Field | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | List | ESGUNIT | UNIT_NAME | 1. Not Null. 2. Must not exceed 4 characters for Jointly Owned Units 3. Maximum of 8 character allowed | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
ESG | Resource Name (Unit Code/Mnemonic) | 04/23/2012 Updated Table to DERATING_ESG | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | Automatic | ESGUNIT & DERATING_ESG | UNIT_CODE_INJ | 1. Not Null. 2. Enter Site Code and Unit Name for this field (Sitecode_Unit Name) 3. All letters must be capital | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
ESG | ESG Parameter Type |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | Automatic | ESGUNIT | ESG_TYPE |  | Required Injection/Withdrawing | R
ESG | Reasonability Limits |  |  |  | Parameters - ESG Injections |  |  | Not in table | Not in table
ESG | High Reasonability Limit |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | ESGUNIT | HR_LMT | 1. High Reasonability Limit >0 2. HighReasonabilityLimit >= LowReasonablityLimit 3. Not Null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit | R | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
ESG | Low Reasonability Limit |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | ESGUNIT | LR_LMT | 1. Low Reasonability Limit >0 for Non PUN sites 2. Low ReasonabilityLimit <= High ReasonablityLimit 3. PUN (Private Use Network) Sites LRL should equal zero or produce a Warning 4. Not Null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
ESG | High Reasonability Ramp Rate Limit |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW/min | ESGUNIT | HR_RAMPRATE_LMT | 1. High Reasonability Ramp Rate Limit >= Low Reasonability Ramp Rate Limit. 2. Not null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS
ESG | Low Reasonability Ramp Rate Limit |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW/min | ESGUNIT | LR_RAMP_RATE_LMT | 1. Low Reasonability Ramp Rate Limit >=0. 2. Not null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS
ESG | Seasonal Ratings Spring |  |  |  | Parameters - ESG Injections |  |  | Not in table | Not in table
ESG | Seasonal Net Max Sustainable Rating - Spring |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | ESGUNIT | SEASON_NET_MAX_SUST_RTG_SP | 1.Seasonal Net Max Sustainable Rating - Spring >= Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Spring > Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Lin Xu/Weihui | MMS,NMMS
ESG | Seasonal Net Min Sustainable Rating - Spring |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | ESGUNIT | SEASON_NET_MIN_SUST_RTG_SP | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS,NMMS
ESG | Seasonal Net Max Emergency Rating - Spring |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | ESGUNIT | SEASON_NET_MAX_EMGY_RTG_SP | 1.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Lin Xu/Weihui | MMS,NMMS
ESG | Seasonal Net Min Emergency Rating - Spring |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | ESGUNIT | SEASON_NET_MIN_EMGY_RTG_SP | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit 2. Not Null | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS,NMMS
ESG | Seasonal Ratings Summer |  |  |  | Parameters - ESG Injections |  |  | Not in table | Not in table
ESG | Seasonal Net Max Sustainable Rating - Summer |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | ESGUNIT | SEASON_NET_MAX_SUST_RTG_SM | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Summer > Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | Seasonal Net Min Sustainable Rating - Summer |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | ESGUNIT | SEASON_NET_MIN_SUST_RTG_SM | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit | R | Lin Xu | MMS
ESG | Seasonal Net Max Emergency Rating - Summer |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | ESGUNIT | SEASON_NET_MAX_EMGY_RTG_SM | 1.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Summer > Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | Seasonal Net Min Emergency Rating - Summer |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | ESGUNIT | SEASON_NET_MIN_EMGY_RTG_SM | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | Seasonal Ratings Fall |  |  |  | Parameters - ESG Injections |  |  | Not in table | Not in table
ESG | Seasonal Net Max Sustainable Rating - Fall |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | ESGUNIT | SEASON_NET_MAX_SUST_RTG_FL | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | Seasonal Net Min Sustainable Rating - Fall |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | ESGUNIT | SEASON_NET_MIN_SUST_RTG_FL | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall. >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | Seasonal Net Max Emergency Rating - Fall |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | ESGUNIT | SEASON_NET_MAX_EMGY_RTG_FL | 1.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Fall > Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | Seasonal Net Min Emergency Rating - Fall |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | ESGUNIT | SEASON_NET_MIN_EMGY_RTG_FL | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | Seasonal Ratings Winter |  |  |  | Parameters - ESG Injections |  |  | Not in table | Not in table
ESG | Seasonal Net Max Sustainable Rating - Winter |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | ESGUNIT | SEASON_NET_MAX_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | Seasonal Net Min Sustainable Rating - Winter |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | ESGUNIT | SEASON_NET_MIN_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | Seasonal Net Max Emergency Rating - Winter |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | ESGUNIT | SEASON_NET_MAX_EMGY_RTG_WT | 1.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Winter > Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | Seasonal Net Min Emergency Rating - Winter |  | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | ESGUNIT | SEASON_NET_MIN_EMGY_RTG_WT | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES |  |  |  | Parameters - ESG Injections |  |  | Not in table | Not in table
ESG | 0°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 5°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 10°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 15°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
ESG | 20°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 25°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 30°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 35°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 40°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 45°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 50°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 55°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 60°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 65°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 70°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 75°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 80°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 85°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 90°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 95°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 100°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 105°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 110°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 115°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 120°f | 04/23/2012 Updated Table to DERATING_ESG 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - ESG Injections | Parameters_ESG_Injections.View | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | Parameters - ESG Withdrawing |  |  |  | Parameters - ESG Withdrawing |  |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type Selected is 'GEN' where GEN is non-CC non-wind Generation Resources. | C | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,MMS,NMMS
ESG | Generator Details |  |  |  | Parameters - ESG Withdrawing |  |  | Not in table | Not in table
ESG | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | List | ESGUNIT | UNIT_NAME | 1. Not Null. 2. Must not exceed 4 characters for Jointly Owned Units 3. Maximum of 8 character allowed | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
ESG | Dispatch Asset Code (Provided by ERCOT) | 04/03/2012 Added to data validation and mapping document already existed in RARF Form | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | List | ESGUNIT | DISPATCH_ASSET_CODE |  |  | R | RARF Glossary Version 4.0 /RARF Guide version 4.0
ESG | Resource Name (Unit Code/Mnemonic) | 04/23/2012 Updated Table to DERATING_ESG | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | Automatic | ESGUNIT & DERATING_ESG | UNIT_CODE | 1. Not Null. 2. Enter Site Code and Unit Name for this field (Sitecode_Unit Name) 3. All letters must be capital | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
ESG | ESG Parameter Type |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | Automatic | ESGUNIT | ESG_TYPE |  | Required Injection/Withdrawing
ESG | Reasonability Limits |  |  |  | Parameters - ESG Withdrawing |  |  | Not in table | Not in table
ESG | High Reasonability Limit |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW | ESGUNIT | HR_LMT | 1. High Reasonability Limit >0 2. HighReasonabilityLimit >= LowReasonablityLimit 3. Not Null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit | R | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
ESG | Low Reasonability Limit |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW | ESGUNIT | LR_LMT | 1. Low Reasonability Limit >0 for Non PUN sites 2. Low ReasonabilityLimit <= High ReasonablityLimit 3. PUN (Private Use Network) Sites LRL should equal zero or produce a Warning 4. Not Null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
ESG | High Reasonability Ramp Rate Limit |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW/min | ESGUNIT | HR_RAMPRATE_LMT | 1. High Reasonability Ramp Rate Limit >= Low Reasonability Ramp Rate Limit. 2. Not null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS
ESG | Storage High Reasonability Ramp Rate Limit |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW/min | ESGUNIT | CHG_EFF_COEFF_PER_ENG_LOST_DUR_CHARG
ESG | Low Reasonability Ramp Rate Limit |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW/min | ESGUNIT | LR_RAMP_RATE_LMT | 1. Low Reasonability Ramp Rate Limit >=0. 2. Not null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS
ESG | StorageLow Reasonability Ramp Rate Limit |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW | ESGUNIT | STRG_LR_RAMP_RATE_LMT
ESG | Seasonal Ratings Spring |  |  |  | Parameters - ESG Withdrawing |  |  | Not in table | Not in table
ESG | Seasonal Net Max Sustainable Rating - Spring |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW | ESGUNIT | SEASON_NET_MAX_SUST_RTG_SP | 1.Seasonal Net Max Sustainable Rating - Spring >= Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Spring > Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Lin Xu/Weihui | MMS,NMMS
ESG | Seasonal Net Min Sustainable Rating - Spring |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW | ESGUNIT | SEASON_NET_MIN_SUST_RTG_SP | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS,NMMS
ESG | Seasonal Net Max Emergency Rating - Spring |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW | ESGUNIT | SEASON_NET_MAX_EMGY_RTG_SP | 1.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Lin Xu/Weihui | MMS,NMMS
ESG | Seasonal Net Min Emergency Rating - Spring |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW | ESGUNIT | SEASON_NET_MIN_EMGY_RTG_SP | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit 2. Not Null | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS,NMMS
ESG | Seasonal Ratings Summer |  |  |  | Parameters - ESG Withdrawing |  |  | Not in table | Not in table
ESG | Seasonal Net Max Sustainable Rating - Summer |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW | ESGUNIT | SEASON_NET_MAX_SUST_RTG_SM | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Summer > Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | Seasonal Net Min Sustainable Rating - Summer |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW | ESGUNIT | SEASON_NET_MIN_SUST_RTG_SM | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit | R | Lin Xu | MMS
ESG | Seasonal Net Max Emergency Rating - Summer |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW | ESGUNIT | SEASON_NET_MAX_EMGY_RTG_SM | 1.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Summer > Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | Seasonal Net Min Emergency Rating - Summer |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW | ESGUNIT | SEASON_NET_MIN_EMGY_RTG_SM | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | Seasonal Ratings Fall |  |  |  | Parameters - ESG Withdrawing |  |  | Not in table | Not in table
ESG | Seasonal Net Max Sustainable Rating - Fall |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW | ESGUNIT | SEASON_NET_MAX_SUST_RTG_FL | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | Seasonal Net Min Sustainable Rating - Fall |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW | ESGUNIT | SEASON_NET_MIN_SUST_RTG_FL | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall. >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | Seasonal Net Max Emergency Rating - Fall |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW | ESGUNIT | SEASON_NET_MAX_EMGY_RTG_FL | 1.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Fall > Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | Seasonal Net Min Emergency Rating - Fall |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW | ESGUNIT | SEASON_NET_MIN_EMGY_RTG_FL | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | Seasonal Ratings Winter |  |  |  | Parameters - ESG Withdrawing |  |  | Not in table | Not in table
ESG | Seasonal Net Max Sustainable Rating - Winter |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW | ESGUNIT | SEASON_NET_MAX_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | Seasonal Net Min Sustainable Rating - Winter |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW | ESGUNIT | SEASON_NET_MIN_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | Seasonal Net Max Emergency Rating - Winter |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW | ESGUNIT | SEASON_NET_MAX_EMGY_RTG_WT | 1.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Winter > Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | Seasonal Net Min Emergency Rating - Winter |  | ADD 04/2012 |  | Parameters - ESG Withdrawing | Parameters_ESG_Withdrawing.View | MW | ESGUNIT | SEASON_NET_MIN_EMGY_RTG_WT | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS
ESG | UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES |  |  |  | Parameters - ESG Withdrawing |  |  | Not in table | Not in table
ESG | 0°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 5°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 10°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 15°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
ESG | 20°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 25°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 30°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 35°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 40°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 45°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 50°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 55°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 60°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 65°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 70°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 75°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 80°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 85°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 90°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 95°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 100°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 105°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 110°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 115°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
ESG | 120°f | 04/23/2012 Updated Table to DERATING_ESG 04/04/2012 Not in Spreadsheet so remove from validation | ADD 04/2012 |  | Parameters - ESG Withdrawing | N/A field was removed from Form | MW | DERATING_ESG | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | Operational Parameters - Solar |  |  |  | Operational Parameters - Solar |  |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Resource Type Selected is 'WIND units' | C | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | MMS,NMMS
Solar | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View |  | SOLAR | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Solar | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View |  | SOLAR | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
Solar | RESOURCE PARAMETERS |  |  |  | Operational Parameters - Solar |  |  | Not in table | Not in table
Solar | Minimum On Line Time | Check | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View | hours | SOLAR | MIN_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum On Line Time >= 0 | R | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Solar | Minimum Off Line Time | Check | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View | hours | SOLAR | MIN_OFFLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum Off Line Time >= 0 | R | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Solar | Hot Start Time | Corrected | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View | hours | SOLAR | HOTSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot Start Time >= 0 3. Hot Start Time <= Intermediate Start Time | O | Angela Moy/Jamil Daouk | NMMS
Solar | Intermediate Start Time | Corrected | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View | hours | SOLAR | INTERMSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate Start Time >= 0 3. Cold Start Time >= Intermediate Start Time >= Hot Start Time | O | Angela Moy/Jamil Daouk | NMMS
Solar | Cold Start Time | Corrected | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View | hours | SOLAR | COLDSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Cold Start Time >= 0 3. Cold Start Time >= Intermediate Start Time | O | Angela Moy/Jamil Daouk | NMMS
Solar | Max Weekly Starts | Check | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View |  | SOLAR | MAXWKLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Lin Xu/Jamil Daouk | MMS,NMMS
Solar | Max On Line Time | Corrected | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View | hours | SOLAR | MAX_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Lin Xu/Jamil Daouk | MMS,NMMS
Solar | Max Daily Starts | Check | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View |  | SOLAR | MAXDLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Daily Start >= 0 3. Max Daily Start <= 999 | R | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Solar | Max Weekly Energy | Corrected | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View | MWh | SOLAR | MAXWKLYENRGY |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Energy >= 0 3. Max Weekly Energy < 1e10 | R | Lin Xu | MMS,NMMS
Solar | Hot-to-Intermediate Time | Check | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View | hours | SOLAR | HOT_TO_INTMDT_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot-to-Intermediate Time >= 0 | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
Solar | Intermediate-to-Cold Time | Check | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View | hours | SOLAR | INTMDT_TO_COLD_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate-to-Cold Time >= 0 | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
Solar | Operational Parameters - Solar - NRRC |  |  | Operational Parameters - Solar - NRRC | Operational Parameters - Solar - NRRC |  |  | Not in table | Not in table
Solar | Generator Details |  |  | Operational Parameters - Solar - NRRC | Operational Parameters - Solar - NRRC |  |  | Not in table | Not in table
Solar | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 | Operational Parameters - Solar - NRRC | Operational Parameters - Solar - NRRC | NRRC_SOLAR.View | List | SOLAR | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Solar | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 | Operational Parameters - Solar - NRRC | Operational Parameters - Solar - NRRC | NRRC_SOLAR.View | List | RAMP_RATES_NRRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Solar | Normal Ramp Rate Curve |  |  |  | Operational Parameters - Solar - NRRC |  |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit.
Solar | MW Number |  |  |  | Operational Parameters - Solar - NRRC
Solar | NRRC Code |  | ADD 04/2012 | Operational Parameters - Solar - NRRC | Operational Parameters - Solar - NRRC | NRRC_SOLAR.View |  | RAMP_RATES_NRRC | UNIT_MW_NRRC |  | This Field is Not in the RARF: Capture Unit Code and MW Number and prepopulate this field with UNIT_CODE_MW_NUMBER_NRRC. | R
Solar | NRRC MW | PHASE II Updated 03/06/2012 Added Step 5 and 6 | ADD 04/2012 |  | Operational Parameters - Solar - NRRC | NRRC_SOLAR.View | MW | RAMP_RATES_NRRC | MW_NUMBER_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk | NMMS
Solar | Upward Ramprate | Check | ADD 04/2012 |  | Operational Parameters - Solar - NRRC | NRRC_SOLAR.View | MW/min | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Lin Xu/Kittipong | MMS,NMMS
Solar | Downward Ramprate | Check | ADD 04/2012 |  | Operational Parameters - Solar - NRRC | NRRC_SOLAR.View | MW/min | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Lin Xu/Kittipong | MMS,NMMS
Solar | Operational Parameters - Solar - ERRC |  |  |  | Operational Parameters - Solar- ERRC |  |  | Not in table | Not in table
Solar | Generator Details |  |  |  | Operational Parameters - Solar- ERRC |  |  | Not in table | Not in table
Solar | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 | Operational Parameters - Solar- ERRC | Operational Parameters - Solar- ERRC | ERRC_SOLAR.View | List | SOLAR | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Solar | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 | Operational Parameters - Solar- ERRC | Operational Parameters - Solar- ERRC | ERRC_SOLAR.View | List | RAMP_RATES_ERRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Solar | Emergency Ramp Rate Curve |  |  |  | Operational Parameters - Solar- ERRC |  |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit.
Solar | ERRC MW | PHASE II Updated 03/06/2012 Added Step 5 and 6 |  |  | Operational Parameters - Solar- ERRC |  | MW | RAMP_RATES_ERRC | MW_NUMBER_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk | NMMS
Solar | MW Number |  | ADD 04/2012 | Operational Parameters - Solar- ERRC | Operational Parameters - Solar- ERRC | ERRC_SOLAR.View
Solar | ERRC Code |  | ADD 04/2012 | Operational Parameters - Solar- ERRC | Operational Parameters - Solar- ERRC | ERRC_SOLAR.View |  | RAMP_RATES_ERRC | UNIT_MW_ERRC |  | Capture Unit Code and MW Number and prepopulate this field with Unit Name_MW_NUMBER_ERRC. | R
Solar | Upward Ramprate | Check | ADD 04/2012 |  | Operational Parameters - Solar- ERRC | ERRC_SOLAR.View | MW/min | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Lin Xu/Kittipong | MMS,NMMS
Solar | Downward Ramprate | Check | ADD 04/2012 |  | Operational Parameters - Solar- ERRC | ERRC_SOLAR.View | MW/min | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Lin Xu/Kittipong | MMS,NMMS
ESG | Oper Parameters - ESG Injections |  |  |  | Oper Parameters - ESG Injections |  |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Resource Type Selected is 'Solar units' | C | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | MMS,NMMS
ESG | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | Oper Parameters - ESG Injections | Opr_Parameters_ESG_Injections.View | List | ESGUNIT | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
ESG | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | Oper Parameters - ESG Injections | Opr_Parameters_ESG_Injections.View | Automatic | ESGUNIT | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
ESG | ESG Parameter Type |  | ADD 04/2012 |  | Oper Parameters - ESG Injections | Opr_Parameters_ESG_Injections.View | Automatic | ESGUNIT | ESG_TYPE |  | Required Injection/Withdrawing
ESG | RESOURCE PARAMETERS |  |  |  | Oper Parameters - ESG Injections |  |  | Not in table | Not in table
ESG | Minimum On Line Time | Check | ADD 04/2012 |  | Oper Parameters - ESG Injections | Opr_Parameters_ESG_Injections.View | hours | ESGUNIT | MIN_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum On Line Time >= 0 | R | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
ESG | Minimum Off Line Time | Check | ADD 04/2012 |  | Oper Parameters - ESG Injections | Opr_Parameters_ESG_Injections.View | hours | ESGUNIT | MIN_OFFLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum Off Line Time >= 0 | R | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
ESG | Hot Start Time | Corrected | ADD 04/2012 |  | Oper Parameters - ESG Injections | Opr_Parameters_ESG_Injections.View | hours | ESGUNIT | HOTSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot Start Time >= 0 3. Hot Start Time <= Intermediate Start Time | O | Angela Moy/Jamil Daouk | NMMS
ESG | Intermediate Start Time | Corrected | ADD 04/2012 |  | Oper Parameters - ESG Injections | Opr_Parameters_ESG_Injections.View | hours | ESGUNIT | INTERMSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate Start Time >= 0 3. Cold Start Time >= Intermediate Start Time >= Hot Start Time | O | Angela Moy/Jamil Daouk | NMMS
ESG | Cold Start Time | Corrected | ADD 04/2012 |  | Oper Parameters - ESG Injections | Opr_Parameters_ESG_Injections.View | hours | ESGUNIT | COLDSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Cold Start Time >= 0 3. Cold Start Time >= Intermediate Start Time | O | Angela Moy/Jamil Daouk | NMMS
ESG | Max Weekly Starts | Check | ADD 04/2012 |  | Oper Parameters - ESG Injections | Opr_Parameters_ESG_Injections.View |  | ESGUNIT | MAXWKLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Lin Xu/Jamil Daouk | MMS,NMMS
ESG | Max On Line Time | Corrected | ADD 04/2012 |  | Oper Parameters - ESG Injections | Opr_Parameters_ESG_Injections.View | hours | ESGUNIT | MAX_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Lin Xu/Jamil Daouk | MMS,NMMS
ESG | Max Daily Starts | Check | ADD 04/2012 |  | Oper Parameters - ESG Injections | Opr_Parameters_ESG_Injections.View |  | ESGUNIT | MAXDLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Daily Start >= 0 3. Max Daily Start <= 999 | R | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
ESG | Max Weekly Energy | Corrected | ADD 04/2012 |  | Oper Parameters - ESG Injections | Opr_Parameters_ESG_Injections.View | MWh | ESGUNIT | MAXWKLYENRGY |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Energy >= 0 3. Max Weekly Energy < 1e10 | R | Lin Xu | MMS,NMMS
ESG | Hot-to-Intermediate Time | Check | ADD 04/2012 |  | Oper Parameters - ESG Injections | Opr_Parameters_ESG_Injections.View | hours | ESGUNIT | HOT_TO_INTMDT_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot-to-Intermediate Time >= 0 | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
ESG | Intermediate-to-Cold Time | Check | ADD 04/2012 |  | Oper Parameters - ESG Injections | Opr_Parameters_ESG_Injections.View | hours | ESGUNIT | INTMDT_TO_COLD_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate-to-Cold Time >= 0 | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
ESG | Operational Parameters - ESG Injections -NRRC |  |  |  | Oper Parameters - ESG Injections -NRRC |  |  | Not in table | Not in table
ESG | Generator Details |  |  |  | Oper Parameters - ESG Injections -NRRC |  |  | Not in table | Not in table
ESG | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 | Oper Parameters - ESG Injections -NRRC | Oper Parameters - ESG Injections -NRRC | NRRC_ESG_Injection.View | List | RAMP_RATES_NRRC | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
ESG | Dispatch Asset Code (Provided by ERCOT) | 04/03/2012 Field Shold be removed, is not at Dispatch Asset code for Injections | ADD 04/2012 |  | Oper Parameters - ESG Injections -NRRC | N/A field was removed from Form | List | RAMP_RATES_NRRC | DISPATCH_ASSET_CODE |  |  | R | RARF Glossary Version 4.0 /RARF Guide version 4.0
ESG | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 | Oper Parameters - ESG Injections -NRRC | Oper Parameters - ESG Injections -NRRC | NRRC_ESG_Injection.View | Automatic | RAMP_RATES_NRRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
ESG | ESG Parameter Type |  | ADD 04/2012 |  | Oper Parameters - ESG Injections -NRRC | NRRC_ESG_Injection.View | Automatic | RAMP_RATES_NRRC | ESG_TYPE |  | Required Injection/Withdrawing
ESG | Normal Ramp Rate Curve |  |  |  | Oper Parameters - ESG Injections -NRRC |  |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit.
ESG | MW Number |  |  |  | Oper Parameters - ESG Injections -NRRC
ESG | NRRC Code |  | ADD 04/2012 | Oper Parameters - ESG Injections -NRRC | Oper Parameters - ESG Injections -NRRC | NRRC_ESG_Injection.View |  | RAMP_RATES_NRRC | UNIT_MW_NRRC |  | Capture Unit Code and MW Number and prepopulate this field with Unit Name_MW_NUMBER_ERRC. | R
ESG | NRRC MW | PHASE II Updated 03/06/2012 Added Step 5 and 6 | ADD 04/2012 |  | Oper Parameters - ESG Injections -NRRC | NRRC_ESG_Injection.View | MW | RAMP_RATES_NRRC | MW_NUMBER_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk | NMMS
ESG | Upward Ramprate | Check | ADD 04/2012 |  | Oper Parameters - ESG Injections -NRRC | NRRC_ESG_Injection.View | MW/min | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Lin Xu/Kittipong | MMS,NMMS
ESG | Downward Ramprate | Check | ADD 04/2012 |  | Oper Parameters - ESG Injections -NRRC | NRRC_ESG_Injection.View | MW/min | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Lin Xu/Kittipong | MMS,NMMS
ESG | Oper Parameters - ESG Injections - ERRC |  |  |  | Oper Parameters - ESG Injections -ERRC |  |  | Not in table | Not in table
ESG | Generator Details |  |  |  | Oper Parameters - ESG Injections -ERRC |  |  | Not in table | Not in table
ESG | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 | Oper Parameters - ESG Injections -ERRC | Oper Parameters - ESG Injections -ERRC | ERRC_ESG_Injection.View | List | RAMP_RATES_ERRC | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
ESG | Dispatch Asset Code (Provided by ERCOT) | 04/03/2012 Field Shold be removed, is not at Dispatch Asset code for Injections | ADD 04/2012 |  | Oper Parameters - ESG Injections -ERRC | N/A field was removed from Form | List | RAMP_RATES_ERRC | DISPATCH_ASSET_CODE |  |  | R | RARF Glossary Version 4.0 /RARF Guide version 4.0
ESG | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 | Oper Parameters - ESG Injections -ERRC | Oper Parameters - ESG Injections -ERRC | ERRC_ESG_Injection.View | Automatic | RAMP_RATES_ERRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
ESG | ESG Parameter Type |  | ADD 04/2012 |  | Oper Parameters - ESG Injections -ERRC | ERRC_ESG_Injection.View | Automatic | RAMP_RATES_ERRC | ESG_TYPE |  | Required Injection/Withdrawing
ESG | Emergency Ramp Rate Curve |  |  |  | Oper Parameters - ESG Injections -ERRC |  |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit.
ESG | MW Number |  |  |  | Oper Parameters - ESG Injections -ERRC
ESG | ERRC Code |  | ADD 04/2012 | Oper Parameters - ESG Injections -ERRC | Oper Parameters - ESG Injections -ERRC | ERRC_ESG_Injection.View |  | RAMP_RATES_ERRC | UNIT_MW_ERRC |  | Capture Unit Code and MW Number and prepopulate this field with Unit Name_MW_NUMBER_ERRC. | R
ESG | ERRC MW | PHASE II Updated 03/06/2012 Added Step 5 and 6 | ADD 04/2012 |  | Oper Parameters - ESG Injections -ERRC | ERRC_ESG_Injection.View | MW | RAMP_RATES_ERRC | MW_NUMBER_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk | NMMS
ESG | Upward Ramprate | Check | ADD 04/2012 |  | Oper Parameters - ESG Injections -ERRC | ERRC_ESG_Injection.View | MW/min | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Lin Xu/Kittipong | MMS,NMMS
ESG | Downward Ramprate | Check | ADD 04/2012 |  | Oper Parameters - ESG Injections -ERRC | ERRC_ESG_Injection.View | MW/min | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Lin Xu/Kittipong | MMS,NMMS
ESG | Oper Parameters - ESG Withdrawing |  |  |  | Oper Parameters - ESG Withdrawing |  |  | Not in table | Not in table |  |  | C | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | MMS,NMMS
ESG | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing | Opr_Parameters_ESG_Withdrawing.View |  | ESGUNIT | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
ESG | Dispatch Asset Code (Provided by ERCOT) | 04/03/2012 Added to data validation and mapping document already existed in RARF Form | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing | Opr_Parameters_ESG_Withdrawing.View | List | ESGUNIT | DISPATCH_ASSET_CODE |  |  | R | RARF Glossary Version 4.0 /RARF Guide version 4.0
ESG | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing | Opr_Parameters_ESG_Withdrawing.View |  | ESGUNIT | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
ESG | ESG Parameter Type |  | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing | Opr_Parameters_ESG_Withdrawing.View | Automatic | ESGUNIT | ESG_TYPE |  | Required Injection/Withdrawing
ESG | RESOURCE PARAMETERS |  |  |  | Oper Parameters - ESG Withdrawing |  |  | Not in table | Not in table
ESG | Minimum On Line Time | Check | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing | Opr_Parameters_ESG_Withdrawing.View | hours | ESGUNIT | MIN_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum On Line Time >= 0 | R | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
ESG | Minimum Off Line Time | Check | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing | Opr_Parameters_ESG_Withdrawing.View | hours | ESGUNIT | MIN_OFFLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum Off Line Time >= 0 | R | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
ESG | Hot Start Time | Corrected | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing | Opr_Parameters_ESG_Withdrawing.View | hours | ESGUNIT | HOTSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot Start Time >= 0 3. Hot Start Time <= Intermediate Start Time | O | Angela Moy/Jamil Daouk | NMMS
ESG | Intermediate Start Time | Corrected | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing | Opr_Parameters_ESG_Withdrawing.View | hours | ESGUNIT | INTERMSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate Start Time >= 0 3. Cold Start Time >= Intermediate Start Time >= Hot Start Time | O | Angela Moy/Jamil Daouk | NMMS
ESG | Cold Start Time | Corrected | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing | Opr_Parameters_ESG_Withdrawing.View | hours | ESGUNIT | COLDSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Cold Start Time >= 0 3. Cold Start Time >= Intermediate Start Time | O | Angela Moy/Jamil Daouk | NMMS
ESG | Max Weekly Starts | Check | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing | Opr_Parameters_ESG_Withdrawing.View |  | ESGUNIT | MAXWKLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Lin Xu/Jamil Daouk | MMS,NMMS
ESG | Max On Line Time | Corrected | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing | Opr_Parameters_ESG_Withdrawing.View | hours | ESGUNIT | MAX_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Lin Xu/Jamil Daouk | MMS,NMMS
ESG | Max Daily Starts | Check | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing | Opr_Parameters_ESG_Withdrawing.View |  | ESGUNIT | MAXDLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Daily Start >= 0 3. Max Daily Start <= 999 | R | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
ESG | Max Weekly Energy | Corrected | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing | Opr_Parameters_ESG_Withdrawing.View | MWh | ESGUNIT | MAXWKLYENRGY |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Energy >= 0 3. Max Weekly Energy < 1e10 | R | Lin Xu | MMS,NMMS
ESG | Hot-to-Intermediate Time | Check | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing | Opr_Parameters_ESG_Withdrawing.View | hours | ESGUNIT | HOT_TO_INTMDT_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot-to-Intermediate Time >= 0 | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
ESG | Intermediate-to-Cold Time | Check | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing | Opr_Parameters_ESG_Withdrawing.View | hours | ESGUNIT | INTMDT_TO_COLD_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate-to-Cold Time >= 0 | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
ESG | Oper Parameters - ESG Withdrawing - NRRC |  |  |  | Oper Parameters - ESG Withdrawing - NRRC |  |  | Not in table | Not in table |  |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | MMS,NMMS
ESG | Generator Details |  |  |  | Oper Parameters - ESG Withdrawing - NRRC |  |  | Not in table | Not in table
ESG | Unit Name | 04/03/2012 Updated Table | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing - NRRC | NRRC_ESG_Withdrawing.View | List | ESGUNIT | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
ESG | Dispatch Asset Code (Provided by ERCOT) | 04/04/2012 add to NRRC RAMP RATE Table | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing - NRRC | NRRC_ESG_Withdrawing.View | List | RAMP_RATES_NRRC | DISPATCH_ASSET_CODE |  |  | R | RARF Glossary Version 4.0 /RARF Guide version 4.0
ESG | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing - NRRC | Oper Parameters - ESG Withdrawing - NRRC | NRRC_ESG_Withdrawing.View | Automatic | RAMP_RATES_NRRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
ESG | ESG Parameter Type |  | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing - NRRC | NRRC_ESG_Withdrawing.View | Automatic | RAMP_RATES_NRRC | ESG_TYPE |  | Required Injection/Withdrawing
ESG | Normal Ramp Rate Curve |  |  |  | Oper Parameters - ESG Withdrawing - NRRC |  |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit.
ESG | MW Number |  |  |  | Oper Parameters - ESG Withdrawing - NRRC
ESG | NRRC Code |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing - NRRC | Oper Parameters - ESG Withdrawing - NRRC | NRRC_ESG_Withdrawing.View |  | RAMP_RATES_NRRC | UNIT_MW_NRRC |  | Capture Unit Code and MW Number and prepopulate this field with Unit Name_MW_NUMBER_ERRC. | R
ESG | NRRC MW | PHASE II Updated 03/06/2012 Added Step 5 and 6 | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing - NRRC | NRRC_ESG_Withdrawing.View | MW | RAMP_RATES_NRRC | MW_NUMBER_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk | NMMS
ESG | Upward Ramprate | Updated 03/09/2012 | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing - NRRC | NRRC_ESG_Withdrawing.View | MW/min | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Lin Xu/Kittipong | MMS,NMMS
ESG | Downward Ramprate | Updated 03/09/2012 | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing - NRRC | NRRC_ESG_Withdrawing.View | MW/min | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Lin Xu/Kittipong | MMS,NMMS
ESG | Oper Parameters - ESG Withdrawing - ERRC |  |  |  | Oper Parameters - ESG Withdrawing - ERRC |  |  | Not in table | Not in table |  |  |  | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | MMS,NMMS
ESG | Generator Details |  |  |  | Oper Parameters - ESG Withdrawing - ERRC |  |  | Not in table | Not in table
ESG | Unit Name | Added 04/03/2012 Updated Table | ADD 04/2012 | Oper Parameters - ESG Withdrawing - ERRC | Oper Parameters - ESG Withdrawing - ERRC | ERRC_ESG_Withdrawing.View | List | ESGUNIT | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
ESG | Dispatch Asset Code (Provided by ERCOT) | 04/04/2012 add to NRRC RAMP RATE Table | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing - ERRC | ERRC_ESG_Withdrawing.View | List | RAMP_RATES_ERRC | DISPATCH_ASSET_CODE |  |  | R | RARF Glossary Version 4.0 /RARF Guide version 4.0
ESG | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing - ERRC | Oper Parameters - ESG Withdrawing - ERRC | ERRC_ESG_Withdrawing.View | Automatic | RAMP_RATES_ERRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
ESG | ESG Parameter Type |  | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing - ERRC | ERRC_ESG_Withdrawing.View | Automatic | RAMP_RATES_ERRC | ESG_TYPE |  | Required Injection/Withdrawing
ESG | Emergency Ramp Rate Curve |  |  |  | Oper Parameters - ESG Withdrawing - ERRC |  |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit.
ESG | MW Number |  |  |  | Oper Parameters - ESG Withdrawing - ERRC
ESG | ERRC Code |  | ADD 04/2012 | Oper Parameters - ESG Withdrawing - ERRC | Oper Parameters - ESG Withdrawing - ERRC | ERRC_ESG_Withdrawing.View |  | RAMP_RATES_ERRC | UNIT_MW_ERRC |  | Capture Unit Code and MW Number and prepopulate this field with Unit Name_MW_NUMBER_ERRC. | R
ESG | ERRC MW | PHASE II Updated 03/06/2012 Added Step 5 and 6 | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing - ERRC | ERRC_ESG_Withdrawing.View | MW | RAMP_RATES_ERRC | MW_NUMBER_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk | NMMS
ESG | Upward Ramprate | Check | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing - ERRC | ERRC_ESG_Withdrawing.View | MW/min | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Lin Xu/Kittipong | MMS,NMMS
ESG | Downward Ramprate | Check | ADD 04/2012 |  | Oper Parameters - ESG Withdrawing - ERRC | ERRC_ESG_Withdrawing.View | MW/min | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Lin Xu/Kittipong | MMS,NMMS
Solar | Reactive Capability - Solar |  |  |  | Reactive Capability - Solar |  |  | Not in table | Not in table
Solar | GENERATOR DETAILS |  |  |  | Reactive Capability - Solar |  |  | Not in table | Not in table
Solar | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | List | REACT_CAP_SOLAR | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R
Solar | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | Automatic | REACT_CAP_SOLAR | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C
Solar | Module # | Added 03/26/2012 |  |  | Reactive Capability - Solar |  | List | REACT_CAP_SOLAR | MOD_NO |  | 1. This field is not null. Data type: Character. 2. .Select from the list: Module1, Module2, Module3, Module4, Module5 | R
Solar | Module_Code | Added 03/26/2012 Hidded column on form |  |  | Reactive Capability - Solar |  | Automatic | REACT_CAP_SOLAR | GROUP_CODE |  | 1. This field is not null. Data type: Character. 2. .Concatanate: UNIT_CODE_MODULE_CODE | R
Solar | REACTIVE CAPABILITY CURVES DETAILS |  |  |  | Reactive Capability - Solar |  |  | Not in table | Not in table
Solar | Reactive Capability Data Provided Below is Gross/Net Values? | 04/02/2012 - Updated RARF Field Name, DB Field and removed Net from Drop down List in data Validation | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | List | REACT_CAP_SOLAR | REACT_CAPB_DATA_GROSS_NET_VAL |  | Select from the list: GROSS
Solar | Reactive Capability Data Provided Below is from NDCRC Test Data? |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | Y/N | REACT_CAP_SOLAR | REACT_CAPB_NDCRC_TEST_DATA |  | Select from the list: Y or N
Solar | If Reactive Capability Data Provided Below Is From Ndcrc Test Data Then Enter The Date On Which The Test Was Performed. |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | mm/dd/yyyy | REACT_CAP_SOLAR | REACT_CAPB_NDCRC_TEST_DATA_DT |  | This field is optional. Format should be: MM/DD/YYYY
Solar | MW1 |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MW | REACT_CAP_SOLAR | MW1 |  | 1. MW1 >=0 .1 2. MW1<MW2. 3. X(1) <= WMN(Unit Minimal output) where X(1) represents MW1( Generate a Warning Only when Business Rule#2 fails) | R
Solar | Lagging MVAR limit associated with MW1 output |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MVAR | REACT_CAP_SOLAR | MVAR1LAG |  | 1. Lagging MVAR limit associated with MW1 output >=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R
Solar | Leading MVAR limit associated with MW1 output |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MVAR | REACT_CAP_SOLAR | MVAR1LEAD |  | 1. Leading MVAR limit associated with MW1 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R
Solar | MW2 |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MW | REACT_CAP_SOLAR | MW2 |  | 1. MW2>0 2. MW2<MW3 | R
Solar | Lagging MVAR limit associated with MW2 output |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MVAR | REACT_CAP_SOLAR | MVAR2LAG |  | 1.Lagging MVAR limit associated with MW2 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R
Solar | Leading MVAR limit associated with MW2 output |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MVAR | REACT_CAP_SOLAR | MVAR2LEAD |  | 1. Leading MVAR limit associated with MW2 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R
Solar | MW3 |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MW | REACT_CAP_SOLAR | MW3 |  | 1. MW3 >0 2. MW3<MW4 | R
Solar | Lagging MVAR limit associated with MW3 output |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MVAR | REACT_CAP_SOLAR | MVAR3LAG |  | 1. Lagging MVAR limit associated with MW3 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R
Solar | Leading MVAR limit associated with MW3 output |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MVAR | REACT_CAP_SOLAR | MVAR3LEAD |  | 1.Leading MVAR limit associated with MW3 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R
Solar | MW4 |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MW | REACT_CAP_SOLAR | MW4 |  | 1. MW4 >0 2. MW4<MW5 3. X(n) > = WMX (Unit Max output) where n is the last MW value in the curve. If the curve has 4 points, X(n) is X(4) [ Generate a Warning Only When Business Rule#2 Fails] | R
Solar | Lagging MVAR limit associated with MW4 output |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MVAR | REACT_CAP_SOLAR | MVAR4LAG |  | 1. Lagging MVAR limit associated with MW4 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R
Solar | Leading MVAR limit associated with MW4 output |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MVAR | REACT_CAP_SOLAR | MVAR4LEAD |  | 1.Leading MVAR limit associated with MW4 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R
Solar | MW5 - Unity Power Factor |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MW | REACT_CAP_SOLAR | MW5UNITYPF
Solar | If hydrogen cooled, indicate hydrogen pressure (psi) associated with your Reactive Curve submitted for ERCOT studies |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | PSI | GENERATION | HYDROCOOLED |  |  | O
Solar | Net Maximum Leading Operating Capability |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MVAR | REACT_CAP_SOLAR | NETMAXLEAD |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if < .3286(max capability in MW). | R
Solar | Net Maximum Lagging Operating Capability |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MVAR | REACT_CAP_SOLAR | NETMAXLAG |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if < .3286(max capability in MW). | R
Solar | Has the Manufacturer's Capability Curve submitted? |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | Y/N | REACT_CAP_SOLAR | MFR_CAP_CURVE
ESG | Reactive Capability -ESG |  | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View |  | Not in table | Not in table
ESG | GENERATOR DETAILS |  |  |  | Reactive Capability -ESG |  |  | Not in table | Not in table
ESG | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View | List | REACT_CAP_ESG | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R
ESG | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View | Automatic | REACT_CAP_ESG | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C
ESG | REACTIVE CAPABILITY CURVES DETAILS |  |  |  | Reactive Capability -ESG |  |  | Not in table | Not in table
ESG | Reactive Capability Data Provided Below is Gross/Net Values? | 04/02/2012 - Updated RARF Field Name, DB Field and removed Net from Drop down List in data Validation | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View | List | REACT_CAP_ESG | REACT_CAPB_DATA_GROSS_NET_VAL |  | Select from the list: GROSS
ESG | Reactive Capability Data Provided Below is from NDCRC Test Data? |  | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View | Y/N | REACT_CAP_ESG | REACT_CAPB_NDCRC_TEST_DATA
ESG | If Reactive Capability Data Provided Below Is From Ndcrc Test Data Then Enter The Date On Which The Test Was Performed. |  | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View | mm/dd/yyyy | REACT_CAP_ESG | REACT_CAPB_NDCRC_TEST_DATA_DT
ESG | MW1 |  | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View | MW | REACT_CAP_ESG | MW1 |  | 1. MW1 >=0 .1 2. MW1<MW2. 3. X(1) <= WMN(Unit Minimal output) where X(1) represents MW1( Generate a Warning Only when Business Rule#2 fails) | R
ESG | Lagging MVAR limit associated with MW1 output |  | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View | MVAR | REACT_CAP_ESG | MVAR1LAG |  | 1. Lagging MVAR limit associated with MW1 output >=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R
ESG | Leading MVAR limit associated with MW1 output |  | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View | MVAR | REACT_CAP_ESG | MVAR1LEAD |  | 1. Leading MVAR limit associated with MW1 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R
ESG | MW2 |  | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View | MW | REACT_CAP_ESG | MW2 |  | 1. MW2>0 2. MW2<MW3 | R
ESG | Lagging MVAR limit associated with MW2 output |  | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View | MVAR | REACT_CAP_ESG | MVAR2LAG |  | 1.Lagging MVAR limit associated with MW2 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R
ESG | Leading MVAR limit associated with MW2 output |  | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View | MVAR | REACT_CAP_ESG | MVAR2LEAD |  | 1. Leading MVAR limit associated with MW2 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R
ESG | MW3 |  | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View | MW | REACT_CAP_ESG | MW3 |  | 1. MW3 >0 2. MW3<MW4 | R
ESG | Lagging MVAR limit associated with MW3 output |  | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View | MVAR | REACT_CAP_ESG | MVAR3LAG |  | 1. Lagging MVAR limit associated with MW3 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R
ESG | Leading MVAR limit associated with MW3 output |  | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View | MVAR | REACT_CAP_ESG | MVAR3LEAD |  | 1.Leading MVAR limit associated with MW3 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R
ESG | MW4 |  | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View | MW | REACT_CAP_ESG | MW4 |  | 1. MW4 >0 2. MW4<MW5 3. X(n) > = WMX (Unit Max output) where n is the last MW value in the curve. If the curve has 4 points, X(n) is X(4) [ Generate a Warning Only When Business Rule#2 Fails] | R
ESG | Lagging MVAR limit associated with MW4 output |  | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View | MVAR | REACT_CAP_ESG | MVAR4LAG |  | 1. Lagging MVAR limit associated with MW4 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R
ESG | Leading MVAR limit associated with MW4 output |  | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View | MVAR | REACT_CAP_ESG | MVAR4LEAD |  | 1.Leading MVAR limit associated with MW4 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R
ESG | Maximum Leading Operating Capability |  | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View | MVAR | REACT_CAP_ESG | NETMAXLEAD
ESG | Maximum Lagging Operating Capability |  | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View | MVAR | REACT_CAP_ESG | NETMAXLAG
ESG | Has the Manufacturer's Capability Curve submitted? |  | ADD 04/2012 |  | Reactive Capability -ESG | ESG_ReactiveCapability.View | Y/N | REACT_CAP_ESG | MFR_CAP_CURVE |  | Select from the list: Y or N
Solar | Ownership - Solar |  |  |  | Ownership - Solar |  |  | Not in table | Not in table
Solar | Generator Detail |  |  |  | Ownership - Solar |  |  | Not in table | Not in table
Solar | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | Ownership - Solar | Solar_Ownership.View |  | OWNERSHIP | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R
Solar | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | Ownership - Solar | Solar_Ownership.View |  | OWNERSHIP | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C
Solar | Ownership Percentages |  |  |  | Ownership - Solar |  |  | Not in table | Not in table |  | 2.All letters should be capital
Solar | Joint Ownership Code |  | ADD 04/2012 |  | Ownership - Solar | Solar_Ownership.View | Y/N | OWNERSHIP | J0CODE |  | 3. Should not allow spaces
Solar | Resource Entity Name | Update 03/13/2012 | ADD 04/2012 |  | Ownership - Solar | Solar_Ownership.View |  | OWNERSHIP | MKT_PRTCPT |  | 1. Not null 2. Do not allow any special characters except spaces and dashes.
Solar | Resource Duns Number |  | ADD 04/2012 |  | Ownership - Solar | Solar_Ownership.View |  | OWNERSHIP | MKT_PRTCPT_DUNS
Solar | Fixed Ownership | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Ownership - Solar | Solar_Ownership.View |  | OWNERSHIP | FIX_OWNRSHP_PCT
Solar | Master Owner (Y or N) |  | ADD 04/2012 |  | Ownership - Solar | Solar_Ownership.View | Y/N | OWNERSHIP | MASTR_OWNR_FLG
Solar | Ownership Start Date | 04/09/2012 Changed Validation to be an Optional 03/07/2012 Updated with Business Rule | ADD 04/2012 |  | Ownership - Solar | Solar_Ownership.View | mm/dd/yyyy | OWNERSHIP | OWNR_START_DT |  | This field is optional. Format should be: MM/DD/YYYY | R O
Solar | Ownership Start Date | 03/07/2012 Updated with Business Rule | ADD 04/2012 |  | Ownership - Solar | Solar_Ownership.View | mm/dd/yyyy | OWNERSHIP | OWNR_END_DT |  | This field is optional. Format should be: MM/DD/YYYY | O
ESG | Ownership - ESG |  |  |  | Ownership - ESG |  |  | Not in table | Not in table
ESG | Generator Detail |  |  |  | Ownership - ESG |  |  | Not in table | Not in table
ESG | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | Ownership - ESG | ESG_Ownership.View | List | OWNERSHIP | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R
ESG | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | Ownership - ESG | ESG_Ownership.View | Automatic | OWNERSHIP | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C
ESG | Ownership Percentages |  |  |  | Ownership - ESG |  |  | Not in table | Not in table |  | 2.All letters should be capital
ESG | Joint Ownership |  | ADD 04/2012 |  | Ownership - ESG | ESG_Ownership.View | Y/N | OWNERSHIP | J0CODE |  | 3. Should not allow spaces | R
ESG | Resource Entity Name |  | ADD 04/2012 |  | Ownership - ESG | ESG_Ownership.View |  | OWNERSHIP | MKT_PRTCPT |  | 1. Not null 2. Do not allow any special characters except spaces and dashes. | C
ESG | Resource Duns Number |  | ADD 04/2012 |  | Ownership - ESG | ESG_Ownership.View |  | OWNERSHIP | MKT_PRTCPT_DUNS |  | This field is Conditional : Required if single entity represents the Resource. This should be either 9 or 13 digit number | C
ESG | Fixed Ownership | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Ownership - ESG | ESG_Ownership.View |  | OWNERSHIP | FIX_OWNRSHP_PCT
ESG | Master Owner (Y or N) |  | ADD 04/2012 |  | Ownership - ESG | ESG_Ownership.View | Y/N | OWNERSHIP | MASTR_OWNR_FLG
ESG | Ownership Start Date | 04/09/2012 Changed Validation to be an Optional 03/07/2012 Updated with Business Rule | ADD 04/2012 |  | Ownership - ESG | ESG_Ownership.View | mm/dd/yyyy | OWNERSHIP | OWNR_START_DT |  | This field is optional. Format should be: MM/DD/YYYY | R O
ESG | Ownership Start Date | 03/07/2012 Updated with Business Rule | ADD 04/2012 |  | Ownership - ESG | ESG_Ownership.View | mm/dd/yyyy | OWNERSHIP | OWNR_END_DT |  | This field is optional. Format should be: MM/DD/YYYY | O
Solar | Planning - Solar |  |  |  | Planning - Solar |  |  | Not in table | Not in table
Solar | GENERATION DETAILS |  |  |  | Planning - Solar |  |  | Not in table | Not in table
Solar | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R
Solar | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R
Solar | INVERTER TYPE | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | INVERTER_TYPE |  | Dropdown list | R
Solar | PLANNING DETAILS |  |  |  | Planning - Solar |  |  | Not in table | Not in table
Solar | What is the MVA base that the following data is based on? |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | MVA | SOLAR | MVABASE |  | 1) This field is required 2) Value must be Float 3) Generate a Warning if MVABASE > 2500 4)[ If MVABASE value is within +/- 25% range of Unit Name Plate Rating] OR [MVABASE value = 100, then it is OK.If MVABASE value is outside the +/- 25% range of Unit Name Plate Rating, then Generate a Warning that the MVABSE is outside the typical +/- 25% variation of unit name plate rating
Solar | What is the kV base that the following data is based on? |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | kV | SOLAR | KVBASE |  | 1) This field is required 2) Value must be >0 and <1000 3) Generate a Warning if KVBASE > 40 4) If KVBASE value is within +/- 25% range of Unit KV value in the unit-information tab then it is OK.If If KVBASE value is outside the typical +/- 25% variation of Unit KV value in the unit-information tab then Generate a Warning that the KVBASE is outside the typical +/- 25% variation of Unit KV value
Solar | Direct Axis Subtransient reactance, X"di (unsaturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | pu | SOLAR | DIRECT_AXIS_SUBSTNT_REACTANCE_UNSATURATED |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Solar | Direct Axis Transient reactance, X'di (unsaturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | pu | SOLAR | DIRECT_AXIS_TRANSNT_REACTANCE_UNSATURATED |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Solar | Positive Sequence Z (unsaturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | R in p.u. | SOLAR | POSITIVE_SEQ_Z_R_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1
Solar | Positive Sequence Z (unsaturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | X in p.u. | SOLAR | POSITIVE_SEQ_Z_X_UNSATURARTED_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Solar | Negative Sequence Z (unsaturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | R in p.u. | SOLAR | NEGATIVE_SEQ_Z_R_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning when value is > 1.0 P.U
Solar | Negative Sequence Z (unsaturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | X in p.u. | SOLAR | NEGATIVE_SEQ_Z_X_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Solar | Does Zero Sequence Z exist? |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | Y/N | SOLAR | DOES_ZERO_SEQ_EXIST |  |  | R | Planning Team
Solar | Zero Sequence Z (unsaturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | R in p.u. | SOLAR | ZERO_SEQ_Z_R_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U
Solar | Zero Sequence Z (unsaturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | X in p.u. | SOLAR | ZERO_SEQ_Z_X_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Solar | Direct Axis Subtransient reactance, X"dv (saturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | p.u. | SOLAR | DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Solar | Direct Axis Transient reactance, X'dv (saturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | p.u. | SOLAR | DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Solar | Positive Sequence Z (saturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | R in p.u. | SOLAR | POSITIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1
Solar | Positive Sequence Z (saturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | X in p.u. | SOLAR | POSITIVE_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Solar | Negative Sequence Z (saturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | R in p.u. | SOLAR | NEGATIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1
Solar | Negative Sequence Z (saturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | X in p.u. | SOLAR | NEGATIVE_SEQ_Z_X-SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Solar | Zero Sequence Z (saturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | R in p.u. | SOLAR | ZERO_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U
Solar | Zero Sequence Z (saturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | X in p.u. | SOLAR | ZERO_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Solar | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | p.u. | SOLAR | ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Solar | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | p.u. | SOLAR | ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Solar | Zero Sequence Resistance In P.u. (100 Mva Base) | 04/24/2012 Remove field from database and form. No validation. | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | p.u. | SOLAR | ZERO_SEQ_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Solar | Zero Sequence Reactance In P.u. (100 Mva Base) | 04/24/2012 Remove field from database and form. No validation. | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | p.u. | SOLAR | ZERO_SEQ_Reactance_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Solar | Generator Auxiliary Load |  |  |  | Planning - Solar |  |  | Not in table | Not in table
Solar | Average Amount of Auxiliary Real Power |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | MW | SOLAR | AUX_MWTOTAL |  | 1) This field is optional 2) Data type is float 3) Value must be < Parameters - GEN - High Reasonability Limit 4) Warn if value > (High Reasonability Limit) * .75 5) Error if value > (High Reasonability Limit) * .66
Solar | Average Amount of Auxiliary Reactive Power |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | MVAR | SOLAR | AUX_MVARTOTAL |  | 1) This field is optional 2) Data type is Float 3) Value must be < Reactive Capability - GEN - Maximum Lagging Operating Capability (MVAR) 4) Warn if value > ( Maximum Lagging Operating Capability) * .75 5) Error if value > ( Maximum Lagging Operating Capability) * .66
Solar | Auxiliary Load Power Factor | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | AUX_LOAD_PWR_FACT |  | Between .8 and 1.0
Solar | Generation Auxiliary Load Characteristics for MW Load |  |  |  | Planning - Solar |  |  | Not in table | Not in table
Solar | Large Motor, percent of total MW load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | LRG_MTR_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
Solar | Small Motor, percent of total MW load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | SML_MTR_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
Solar | Resistive (Heating) Load, percent of total MW load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | RESISTIVE_LOAD_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
Solar | Discharge Lighting, percent of total MW load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | DISCHARGE LIGHT_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
Solar | Other, percent of total MW load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | OTH_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
Solar | Generation Auxiliary Load Characteristics for MVAR Load |  |  |  | Planning - Solar |  |  | Not in table | Not in table
Solar | Large Motor, percent of total MVAR load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | LRG_MTR_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y'
Solar | Small Motor, percent of total MVAR load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | SML_MTR_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y'
Solar | Discharge Lighting, percent of total MVAR load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | DISCHARGE LIGHT_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y'
Solar | Other, percent of total MVAR load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | OTH_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y'
Solar | INVERTER STEP-UP TRANSFORMER DATA |  |  |  | Planning - Solar |  |  | Not in table | Not in table
Solar | High Side Voltage Level (nominal) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | kV | SOLAR | HIGH_SIDE_VT_LEVL |  | 1) This field is required 2) Data type must be real 3) Generate an Error if not between 345 and 69
Solar | Low Side Voltage Level (nominal) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | kV | SOLAR | LOW_SIDE_VT_LEVL |  | 1) This field is required 2) Data type must be real 3) Generate an Error if not < 69
Solar | High Side Voltage Connection - Wye / Wye - Grounded / Delta |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | HIGH_SIDE_VT_CONNT |  | 1) This field is required 2) Data type must be from list (Wye, Wye - Grounded or Delta) 3) Generate an Error if blank
Solar | Low Side Voltage Connection - Wye / Wye - Grounded / Delta |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | LOW_SIDE_VT_CONNT |  | 1) This field is required 2) Data type must be from list (Wye, Wye - Grounded or Delta) 3) Generate an Error if blank
Solar | Impedance Z |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | p.u. | SOLAR | IMPEDANCE_Z |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0
Solar | X/r Ratio |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | X_R_RATIO |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 1
Solar | Zero Sequence Z |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | p.u. | SOLAR | ZERO_SEQ_Z |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0
Solar | Zero Sequence X/r Ratio |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | ZERO_SEQ_X_R_RATIO |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 1
Solar | Base Mva For Transformer Data |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | MVA | SOLAR | BASE_MVA_TRANSFORMER_DATA |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank, Generate Warning if > 2000
Solar | Inverter Limits In P.u. Of Nominal Output For Fault Duty Studies |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | p.u. | SOLAR | INVERTER_LIMT_PU_NOMINAL_FAULT_DUTY_STUDIES
Solar | VOLTAGE REGULATION |  |  |  | Planning - Solar |  |  | Not in table | Not in table
Solar | Automatic Voltage Regulation | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | Y/N | SOLAR | AUTO_VLT_REG |  | 1) This field is required 2) Value must be from the following list: 'Y', 'N'
Solar | Does Transformer Have A Load Tap Changer? | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | Y/N | SOLAR | TRANS_LOAD_TAPCHARGER |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) Value must be from the following list: 'Y', 'N' 3) Load Tap Changer is expected to be 'Y' when total number of tap positions >=16. Warn if "Load Tap Changer" = 'N' and Total Number of Tap Positions>=16
Solar | Location of Tap Changer High or Low | 03/28/2012 Removed High or Low from Field Name and removed validation Rule #3. Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | List | SOLAR | LOC_LOAD_TAPCHARGER |  | 1) This field is conditionally required if 'Does Transformer have a Load Tap Changer ?' = 'Y' 2) Value must be of the following: 'HIGH', 'LOW, BOTH, NONE' 3) Load Tap Changer should be 'Y' when AVR is 'Y'. Generate an error if Load Tap Changer is 'N' and AVR = 'Y'. | T | Planning
Solar | Base Kv Of Regulated Side | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | kV | SOLAR | BASE_LV_REG_SIDE |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 5) The value must be >= Low Voltage Level (no-load)
Solar | Target Kv Of Regulated Side | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | kV | SOLAR | TARG_KV_REG_SIDE |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) Value must be > 0
Solar | Acceptable Deviation Of Target Voltage | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | DEVITON_TARG_VT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0
Solar | ONLY IF HIGH SIDE TAP EXISTS |  |  |  | Planning - Solar |  |  | Not in table | Not in table
Solar | Tap Position At Manufactured Nominal Voltage | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | Y/N | SOLAR | TAP_POS_MAN_NOMINAL_VT_HIGH |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
Solar | Total Number Of Tap Positions |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | Integer | SOLAR | TOT_NUM_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
Solar | Normal Tap Position | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | Integer | SOLAR | NORML_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
Solar | Lowest Tap Position | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | Integer | SOLAR | LOW_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
Solar | Voltage At Lowest Tap Position | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | kV | SOLAR | VT_LOWST_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be real 3) Generate an Warning if not within 15% of nominal on tapped side of transformer
Solar | Highest Tap Position | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | Integer | SOLAR | HIGH_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
Solar | Voltage At Highest Tap Position | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | kV | SOLAR | VT_HIGHST_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be real 3) Generate an Warning if not within 15% of nominal on tapped side of transformer
Solar | Size Of Each Voltage Level Step | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | kV | SOLAR | SIZE_EACH_VT_LEVL_STEP_HIGH |  | 1) This field is required 2) Data type must be real 3) Generate an Warning if not within 10% of nominal kV / number of taps
Solar | PSSE MODEL : THE FOLLOWING LIST OF FILES ARE REQUIRED TO BE SUBMITTED IF THIS IS AN INITIAL REGISTRATION OR IF THERE ARE CHANGES MODIFYING PREVIOUSLY SUBMITTED PSSE FILES. PLEASE INCLUDE ALL PSSE FILES IN A ZIP OR COMPRESSED FOLDER FILE ALONG WITH YOUR RARF SUBMITTAL IN THE SAME SERVICE REQUEST |  |  |  | Planning - Solar |  |  | Not in table | Not in table
Solar | Psse Compatible Solar Pv Generator Models |  |  |  | Planning - Solar |  | Y/N | Not in table | Not in table
Solar | Dynamic Reactive Device Form/models |  |  |  | Planning - Solar |  | Y/N | Not in table | Not in table
ESG | Planning - ESG |  |  |  | Planning - ESG |  |  | Not in table | Not in table
ESG | GENERATOR DETAILS |  |  |  | Planning - ESG |  |  | Not in table | Not in table
ESG | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | List | ESGUNIT | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R
ESG | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | Automatic | ESGUNIT | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C
ESG | Dispatch Asset Code (Provided by ERCOT) | 04/04/2012 Not In RARF Form but needed for Reports | ADD 04/2012 | NOT IN RARF FORM | Planning - ESG | Planning_ESGUNIT.View | all caps | ESGUNIT | DISPATCH_ASSET_CODE
ESG | PLANNING DETAILS |  |  |  | Planning - ESG |  |  | Not in table | Not in table
ESG | What is the MVA base that the following data is based on? | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | MVA | ESGUNIT | MVABASE |  | 1) This field is required 2) Value must be Float 3) Generate a Warning if MVABASE > 2500 4)[ If MVABASE value is within +/- 25% range of Unit Name Plate Rating] OR [MVABASE value = 100, then it is OK.If MVABASE value is outside the +/- 25% range of Unit Name Plate Rating, then Generate a Warning that the MVABSE is outside the typical +/- 25% variation of unit name plate rating | R
ESG | What is the kV base that the following data is based on? |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | kV | ESGUNIT | KVBASE |  | 4. Can not exceed 13 characters for split gen resources | R
ESG | Direct Axis Subtransient reactance, X"di (unsaturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | p.u. | ESGUNIT | DIRECT_AXIS_SUBSTNT_REACTANCE_UNSATURATED |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value.(* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
ESG | Direct Axis Transient reactance, X'di (unsaturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | p.u. | ESGUNIT | DIRECT_AXIS_TRANSNT_REACTANCE_UNSATURATED |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
ESG | Positive Sequence Z (unsaturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | R in p.u. | ESGUNIT | POSITIVE_SEQ_Z_R_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1
ESG | Positive Sequence Z (unsaturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | X in p.u. | ESGUNIT | POSITIVE_SEQ_Z_X_UNSATURARTED_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
ESG | Negative Sequence Z (unsaturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | R in p.u. | ESGUNIT | NEGATIVE_SEQ_Z_R_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1
ESG | Negative Sequence Z (unsaturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | X in p.u. | ESGUNIT | NEGATIVE_SEQ_Z_X_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
ESG | Does Zero Sequence Z exist? |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | Y/N | ESGUNIT | DOES_ZERO_SEQ_EXIST |  | Drop Down List Y or N | R | Planning Team
ESG | Zero Sequence Z (unsaturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | R in p.u. | ESGUNIT | ZERO_SEQ_Z_R_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 . Generate a Warning when value is > 1.0 P.U
ESG | Zero Sequence Z (unsaturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | X in p.u. | ESGUNIT | ZERO_SEQ_Z_X_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
ESG | Direct Axis Subtransient reactance, X"dv (saturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | p.u. | ESGUNIT | DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value.(* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R
ESG | Direct Axis Transient reactance, X'dv (saturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | p.u. | ESGUNIT | DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R
ESG | Positive Sequence Z (saturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | R in p.u. | ESGUNIT | POSITIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R
ESG | Positive Sequence Z (saturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | X in p.u. | ESGUNIT | POSITIVE_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R
ESG | Negative Sequence Z (saturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | R in p.u. | ESGUNIT | NEGATIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R
ESG | Negative Sequence Z (saturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | X in p.u. | ESGUNIT | NEGATIVE_SEQ_Z_X-SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R
ESG | Zero Sequence Z (saturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | R in p.u. | ESGUNIT | ZERO_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U | R
ESG | Zero Sequence Z (saturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | X in p.u. | ESGUNIT | ZERO_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R
ESG | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | p.u. | ESGUNIT | ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
ESG | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | p.u. | ESGUNIT | ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
ESG | Zero Sequence Resistance In P.u. (100 Mva Base) | 04/24/2012 Remove field from database and form. No validation. Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | p.u. | ESGUNIT | ZERO_SEQ_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Planning Team
ESG | Zero Sequence Reactance In P.u. (100 Mva Base) | 04/24/2012 Remove field from database and form. No validation. Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | p.u. | ESGUNIT | ZERO_SEQ_Reactance_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Planning Team
ESG | Generator Auxiliary Load |  |  |  | Planning - ESG |  |  | Not in table | Not in table
ESG | Average Amount of Auxiliary Real Power |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | MW | ESGUNIT | AUX_MWTOTAL |  | 1) This field is optional 2) Data type is float 3) Value must be < Parameters - GEN - High Reasonability Limit 4) Warn if value > (High Reasonability Limit) * .75 5) Error if value > (High Reasonability Limit) * .66
ESG | Average Amount of Auxiliary Reactive Power |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | MVAR | ESGUNIT | AUX_MVARTOTAL |  | 1) This field is optional 2) Data type is Float 3) Value must be < Reactive Capability - GEN - Maximum Lagging Operating Capability (MVAR) 4) Warn if value > ( Maximum Lagging Operating Capability) * .75 5) Error if value > ( Maximum Lagging Operating Capability) * .66
ESG | Auxiliary Load Power Factor | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View |  | ESGUNIT | AUX_LOAD_PWR_FACT |  | Between .8 and 1.0
ESG | Generation Auxiliary Load Characteristics for MW Load |  |  |  | Planning - ESG |  |  | Not in table | Not in table
ESG | Large Motor, percent of total MW load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View |  | ESGUNIT | LRG_MTR_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
ESG | Small Motor, percent of total MW load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View |  | ESGUNIT | SML_MTR_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
ESG | Resistive (Heating) Load, percent of total MW load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View |  | ESGUNIT | RESISTIVE_LOAD_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
ESG | Discharge Lighting, percent of total MW load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View |  | ESGUNIT | DISCHARGE LIGHT_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
ESG | Other, percent of total MW load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View |  | ESGUNIT | OTH_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
ESG | Generation Auxiliary Load Characteristics for MVAR Load |  |  |  | Planning - ESG |  |  | Not in table | Not in table
ESG | Large Motor, percent of total MVAR load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View |  | ESGUNIT | LRG_MTR_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y'
ESG | Small Motor, percent of total MVAR load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View |  | ESGUNIT | SML_MTR_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y'
ESG | Discharge Lighting, percent of total MVAR load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View |  | ESGUNIT | DISCHARGE LIGHT_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y'
ESG | Other, percent of total MVAR load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View |  | ESGUNIT | OTH_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y'
ESG | Voltage Regulation |  |  |  | Planning - ESG |  |  | Not in table | Not in table
ESG | Automatic Voltage Regulation |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | Y/N | ESGUNIT | AUTO_VLT_REG |  | 1) This field is required 2) Value must be from the following list: 'Y', 'N'
ESG | Does Transformer have a Load Tap Changer? |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | Y/N | ESGUNIT | TRANS_LOAD_TAPCHARGER |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) Value must be from the following list: 'Y', 'N' 3) Load Tap Changer is expected to be 'Y' when total number of tap positions >=16. Warn if "Load Tap Changer" = 'N' and Total Number of Tap Positions>=16
ESG | Location of Tap Changer High or Low | 03/28/2012 Removed High or Low from Field Name and removed validation Rule #3. Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | List | ESGUNIT | LOC_LOAD_TAPCHARGER |  | 1) This field is conditionally required if 'Does Transformer have a Load Tap Changer ?' = 'Y' 2) Value must be of the following: 'HIGH', 'LOW, BOTH, NONE' 3) Load Tap Changer should be 'Y' when AVR is 'Y'. Generate an error if Load Tap Changer is 'N' and AVR = 'Y'. | T | Planning
ESG | Base kV of Regulated Side |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | kV | ESGUNIT | BASE_LV_REG_SIDE |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 5) The value must be >= Low Voltage Level (no-load)
ESG | Target kV of Regulated Side |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | kV | ESGUNIT | TARG_KV_REG_SIDE |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) Value must be > 0
ESG | Acceptable Deviation of Target Voltage | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View |  | ESGUNIT | DEVITON_TARG_VT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0
ESG | Only if High Side Tap Exists |  |  |  | Planning - ESG |  |  | Not in table | Not in table
ESG | Tap position at Manufactured Nominal Voltage |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | Integer | ESGUNIT | TAP_POS_MAN_NOMINAL_VT_HIGH |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
ESG | Total Number of Tap Positions |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | Integer | ESGUNIT | TOT_NUM_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
ESG | Normal Tap Position |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | Integer | ESGUNIT | NORML_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
ESG | Lowest Tap Position |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | Integer | ESGUNIT | LOW_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
ESG | Voltage at Lowest Tap Position |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | kV | ESGUNIT | VT_LOWST_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be real 3) Generate an Warning if not within 15% of nominal on tapped side of transformer
ESG | Highest Tap Position |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | Integer | ESGUNIT | HIGH_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
ESG | Voltage at Highest Tap Position |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | kV | ESGUNIT | VT_HIGHST_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be real 3) Generate an Warning if not within 15% of nominal on tapped side of transformer
ESG | Size of each Voltage Level Step |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | kV | ESGUNIT | SIZE_EACH_VT_LEVL_STEP_HIGH |  | 1) This field is required 2) Data type must be real 3) Generate an Warning if not within 10% of nominal kV / number of taps
ESG | Only if Low Side Tap Exists |  |  |  | Planning - ESG |  |  | Not in table | Not in table
ESG | Tap position at Manufactured Nominal Voltage |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | Integer | ESGUNIT | TAP_POSITNS_MANFACTURED_NOMINAL_VT_LOW |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
ESG | Total Number of Tap Positions |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | Integer | ESGUNIT | TOT_NUM_TAP_POSITNS_LOW |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
ESG | Normal Tap Position |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | Integer | ESGUNIT | NORML_TAP_POSITNS_LOW |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
ESG | Lowest Tap Position |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | Integer | ESGUNIT | LOW_TAP_POSITNS_LOW |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
ESG | Voltage at Lowest Tap Position |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | kV | ESGUNIT | VT_LOWST_TAP_POSITNS_LOW |  | 1) This field is required 2) Data type must be real 3) Generate an Warning if not within 15% of nominal on tapped side of transformer
ESG | Highest Tap Position |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | Integer | ESGUNIT | HIGH_TAP_POSITNS_LOW |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
ESG | Voltage at Highest Tap Position |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | kV | ESGUNIT | VT_HIGHST_TAP_POSITNS_LOW |  | 1) This field is required 2) Data type must be real 3) Generate an Warning if not within 15% of nominal on tapped side of transformer
ESG | Size of each Voltage Level Step |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | kV | ESGUNIT | SIZE_EACH_VT_LEVL_STEP_LOW |  | 1) This field is required 2) Data type must be real 3) Generate an Warning if not within 10% of nominal kV / number of taps
ESG | Inverter Data (if applicable) |  |  |  | Planning - ESG |  |  | Not in table | Not in table
ESG | What is the MVA base that the following data is based on? |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | MVA | ESGUNIT | INVERTER_MVA_BASE |  | 1) This field is required 2) Value must be Float 3) Generate a Warning if MVABASE > 2500 4)[ If MVABASE value is within +/- 25% range of Unit Name Plate Rating] OR [MVABASE value = 100, then it is OK.If MVABASE value is outside the +/- 25% range of Unit Name Plate Rating, then Generate a Warning that the MVABSE is outside the typical +/- 25% variation of unit name plate rating
ESG | What is the kV base that the following data is based on? |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | kV | ESGUNIT | INVERTER_KV_BASE |  | 1) This field is required 2) Value must be >0 and <1000 3) Generate a Warning if KVBASE > 40 4) If KVBASE value is within +/- 25% range of Unit KV value in the unit-information tab then it is OK.If If KVBASE value is outside the typical +/- 25% variation of Unit KV value in the unit-information tab then Generate a Warning that the KVBASE is outside the typical +/- 25% variation of Unit KV value
ESG | Direct Axis Subtransient reactance, X"di |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | p.u. | ESGUNIT | DIRECT_AXIS_SUBSTNT_REACTANCE_INVERTER |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
ESG | Direct Axis Transient reactance, X'di |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | p.u. | ESGUNIT | DIRECT_AXIS_TRANSNT_REACTANCE_UINVERTER |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
ESG | Positive Sequence Z (Unsaturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | R in p.u. | ESGUNIT | POSITIVE_SEQ_Z_R_UNSATURARTED_PU_INVERTER |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1
ESG | Positive Sequence Z (Unsaturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | X in p.u. | ESGUNIT | POSITIVE_SEQ_Z_X_UNSATURARTED_PU_INVERTER |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
ESG | Negative Sequence Z (Unsaturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | R in p.u. | ESGUNIT | NEGATIVE_SEQ_Z_R_UNSATURARTED_PU_INVERTER. |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1
ESG | Negative Sequence Z (Unsaturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | X in p.u. | ESGUNIT | NEGATIVE_SEQ_Z_X_UNSATURARTED_PU_INVERTER |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
ESG | Zero Sequence Z (Unsaturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | R in p.u. | ESGUNIT | ZERO_SEQ_Z_R_UNSATURARTED_PU_INVERTER |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 . Generate a Warning when value is > 1.0 P.U
ESG | Zero Sequence Z (Unsaturated) |  | ADD 04/2012 |  | Planning - ESG | Planning_ESGUNIT.View | X in p.u. | ESGUNIT | ZERO_SEQ_Z_X_UNSATURARTED_PU_INVERTER |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
ESG | PSSE Models : The following files are required to be submitted if not listed in the Wind Turbine Dynamic Models available at ERCOT or if additional equipment has been added to the site requiring Model updates. Please include all PSSE files in a ZIP or Compressed Folder along with your RARF submittal Service Request. |  |  |  | Planning - ESG |  |  | Not in table | Not in table
ESG | PSSE Compatible Solar Pv Generator Models |  |  |  | Planning - ESG |  |  | Not in table | Not in table
ESG | Dynamic Reactive Device Form/models |  |  |  | Planning - ESG |  |  | Not in table | Not in table
Solar | Protection - Solar |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View |  | Not in table | Not in table
Solar | GENERATOR DETAILS |  |  |  | Protection - Solar |  |  | Not in table | Not in table
Solar | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View |  | SOLAR | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R
Solar | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View |  | SOLAR | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C
Solar | Breaker Interruption Time |  |  |  | Protection - Solar |  |  | Not in table | Not in table
Solar | Breaker Interruption Time |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | cycles | SOLAR | BREAKER_INTERRUP |  | 1) this field is required 2) Data type must be Integer | R
Solar | PLANT VOLTAGE PROTECTION |  |  |  | Protection - Solar |  |  | Not in table | Not in table
Solar | Instantaneous Undervoltage Trip |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | p.u. | SOLAR | UVOLT_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Solar | Undervoltage 1 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | p.u. | SOLAR | UVOLT_TRIP_VOLT1 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Solar | Time 1 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | UVOLT_TRIP_TIME1 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Solar | Undervoltage 2 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | p.u. | SOLAR | UVOLT_TRIP_VOLT2 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Solar | Time 2 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | UVOLT_TRIP_TIME2 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Solar | Undervoltage 3 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | p.u. | SOLAR | UVOLT_TRIP_VOLT3 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Solar | Time 3 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | UVOLT_TRIP_TIME3 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Solar | Undervoltage 4 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | p.u. | SOLAR | UVOLT_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Solar | Time 4 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | UVOLT_TRIP_VOLT4 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Solar | Instantaneous Overvoltage Trip |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | p.u. | SOLAR | OVOLT_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Solar | Overvoltage 1 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | p.u. | SOLAR | OVOLT_TRIP_VOLT1 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Solar | Time 1 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | OVOLT_TRIP_TIME1 |  | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Solar | Overvoltage 2 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | p.u. | SOLAR | OVOLT_TRIP_VOLT2 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Solar | Time 2 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | OVOLT_TRIP_TIME2 |  | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Solar | Overvoltage 3 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | p.u. | SOLAR | OVOLT_TRIP_VOLT3 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Solar | Time 3 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | OVOLT_TRIP_TIME3 |  | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Solar | Overvoltage 4 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | p.u. | SOLAR | OVOLT_TRIP_VOLT4 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Solar | Time 4 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | OVOLT_TRIP_TIME4 |  | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Solar | PLANT FREQUENCY PROTECTION |  |  |  | Protection - Solar |  |  | Not in table | Not in table
Solar | Instantaneous Underfrequency Trip |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Hz | SOLAR | UFREQ_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float
Solar | Underfrequency 1 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Hz | SOLAR | UFREQ_TRIP_HZ1 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab
Solar | Time 1 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | UFREQ_TRIP_TIME1 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Solar | Underfrequency 2 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Hz | SOLAR | UFREQ_TRIP_HZ2 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab
Solar | Time 2 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | UFREQ_TRIP_TIME2 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Solar | Underfrequency 3 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Hz | SOLAR | UFREQ_TRIP_HZ3 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab
Solar | Time 3 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | UFREQ_TRIP_TIME3 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Solar | Underfrequency 4 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Hz | SOLAR | UFREQ_TRIP_HZ4 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab
Solar | Time 4 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | UFREQ_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Solar | Instantaneous Overfrequency Trip |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Hz | SOLAR | OFREQ_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float
Solar | Overfrequency 1 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Hz | SOLAR | OFREQ_TRIP_HZ1 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab
Solar | Time 1 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | OFREQ_TRIP_TIME1 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Solar | Overfrequency 2 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Hz | SOLAR | OFREQ_TRIP_HZ2 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab
Solar | Time 2 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | OFREQ_TRIP_TIME2 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Solar | Overfrequency 3 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Hz | SOLAR | OFREQ_TRIP_HZ3 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab
Solar | Time 3 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | OFREQ_TRIP_TIME3 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Solar | Overfrequency 4 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Hz | SOLAR | OFREQ_TRIP_HZ4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab
Solar | Time 4 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | OFREQ_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Solar | PV INVERTER VRT CAPABILITY |  |  |  | Protection - Solar |  |  | Not in table | Not in table
Solar | Provide Manufacturer's Technical Document / Simulation Results / Test Result, Etc. Describing The Solar Technology & Vrt OPTIons Purchased With Inverter, If Any |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Y/N | SOLAR | MAN_TECH_DOC_SIM_RESULTS
Solar | Do Personnel (onsite Operator/engineer Etc.) Have Control To Enable/disable Or Change The Settings For Voltage Ride-through |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Y/N | SOLAR | PERSONNEL_CHANGE_SET_CNTRL
Solar | Does The Resource Use Dynamic Reactive Devices (SVC/statcom, Etc.) At Solar Plant Facility? - (note: Capacitor Banks Used For Conventional Reactive Support Cannot Be Considered As Dynamic Reactive Devices) - If Yes, Please Provide Supporting Documentation. (manufacturer's Technical Document, Pss/e Model Etc.) |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Y/N | SOLAR | DYNAMIC_REACT_DEVICES
Solar | Provide Inverter Voltage & Frequency Protection Settings As Per Manufacturer - Technical Document And/or Spec Sheet |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Y/N | SOLAR | INVERTER_VOLTAGE_FREQ_PROT_SET
Solar | Does The Resource Have Plant Voltage Protection? If Yes, Please Provide Supporting Documentation. |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Y/N | SOLAR | RE_PLANT_VOLTAGE_PROT
Solar | Does The Resource Have Feeder Voltage Protection? If Yes, Please Provide Supporting Documentation. |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Y/N | SOLAR | RE_VOLTAGE_FEEDER_PROT
ESG | Protection - ESG |  |  |  | Protection - ESG |  |  | Not in table | Not in table
ESG | GENERATOR DETAILS |  |  |  | Protection - ESG |  |  | Not in table | Not in table
ESG | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | List | ESGUNIT | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R
ESG | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | Automatic | ESGUNIT | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C
ESG | Dispatch Asset Code (Provided by ERCOT) | 04/04/2012 Not In RARF Form but needed for Reports | ADD 04/2012 | NOT IN RARF FORM | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | all caps | ESGUNIT | DISPATCH_ASSET_CODE
ESG | Breaker Interruption Time |  |  |  | Protection - ESG |  |  | Not in table | Not in table |  | 3. Should not allow spaces
ESG | Breaker Interruption Time |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | cycles | ESGUNIT | BREAKER_INTERRUP |  | 3. Should not allow spaces
ESG | PLANT VOLTAGE PROTECTION |  |  |  | Protection - ESG |  |  | Not in table | Not in table |  | 4. Can not exceed 13 characters for split gen resources
ESG | Instantaneous Undervoltage Trip |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | p.u. | ESGUNIT | UVOLT_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | O
ESG | Undervoltage 1 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | p.u. | ESGUNIT | UVOLT_TRIP_VOLT1 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | R
ESG | Time 1 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | sec | ESGUNIT | UVOLT_TRIP_TIME1 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | R
ESG | Undervoltage 2 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | p.u. | ESGUNIT | UVOLT_TRIP_VOLT2 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | O
ESG | Time 2 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | sec | ESGUNIT | UVOLT_TRIP_TIME2 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | R
ESG | Undervoltage 3 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | p.u. | ESGUNIT | UVOLT_TRIP_VOLT3 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | R
ESG | Time 3 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | sec | ESGUNIT | UVOLT_TRIP_TIME3 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | O
ESG | Undervoltage 4 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | p.u. | ESGUNIT | UVOLT_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | R
ESG | Time 4 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | sec | ESGUNIT | UVOLT_TRIP_VOLT4 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | R
ESG | Instantaneous Overvoltage Trip |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | p.u. | ESGUNIT | OVOLT_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | O
ESG | Overvoltage 1 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | p.u. | ESGUNIT | OVOLT_TRIP_VOLT1 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | R
ESG | Time 1 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | sec | ESGUNIT | OVOLT_TRIP_TIME1 |  | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | R
ESG | Overvoltage 2 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | p.u. | ESGUNIT | OVOLT_TRIP_VOLT2 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | R
ESG | Time 2 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | sec | ESGUNIT | OVOLT_TRIP_TIME2 |  | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | R
ESG | Overvoltage 3 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | p.u. | ESGUNIT | OVOLT_TRIP_VOLT3 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | R
ESG | Time 3 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | sec | ESGUNIT | OVOLT_TRIP_TIME3 |  | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | R
ESG | Overvoltage 4 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | p.u. | ESGUNIT | OVOLT_TRIP_VOLT4 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | R
ESG | Time 4 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | sec | ESGUNIT | OVOLT_TRIP_TIME4 |  | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | R
ESG | PLANT FREQUENCY PROTECTION |  |  |  | Protection - ESG |  |  | Not in table | Not in table
ESG | Instantaneous Underfrequency Trip |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | Hz | ESGUNIT | UFREQ_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float | O
ESG | Underfrequency 1 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | Hz | ESGUNIT | UFREQ_TRIP_HZ1 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | R
ESG | Time 1 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | sec | ESGUNIT | UFREQ_TRIP_TIME1 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R
ESG | Underfrequency 2 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | Hz | ESGUNIT | UFREQ_TRIP_HZ2 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | R
ESG | Time 2 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | sec | ESGUNIT | UFREQ_TRIP_TIME2 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R
ESG | Underfrequency 3 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | Hz | ESGUNIT | UFREQ_TRIP_HZ3 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | R
ESG | Time 3 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | sec | ESGUNIT | UFREQ_TRIP_TIME3 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R
ESG | Underfrequency 4 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | Hz | ESGUNIT | UFREQ_TRIP_HZ4 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | R
ESG | Time 4 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | sec | ESGUNIT | UFREQ_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R
ESG | Instantaneous Overfrequency Trip |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | Hz | ESGUNIT | OFREQ_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float | O
ESG | Overfrequency 1 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | Hz | ESGUNIT | OFREQ_TRIP_HZ1 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | R
ESG | Time 1 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | sec | ESGUNIT | OFREQ_TRIP_TIME1 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R
ESG | Overfrequency 2 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | Hz | ESGUNIT | OFREQ_TRIP_HZ2 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | R
ESG | Time 2 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | sec | ESGUNIT | OFREQ_TRIP_TIME2 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R
ESG | Overfrequency 3 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | Hz | ESGUNIT | OFREQ_TRIP_HZ3 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | R
ESG | Time 3 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | sec | ESGUNIT | OFREQ_TRIP_TIME3 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R
ESG | Overfrequency 4 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | Hz | ESGUNIT | OFREQ_TRIP_HZ4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | R
ESG | Time 4 |  | ADD 04/2012 |  | Protection - ESG | Audit - ESG_Protection.View Delta - PROTECTION_ESG.View | sec | ESGUNIT | OFREQ_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R
Solar | Collector System - Solar | Corrected Tab name 03/26/2012 |  |  | Collector System - Solar |  |  | Not in table | Not in table
Solar | Site Code | 04/19/2012 Added field to Mapping but not added to Form |  |  | Collector System - Solar |  |  | SITECODES | SITE_CODE
SOLAR | Resource Name (Unit Code/Mnemonic) | 05/17/2012 Update #3 validation Added field in form 03/26/2012 |  |  | Collector System - Solar |  |  | COLLECTOR_SYS | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters for split gen resources | C
Solar | COLLECTION SYSTEM DETAILED MODEL | Corrected Tab name 03/26/2012 |  |  | Collector System - Solar |  |  | Not in table | Not in table
Solar | Cable Type | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Solar | CollectorSystem.View |  | COLLECTOR_SYS | CABLE_TYPE |  | 1) This field is required 2) Data type must string 3) Generate an Warning if blank
Solar | Voltage Level kV | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Solar | CollectorSystem.View | kV | COLLECTOR_SYS | VT_LEVEL_KV |  | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0
Solar | POSITIVE SEQUENCE DATA | Corrected Tab name 03/26/2012 |  |  | Collector System - Solar |  | Label | Not in table | Not in table
Solar | R/kft | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Solar | CollectorSystem.View | R/kft | COLLECTOR_SYS | POS_R_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank
Solar | X/kft | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Solar | CollectorSystem.View | X/kft | COLLECTOR_SYS | POS_X_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank
Solar | Charging Bc/kft | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Solar | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_CHRG_BC_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank
Solar | ZERO SEQUENCE DATA | Corrected Tab name 03/26/2012 |  |  | Collector System - Solar |  | Label | Not in table | Not in table
Solar | R0/kft | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Solar | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | ZERO_R0_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank
Solar | X0/kft | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Solar | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | ZERO_X0_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank
Solar | Collector System-Solar Seg Data | Corrected Tab name 03/26/2012 |  |  | Collector System - Seg Data Solar |  |  | Not in table | Not in table
Solar | Site Code | 04/19/2012 Added field to Mapping but not added to Form |  |  | Collector System - Seg Data Solar |  |  | SITECODES | SITE_CODE
Solar | CABLE TYPE | Corrected Tab name 03/26/2012 |  |  | Collector System - Seg Data Solar |  |  | Not in table | Not in table
Solar | Cable Type | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Seg Data Solar | CollectorSystem_SegData.View |  | CABLE_SEG_DATA | CABLE_TYPE |  | 1) This field is required 2) Data type must string 3) Generate an Warning if blank
SOLAR | Resource Name (Unit Code/Mnemonic) | Added 03/26/2012 |  |  | Collector System - Seg Data Solar |  |  | CABLE_SEG_DATA | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C
Solar | CABLE SEGAMENT DATA | Corrected Tab name 03/26/2012 |  |  | Collector System - Seg Data Solar |  |  | Not in table | Not in table
Solar | From | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Seg Data Solar | CollectorSystem_SegData.View | Integer | CABLE_SEG_DATA | CABLE_SEG_DATA_FROM |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank
Solar | To | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Seg Data Solar | CollectorSystem_SegData.View | Integer | CABLE_SEG_DATA | CABLE_SEG_DATA_TO |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank
Solar | Circuit Number | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Seg Data Solar | CollectorSystem_SegData.View | Integer | CABLE_SEG_DATA | CIRCT_NUM |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank
Solar | Voltage Level | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Seg Data Solar | CollectorSystem_SegData.View | kV | CABLE_SEG_DATA | VT_LEVL |  | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0.
Solar | Cable Segment Length | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Seg Data Solar | CollectorSystem_SegData.View | in kft | CABLE_SEG_DATA | CABLE_SEG_LENTH |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank
Solar | Number of Turbines On Cable Segment | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Seg Data Solar | CollectorSystem_SegData.View | Integer | CABLE_SEG_DATA | NUM_TURBIN_ON_CABLE_SEG |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank
ESG | Load Characteristics for MVAR Load |  |  |  | Private Network -ESG |  |  | Not in table | Not in table
ESG | Private Network - Unit - ESG |  |  |  | Private Network - Unit - ESG |  |  | Not in table | Not in table
ESG | GENERATOR DETAILS |  |  |  | Private Network - Unit - ESG |  |  | Not in table | Not in table
ESG | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 | Private Network - Unit - ESG | Private Network - Unit - ESG | ESG_PrivateNetwork.View | List | SITECODES | UNIT_NAME | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | 1. This field is not null. Data type: Character. | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
ESG | SITE_CODE |  | ADD 04/2012 | Private Network - Unit - ESG | Private Network - Unit - ESG | ESG_PrivateNetwork.View | Automatic | SITECODES | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
ESG | Resource Name (Unit Code/Mnemonic) | Do not show Message on Audit or Delta | ADD 04/2012 | Private Network - Unit - ESG | Private Network - Unit - ESG | ESG_PrivateNetwork.View | Automatic | SITECODES | UNIT_CODE | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | Character | Lodestar
ESG | Dispatch Asset Code (Provided by ERCOT) | 04/04/2012 Not In RARF Form but needed for Reports | ADD 04/2012 | NOT IN RARF FORM | Private Network - Unit - ESG | ESG_PrivateNetwork.View | all caps | ESGUNIT | DISPATCH_ASSET_CODE
ESG | PRIVATE NETWORK - UNIT INFORMATION |  |  |  | Private Network - Unit - ESG |  |  | Not in table | Not in table
ESG | Average Amount of Self-Serve private load |  | ADD 04/2012 |  | Private Network - Unit - ESG | ESG_PrivateNetwork.View | MW | ESGUNIT | AVG_LD_MW_UNIT
ESG | Average Amount of Self-Serve private reactive load |  | ADD 04/2012 |  | Private Network - Unit - ESG | ESG_PrivateNetwork.View | MVAR | ESGUNIT | AVG_LD_MVAR_UNIT
ESG | Expected Typical Private Network Net Interchange |  | ADD 04/2012 |  | Private Network - Unit - ESG | ESG_PrivateNetwork.View | MW | ESGUNIT | NET_INTERCHNG_MW_UNIT
ESG | Expected Typical Private Network Net Reactive Interchange |  | ADD 04/2012 |  | Private Network - Unit - ESG | ESG_PrivateNetwork.View | MVAR | ESGUNIT | NET_INTERCHNG_MVAR_UNIT
ESG | Private Network Gross Unit Capability |  | ADD 04/2012 |  | Private Network - Unit - ESG | ESG_PrivateNetwork.View | MW | ESGUNIT | GROSS_CAPBLTY_MW_UNIT
ESG | Private Network Gross Unit Reactive Capability |  | ADD 04/2012 |  | Private Network - Unit - ESG | ESG_PrivateNetwork.View | MWAR | ESGUNIT | GROSS_CAPBLTY_MVAR_UNIT
ESG | If Unit trips, does Load trip? |  | ADD 04/2012 |  | Private Network - Unit - ESG | ESG_PrivateNetwork.View | Y/N | ESGUNIT | LOAD_TRIP_FLG
ESG | If yes, approximate percentage of Load that will trip? | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Private Network -ESG | ESG_PrivateNetwork.View |  | ESGUNIT | LOAD_TRIP_PCT
Solar | Load Characteristics for MVAR Load |  |  |  | Private Network -Solar |  |  | Not in table | Not in table
Solar | Private Network - Unit - Solar |  |  |  | Private Network - Unit - Solar |  |  | Not in table | Not in table
Solar | GENERATOR DETAILS |  |  |  | Private Network - Unit - Solar |  |  | Not in table | Not in table
Solar | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 | Private Network - Unit - Solar | Private Network - Unit - Solar | Solar_PrivateNetwork.View | List | SITECODES | UNIT_NAME | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | 1. This field is not null. Data type: Character. | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Solar | SITE_CODE |  | ADD 04/2012 | Private Network - Unit - Solar | Private Network - Unit - Solar | Solar_PrivateNetwork.View | Automatic | SITECODES | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
Solar | Resource Name (Unit Code/Mnemonic) | Do not show Message on Audit or Delta | ADD 04/2012 | Private Network - Unit - Solar | Private Network - Unit - Solar | Solar_PrivateNetwork.View | Automatic | SITECODES | UNIT_CODE | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | Character | Lodestar
Solar | PRIVATE NETWORK - Unit Information |  |  |  | Private Network - Unit - Solar |  |  | Not in table | Not in table
Solar | Average Amount of Self-Serve private load |  | ADD 04/2012 |  | Private Network - Unit - Solar | Solar_PrivateNetwork.View | MW | SOLAR | AVG_LD_MW_UNIT
Solar | Average Amount of Self-Serve private reactive load |  | ADD 04/2012 |  | Private Network - Unit - Solar | Solar_PrivateNetwork.View | MVAR | SOLAR | AVG_LD_MVAR_UNIT
Solar | Expected Typical Private Network Net Interchange |  | ADD 04/2012 |  | Private Network - Unit - Solar | Solar_PrivateNetwork.View | MW | SOLAR | NET_INTERCHNG_MW_UNIT
Solar | Expected Typical Private Network Net Reactive Interchange |  | ADD 04/2012 |  | Private Network - Unit - Solar | Solar_PrivateNetwork.View | MVAR | SOLAR | NET_INTERCHNG_MVAR_UNIT
Solar | Private Network Gross Unit Capability |  | ADD 04/2012 |  | Private Network - Unit - Solar | Solar_PrivateNetwork.View | MW | SOLAR | GROSS_CAPBLTY_MW_UNIT
Solar | Private Network Gross Unit Reactive Capability |  | ADD 04/2012 |  | Private Network - Unit - Solar | Solar_PrivateNetwork.View | MVAR | SOLAR | GROSS_CAPBLTY_MVAR_UNIT
Solar | If Unit trips, does Load trip? |  | ADD 04/2012 |  | Private Network - Unit - Solar | Solar_PrivateNetwork.View | Y/N | SOLAR | LOAD_TRIP_FLG
Solar | If yes, approximate percentage of Load that will trip? | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Private Network - Unit - Solar | Solar_PrivateNetwork.View |  | SOLAR | LOAD_TRIP_PCT
Note on H6: This column represents the name of the SQL file/view that uses the field. The name is the same for Delta and Aufit reports unless otherwise noted. The full filename convention is dbo.[RARFAUDIT or DELTA].[Source Report Name].sql

## Sheet7 (hidden)
RARF FORM TYPE | RARF DATA FIELD |  | Field Updates | Change Description | RARF Tab | Source Report Name | Label | TABLE | DB Field | EXCEL | Business Rules/Basic UI validations | Field/ Tab Type | Data type
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | General and Site Information |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | This tab is Required for all Resource Entities (Load and Generation Resources) | R
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | This submittal is for |  | Updated 03/09/2012 validation rule to match view |  | General and Site Information |  |  | SITECODES | SUBMIT_REASON | Not null. Select from the list: New Site, Revision, Addition of Units, Deletion of Units | Not null. Select from the list: New Site, Revision, Addition of Unit(s), Deletion of Unit(s)* | R | Dropdown List
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Submittal Information |  |  |  | General and Site Information |  |  | Not in table | Not in table | Not null. Select from the list: New Site, Revision, Addition of Units, Deletion of Units | Not null. Select from the list: New Site, Revision, Addition of Units, Deletion of Units | R | Dropdown List
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Date Form Completed: |  |  |  | General and Site Information |  |  | SITECODES | FORM_COMP_DT | Optional | Not null. Equal to the System Date. Date Format should be mm/dd/yyyy | R | Date
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Resource Entity Submitting Form: |  | 03/09/2012 Updated Validation | ADD 04/2012 | General and Site Information | GeneralInformation.View |  | RE_RARF | RE_NAME | 1. Not null. 2. Name must match ERCOT records (SIEBEL) | 1.This field is not null. 2. All should be capital letters 3.No Special characters except spaces and dashes. | R | Character
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Resource Entity DUNS #: |  |  |  | General and Site Information |  |  | SITECODES & RE_RARF | RE_DUNS | 1. Not null. 2. DUNS number must match ERCOT records (SIEBEL) | Not null. Data type should be varchar (as sometimes the value contains # with a leading zero). Duns# is either 9 digit or 13 digit .Should match with RE Duns# IN Siebel | R | Character
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Site Information |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | This tab is Conditional: Required if the Generation Type is ' WIND or CC or GEN' , where GEN is non-cc non-wind generation resources. This tab is not required for Load Resources. | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Resource Site Name: |  |  |  | General and Site Information |  |  | SITECODES | SITE_NAME | 1. Not null. 2. Validate with ERCOT records (Lodestar). 3. All should be capital letters | 1.This field is not null. Validate with the existing record in ERCOT?? 2. All should be capital letters | R | Character
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Resource Site Code: |  | 05/02/2012 Updated Table that this field is mapped to, adding SITE_LOAD_SPLIT. |  | General and Site Information |  |  | SITECODES & SITE_LOAD_SPLIT | SITE_CODE | 1. Not null. 2. Validate with ERCOT records (Lodestar). 3. All should be capital letters | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R | Character
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Street Address: |  |  |  | General and Site Information |  |  | SITECODES | STREET_ADDRESS | Not null | Not null | R | Character
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | City: |  |  |  | General and Site Information |  |  | SITECODES | CITY | Not null | Not null | R | Character
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | State |  |  |  | General and Site Information |  |  | SITECODES | STATE | Not null | This is Required field (can not be null) Data type should be character, no numbers or commas are allowed. | R | Character
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Zip Code |  |  |  | General and Site Information |  |  | SITECODES | ZIPCODE | Not null | This is a Required field and can not be null. Only numbers are allowed | R | Number
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | County: |  |  |  | General and Site Information |  |  | SITECODES | COUNTY | Not null | Not null | R | Character
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Site In-Service Date: |  |  |  | General and Site Information |  |  | SITECODES | SITE_IN_SRVC_DT | 1. Must be earlier than Site-Stop Service Date. 2. mm/dd/yy format. 3. Not null. | Site-In Service Date is earlier than Site-Stop Service Date. Enter the date in mm/dd/yy format. This field is not null. | R | Date
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Site Stop Service Date: |  |  |  | General and Site Information |  |  | SITECODES | SITE_STOP_SRVC_DT | 1. Must be later than Site In-Service Date. 2. mm/dd/yy format. 3. Not null. | Site Stop Service Date should be later than Site-In Service Date. Format is mm/dd/yyy. This field is optional. NA is not valid , Leave it blank if not applicable. | O | Date
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Congestion Management Zone for 2003: |  |  |  | General and Site Information |  |  | SITECODES | CMZ_2003 | 1. Select from the list: North,South,Houston,West. 2. Not Null | Select from the list: North,South,Houston,West. This field is Required | O | Dropdown List
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Resource owned by NOIE? |  |  |  | General and Site Information |  |  | SITECODES | RE_OWNED_NOIE_FLG | 1. Select from the list: Y or N 2. Not Null | Select from the list: Y or N | R | Dropdown List
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Is Resource behind a NOIE Settlement Meter Point? |  |  |  | General and Site Information |  |  | SITECODES | RE_BHND_NOIE_SMP_FLG | 1. Select from the list: Y or N 2. Not Null | Select from the list: Y or N | R | Dropdown List
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Number of EPS Primary meters: |  |  |  | General and Site Information |  |  | SITECODES | NUM_EPS_METERS | Not null | This field is required and it should be an integer | R | Integer
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Is Resource claiming status as a Non-Modeled Generator as defined in ERCOT Protocol Section 2, Resource |  | 05/23/2012 Updated validation Rule 04/12/2012 Updated RARF TAB | ADD 04/2012 | Site Info - DG General Information - DG | DG_SiteInfo.View | Y/N | SITECODES | RE_CLAIM_NONMOD_STATUS |  | 1. If Site_Code is in NON_MODELED then If RE_CLAIM_NONMOD_STATUS is null then Error Else if RE_CLAIM_NONMOD_STATUS not Y or N, Error If Site_Code is NOT in NON_MODELED then do not validate | C | Dropdown List
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Is Resource >10 MW? |  | 05/23/2012 Updated validation Rule 04/12/2012 Updated RARF TAB | ADD 04/2012 | Site Info - DG General Information - DG | DG_SiteInfo.View | Y/N | SITECODES | RES_GREAT_TEN_MW |  | 1.If Site_Code is in NON_MODELED then If RE_CLAIM_NONMOD_STATUS is null then Error Else if RE_CLAIM_NONMOD_STATUS not Y or N, Error If Site_Code is NOT in NON_MODELED then do not validate . | C | Dropdown List
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Primary Contact (name of person ERCOT can contact with questions regarding this form) |  |  |  | General and Site Information |  |  | Not in table | Not in table
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Printed Name: |  |  |  | General and Site Information |  |  | SITECODES | NAME_PC | Not null | Not null. Validate that the Authorized rep has valid digital certificate to access the User Interface | R | Character
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Title: |  |  |  | General and Site Information |  |  | SITECODES | TITLE_PC | Not null | Not null | R | Character
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Phone Number: |  |  |  | General and Site Information |  |  | SITECODES | PHONE_PC | Not null | Not null | R | Character
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | E-mail Address: |  |  |  | General and Site Information |  |  | SITECODES | EMAIL_PC | Not null | Not null | R | Character
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Fax Number: |  |  |  | General and Site Information |  |  | SITECODES | FAX_PC | Optional | Optional | O | Character
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Secondary Contact (if available) |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | Optional
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Printed Name: |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | Optional
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Title: |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | Optional
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Phone Number: |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | Optional
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | E-mail Address: |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | Optional
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Fax Number: |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | Optional
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | GEN Load Split -ESIID |  |  |  | GEN Load Split -ESIID |  |  | Not in table | Not in table
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | GENERATION SITE LOAD DETAILS |  |  |  | GEN Load Split -ESIID |  |  | Not in table | Not in table
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | ESIID_NUMBER |  |  | ADD 02/2012 to RARF FORM | GEN Load Split - ESIID |  |  | SITE_LOAD_SPLIT | ESIID_NUMBER | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2. Must have minimum of 2 ESI ID's entered 3. Data type is character | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Generate ESIID Number + 1 (ex. ESIID_1, ESIID_2, ESIID_3)
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | SITECODE_ESIID |  |  | ADD 02/2012 to RARF FORM | GEN Load Split - ESIID |  |  | SITE_LOAD_SPLIT | SITECODE_ESIID | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2.Concantanate SITE_CODE and ESIID_NUMBER | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Concantanate SITECODE_ESIID_Number
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Generation Load Split? |  | Corrected 02/29/2012 |  | GEN Load Split - ESIID |  | Y/N | SITECODES | GEN_LOAD_SPLIT_FLG | 1.This field is conditional. Required only if Generation Load Split is 'N'. 2. Not Required of Resource Behind NOIE Settlement point is 'Y' 2. Data type is character | Select from the list: Y or N | R | Dropdown List
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | ERCOT Read Meter? |  |  |  | GEN Load Split - ESIID |  | Y/N | SITECODES | ERCOT_READ_FLG | 1. Select from the list: Y or N 2. Not Null | Select from the list: Y or N | R | Dropdown List
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | SITECODE |  | 05/02/2012 Removed from form, column remains but data will now be populated from SITECODE tab | ADD 02/2012 | GEN Load Split - ESIID |  | Automatic | SITECODES & SITE_LOAD_SPLIT | SITE_CODE | 1. Not null. 2. Validate with ERCOT records (Lodestar). 3. All should be capital letters | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R | Character
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | ESI ID: |  | 05/02/2012 Updated Validation Rule | UPDATE 02/2012 | GEN Load Split - ESIID |  |  | SITE_LOAD_SPLIT | ESI_ID |  | 1.Data type is character 2.If Generation Load Split is 'N', ESIID is required. 3. If Generation Load Split is 'Y' then If RE_BHND_NOIE_SMP_FLG is 'Y' and Site_Code is in NON_MODELED, then no ESIID is required else ESIID is required | C | Character
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | TDSP Providing Service To Resource: |  | Corrected |  | GEN Load Split - ESIID |  | List | SITE_LOAD_SPLIT | TDSP_PROVIDING_SVC | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Select From drop down list provided. | This field is conditional. Required only if If the Generation Load Split question is answered as 'N' . Validate with the existing record in ERCOT?? | C | Character
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | TDSP DUNS Number: |  | 03/09/2012 Updated Validation |  | GEN Load Split - ESIID |  | Automatic | SITE_LOAD_SPLIT | TDSP_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Prepopulated with DUNS of TDSP provided in cell above | 1. Not null 2. Must match with the data existing in Siebel 3. Data type: varchar (as sometimes the value contains # with a leading zero) 4. Either a 9 or 13 digit DUNS number | R | Integer
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Fixed Load Splitting % |  | 05/03/2012 removed percent from label on form |  | GEN Load Split - ESIID |  |  | SITE_LOAD_SPLIT | FIXED_LD_SPLIT | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2. Must have minimum of 2 ESI ID's entered | 1.This field is optional/conditional. Required only if Gen Site is split among multiple ESI Id's.If entered, cross check the data with Lodestar. 2. Sum of the Fixed Load Splitting % (corresponding to each ESIID) should be 100. Generate an error if the rule fails | C/O | Numeric
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Load Serving Entity |  |  |  | GEN Load Split - ESIID |  | List | SITE_LOAD_SPLIT | COMP_RETAILER | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Select From drop down list provided. | This field is optional/conditional. Required only if Gen Site is split among multiple ESI Id's. | C | Character
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Load Serving Entity Duns# |  |  |  | GEN Load Split - ESIID |  | Automatic | SITE_LOAD_SPLIT | COMP_RETAILER_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Prepopulated with DUNS of Competitive Retailer provided in cell above | This field is optional/conditional. Required only if Gen Site is split among multiple ESI Id's. If entered it should be either 9 or 13 digit number AND should match with the existing record in Lodestar? | C | Integer
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Private Network - Site |  |  |  | Private Network - Site |  |  | Not in table | Not in table
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | SITE DETAILS |  |  |  | Private Network - Site |  |  | Not in table | Not in table
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Private Network? |  | 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  | Y/N | SITECODES | PRIVATE_NTWK_SITE_FLG |  | Select from Y or N. Private Network Flag is not null | R | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms/Kittiepong
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | PRIVATE NETWORK - SITE INFORMATION |  |  |  | Private Network - Site |  |  | Not in table | Not in table |  | This tab is conditional : Required for all Private Use Networks |  | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Average Amount Of Self-serve Private Load |  | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  | MW | SITECODES | AVG_LD_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Average Amount Of Self-serve Private Reactive Load |  | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  | MVAR | SITECODES | AVG_LD_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Expected Typical Private Network Net Interchange |  | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  | MW | SITECODES | NET_INTERCHNG_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Expected Typical Private Network Net Reactive Interchange |  | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  | MVAR | SITECODES | NET_INTERCHNG_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Private Network Gross Unit Capability |  | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  | MW | SITECODES | GROSS_CAPBLTY_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Private Network Gross Unit Reactive Capability |  | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  | MVAR | SITECODES | GROSS_CAPBLTY_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Load Characteristics For MW Load |  |  |  | Private Network - Site |  |  | Not in table | Not in table |  | This tab is conditional : Required for all Private Use Networks |  | RARF Glossary Version 4.0/RARF Guide Version 4.0/RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Large Motor, Percent Of Total |  | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  |  | SITECODES | PUN_MW_LARGEMTR_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Small Motor, Percent Of Total |  | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  |  | SITECODES | PUN_MW_SMALLMTR_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Resistive (heating) Load, Percent Of Total MW Load |  | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  |  | SITECODES | PUN_MW_RESISTIVE_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Discharge Lighting, Percent Of Total |  | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  |  | SITECODES | PUN_MW_DISCHARGE_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Other, Percent Of Total MW Load |  | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  |  | SITECODES | PUN_MW_OTHER_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Load Characteristics for MVAR Load |  |  |  | Private Network - Site |  |  | Not in table | Not in table |  | This tab is conditional : Required for all Private Use Networks
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Large Motor, Percent Of Total MVAR Load |  | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  |  | SITECODES | PUN_MVAR_LARGEMTR_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Small Motor, Percent Of Total MVAR Load |  | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  |  | SITECODES | PUN_MVAR_SMALLMTR_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | R | Lin Xu
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Discharge Lighting, Percent Of Total MVAR Load |  | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  |  | SITECODES | PUN_MVAR_DISCHARGE_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR and ESG) | Other, Percent Of Total MVAR Load |  | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  | Private Network - Site |  |  | SITECODES | PUN_MVAR_OTHER_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Lin Xu
Wind | Unit Info - Wind |  |  |  | Unit Info - Wind |  |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type selected is 'WIND ' | C
Wind | GENERATOR DETAILS |  |  |  | Unit Info - Wind |  |  | Not in table | Not in table
Wind | Unit Name |  | Do not show Message on Audit or Delta |  | Unit Info - Wind |  | All Caps | WIND | UNIT_NAME | 1. Not Null. 2. Must not exceed 4 characters for Jointly Owned Units 3. Maximum of 8 character allowed | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character
Wind | Resource Name (Unit Code/Mnemonic) |  | 05/17/2012 Update #3 validation |  | Unit Info - Wind |  | Automatic | Wind | UNIT_CODE | 1. Not Null. 2. Enter Site Code and Unit Name for this field (Sitecode_Unit Name) 3. All letters must be capital | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters for split gen resources | R | Character
Wind | Non_Modeled Generator | Passed for flag not checked error on audit |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | Y/N | WIND | NON_MOD_GEN | 1.Select from the list: Y or N 2.Not Null | Select from the list: Y or N | R | Dropdown List |  | Done
Wind | PUC Registration Number |  |  |  | Unit Info - Wind |  |  | Wind | PUC_NUM | 1. Optional. | This field is optional and it should be a number. NA is not valid , Leave it blank if not applicable. | O | Integer
Wind | ERCOT Interconnection Project Number - only new units |  |  |  | Unit Info - Wind |  |  | Wind | ERCOT_INTRCONN_PROJ_NUM | 1. Required for new sites only | 1.This field is optional. Required only for new units. NA is not valid , Leave it blank if not applicable. 2. Cross check with the data entered in the field 'This submittal is for' in General Information Tab. If the value is 'New Site' then only this field is required. | O | Character
Wind | NERC Number |  |  |  | Unit Info - Wind |  |  | Wind | NERC_NUM | 1. Optional. | This field is optional. NA is not valid , Leave it blank if not applicable. | O | Character
Wind | Qualifying Facility |  |  |  | Unit Info - Wind |  | Y/N | Wind | QUAL_FACILITY_FLG | 1. Not null. 2. Select Y or N | Select from the list: Y or N. QF Flag is not null | R | Dropdown List
Wind | SITE AND UNIT DATES |  |  |  | Unit Info - Wind |  |  | Not in table | Not in table
Wind | Transmission Only Date (POI) |  |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | mm/dd/yyyy | WIND | TRANS_ONLY_DT | 1. Optional. 2. Format should be: MM/DD/YYYY | This field is optional. Format should be: MM/DD/YYYY | O | Date
Wind | Standard Generation Interconnection Agreement (SGIA) Signature Date | Passed for flag not checked error on audit |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | mm/dd/yyyy | WIND | SGIA_SIG_DT | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date. | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date. | R | Date | 1 Done
Wind | Unit Start Date (Model Ready Date) |  | 03/13/2012 Updated Validation | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | mm/dd/yyyy | WIND | UNIT_MRD_ST_DT | 1.This field is not null. Format should be: MM/DD/YYYY 2.Date should be Vaild Data Base Load Date 3.Unit Start Date should be >= Site Start Date ( Site-Information Tab) | This field is optional. Format should be: MM/DD/YYYY |  |  | 1. Done
Wind | Unit Commercial Date |  |  |  | Unit Info - Wind |  | mm/dd/yyyy | Wind | UNIT_START_DT | 1. Not null. 2. Format should be: MM/DD/YYYY 3. Must be equal to or greater than Site In-Service Date. | This field is not null. Format should be: MM/DD/YYYY Unit Start Date should be >= Site Start Date ( Site-Information Tab) | R | Date
Wind | Unit End Date |  |  |  | Unit Info - Wind |  | mm/dd/yyyy | Wind | UNIT_END_DT | 1. Not null. 2. Format should be: MM/DD/YYYY 3. Must be greater than Unit Start Date. | This field is optional. Format Should be: MM/DD/YYYY. NA is not valid , Leave it blank if not applicable. | O | Date
Wind | POINT OF INTERCONNECTION |  |  |  | Unit Info - Wind |  |  | Not in table | Not in table
Wind | SubStation Code/SubStation Mnemonic | Passed for flag not checked error on audit |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | All caps | Wind | SUBSTAT_CODE_SUB_MNEMONIC | 1) This field is not null (required). Data type must be Character. 2) Must match ERCOT records (unless new). Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" . 4) Must be <= 8 characters. Warning! Substation Code should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) Substation code should be in Upper case letters. Generate an error if the rule fails. | 1) This field is not null (required). Data type must be Character. 2) Must match ERCOT records (unless new). Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" . 4) Must be <= 8 characters. Warning! Substation Code should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) Substation code should be in Upper case letters. Generate an error if the rule fails. | R | Character | 1. Done
Wind | Voltage Level | Passed for flag not checked error on audit | 03/13/12 Updated | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | kV | Wind | VOL_LEV | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0. | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0. | R | Float | 1. Done
Wind | PTI Bus Number | Passed for flag not checked error on audit |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | # | Wind | PTI_BUS_NUM | 1) This field isnot null (required). Data type must be Integer. 2) The value must be > 0. | 1) This field isnot null (required). Data type must be Integer. 2) The value must be > 0. | R | Integer | 1. Done
Wind | FUEL INFORMATION |  |  |  | Unit Info - Wind |  |  | Not in table | Not in table
Wind | Renewable |  |  |  | Unit Info - Wind |  | Y/N | Wind | RENEWABLE_FLG | 1. Not null. 2. Select Y or N | Select from the list: Y or N. This field is not null | R | Dropdown List
Wind | Renewable/Offset |  |  |  | Unit Info - Wind |  | List | Wind | RENEWABLE_OFFSET | 1. Not null. 2. Select from the list | Select from the list : RN, OS, NA. This field is not null. | R | Dropdown List
Wind | Resource Category |  |  | UPDATE 02/2012 | Unit Info - Wind |  | List | Wind | RES_CATG | 1. Not null. 2. Select from the list WGR, OT. | 1.Resource Category is not null. 2.Select from the list: Wind Generation Resource and OT | R | Dropdown List
Wind | RATINGS AND DESIGNS |  |  |  | Unit Info - Wind |  |  | Not in table | Not in table
Wind | Physical Unit Type |  | Updated Validation 03/28/2012 | UPDATE 02/2012 | Unit Info - Wind |  | List | Wind | PHYS_UNIT_TYPE | Select from the list: OT, WT not null. | Select from the list: WT, OT | R | Dropdown List
Wind | Name Plate Rating |  |  |  | Unit Info - Wind |  | MVA | Wind | NAME_PLT_RTG | 1. Name Plate Rating must be >= Real Power Rating | Name Plate Rating should be >= Real Power Rating | R | Numeric
Wind | Real Power Rating |  |  |  | Unit Info - Wind |  | MW | Wind | RTG_MW | 1. Real Power Rating must be > Reactive Power Rating | Real Power Rating should be > Reactive Power Rating | R | Numeric
Wind | Reactive Power Rating |  |  |  | Unit Info - Wind |  | MVAR | Wind | RTG_MVAR | 1. Reactive Power Rating must be <= Name Plate Rating | Name Plate Rating should be >= Reactive Power Rating | R | Numeric
Wind | Unit Generating Voltage |  |  |  | Unit Info - Wind |  | kV | Wind | UNIT_KV | 1. Numeric entry only 2. Not null. | Data type is Numeric. Unit Generating voltage can not be below 4.16 KV | R | Numeric
Wind | Governor Droop Setting | Passed for flag not checked error on audit | 05/03/2012 removed percent from label on form | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View |  | Wind | GOV_DROOP |  | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if it is not between 0 and 25. Generate Warning if > 5 (protocol requirement). | R | Numeric | 1. Done
Wind | Governor Dead-Band | Passed for Validation Rule 1 and 3 |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | Hz | Wind | GOV_DEAD_BND |  | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if > 0.1. Generate Warning if > 0.03. | R | Numeric | 1. Done
Wind | Design Max Ambient Temperature |  |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | Degree F | Wind | DESIGN_MAX_AMB_TEMP |  | >100 <150
Wind | Design Min Ambient Temperature |  |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | Degree F | Wind | DESIGN_MIN_AMB_TEMP |  | >-100 <32
Wind | METEOROLOGICAL TOWER AND INSTRUMENTATION INFORMATION |  |  |  | Unit Info - Wind |  |  | Not in table | Not in table
Wind | Average Height Above Ground Of Turbine Hub |  |  |  | Unit Info - Wind |  | Meters | Wind | AVG_HGHT_ABV_GRND | 1. Not null. | This field is not null and it should be a number | R | Numeric
Wind | Latitude of Meteorological Tower |  |  |  | Unit Info - Wind |  | decimal degrees(N) | Wind | LAT_METG_TOWER | 1. Not null. | 1. This field is not null. Data type must be Float 2. Latitude of Meteorological Tower : Must be <= 90 decimal degrees | R | Numeric
Wind | Longitude of Meteorological Tower |  |  |  | Unit Info - Wind |  | decimal degrees(W) | Wind | LONG_METG_TOWER | 1. Not null. | 1. This field is not null. Data type must be Float 2.Longitude of Meteorological Tower: Must be <= 180 decimal degrees | R | Numeric
Wind | Height of Meteorological Instrumentation - Wind Speed | Passed for flag not checked error on audit |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | Meters | Wind | HGT_MET_TWR_WND_SPD |  | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Float | 1. Done
Wind | Height of Meteorological Instrumentation - Wind Direction | Passed for flag not checked error on audit |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | Meters | Wind | HGT_MET_TWR_WND_DIRT |  | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Float | 1. Done
Wind | Height of Meteorological Instrumentation - Barometric Pressure | Passed for flag not checked error on audit |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | Meters | Wind | HGT_MET_TWR_BAR_PRES |  | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Float | 1. Done
Wind | Height of Meteorological Instrumentation - Temperature | Passed for flag not checked error on audit |  | ADD 04/2012 | Unit Info - Wind | Wind_UnitInfo.View | Meters | Wind | HGT_MET_TWR_TEMP |  | 1) This field is not null (required). Data type must be Float. 2) The value must be > 0. | R | Float | 1. Done
Wind | GEOGRAPHIC LOCATION (CENTER OF PLANT) |  |  |  | Unit Info - Wind |  |  | Not in table | Not in table
Wind | Latitude Of Center Of Plant |  |  | UPDATE 02/2012 | Unit Info - Wind |  | decimal degrees(N) | Wind | LAT_CTR_WNDFARM | 1. Not null. | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if Latitude < 25.0 or > 37.0.
Wind | Longitude Of Center Of Plant |  |  | UPDATE 02/2012 | Unit Info - Wind |  | decimal degrees(W) | Wind | LONG_CTR_WNDFARM | 1. Not null. | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if <93 or > 107 .
Wind | Unit Info - Wind Turbine |  |  |  | Unit Info -Wind Turbine |  |  | Not in table | Not in table
Wind | GENERATOR DETAILS |  |  |  | Unit Info -Wind Turbine |  |  | Not in table | Not in table
Wind | Resoure Name (Unit Code/Mnemonic) |  |  | ADD 02/2012 | Unit Info -Wind Turbine |  | Automatic | Wind | UNIT_CODE | 1. Not Null. 2. Enter Site Code and Unit Name for this field (Sitecode_Unit Name) 3. All letters must be capital | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character
Wind | TURBINE DETAILS |  |  |  | Unit Info -Wind Turbine |  |  | Not in table | Not in table
Wind | Type of Turbine (Manufacturer/Model) |  |  |  | Unit Info -Wind Turbine |  |  | Wind | TUR_TYPE | 1. Not null. | This field is not null and the Data type should be character. | R | Character
Wind | MW Rating for this model of Turbine |  |  |  | Unit Info -Wind Turbine |  | MW | Wind | TUR_MW_MDL_RTG | 1. Not null. | This field is not null and the Data type should be Numeric | R | Numeric
Wind | Number of this type of Turbine |  |  |  | Unit Info -Wind Turbine |  | # | Wind | TUR_NUM | 1. Not null. | This field is not null and it should be an integer | R | Numeric
Wind | Ownership - WIND |  |  |  | Ownership - WIND |  |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type selected is 'WIND ' | C
Wind | GENERATOR DETAILS |  |  |  | Ownership - WIND |  |  | Not in table | Not in table
Wind | Unit Name |  | Do not show Message on Audit or Delta | ADD 02/2012 | Ownership - WIND |  | List | WIND | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character
Wind | Resource Name (Unit Code/Mnemonic) |  |  | ADD 02/2012 | Ownership - WIND |  | Automatic | OWNERSHIP & SITECODES | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character
Wind | OWNERSHIP PERCENTAGES |  |  |  | Ownership - WIND |  |  | Not in table | Not in table
Wind | Joint Ownership? |  |  | ADD 04/2012 | Ownership - WIND | WIND_Ownership.View | Y/N | OWNERSHIP | J0CODE |  | 1. Select from the list: Y or N 2. If N then Fixed Ownership 100% | R | Dropdown List
Wind | Resource Entity Name |  |  |  | Ownership - WIND |  |  | OWNERSHIP | MKT_PRTCPT |  | This field is conditional: Required if single entity represents the Resource. Data type: Character. Resource Entity Name should not allow any special characters except spaces. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | C | Character
Wind | Resource Duns Number |  |  |  | Ownership - WIND |  | 9-13 digits | OWNERSHIP | MKT_PRTCPT_DUNS |  | This field is Conditional : Required if single entity represents the Resource. This should be either 9 or 13 digit number | C | Integer
Wind | Fixed Ownership |  | 05/03/2012 removed percent from label on form |  | Ownership - WIND |  |  | OWNERSHIP | FIX_OWNRSHP_PCT |  | Sum of the Ownership percentage should be 100. Up to 4 decimal places are valid (limit submission to 4 places after the point) | C | Numeric
Wind | Master Owner |  |  |  | Ownership - WIND |  | Y/N | OWNERSHIP | MASTR_OWNR_FLG |  | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | R | Dropdown List
Wind | Ownership Start Date |  | 04/09/2012 Changed Validation to be an Optional | ADD 04/2012 | Ownership - Wind | WIND_Ownership.View | mm/dd/yyyy | OWNERSHIP | OWNR_START_DT |  | Format should be: MM/DD/YYYY | O | Date
Wind | Ownership Stop Date |  |  | ADD 04/2012 | Ownership - Wind | WIND_Ownership.View | mm/dd/yyyy | OWNERSHIP | OWNR_END_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date
Wind | Parameters - WIND |  |  |  | Parameters - Wind |  |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type selected is 'WIND ' | C
Wind | GENERATOR DETAILS |  |  |  | Parameters - Wind |  |  | Not in table | Not in table
Wind | Unit Name |  | Do not show Message on Audit or Delta | ADD 02/2012 | Parameters - Wind |  | List | WIND | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character
Wind | Resource Name (Unit Code/Mnemonic) |  | 04/23/2012 Updated Table to DERATING_WIND | ADD 02/2012 | Parameters - Wind |  | Automatic | WIND & DERATING_WIND | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character
Wind | REASONABILITY LIMITS |  |  |  | Parameters - Wind |  |  | Not in table | Not in table
Wind | High Reasonability Limit |  |  | UPDATE 02/2012 | Parameters - Wind |  | MW | WIND | HR_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit | R | Numeric
Wind | Low Reasonability Limit |  |  | UPDATE 02/2012 | Parameters - Wind |  | MW | WIND | LR_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | Numeric
Wind | High Reasonability Ramp Rate Limit |  |  | UPDATE 02/2012 | Parameters - Wind |  | MW/min | WIND | HR_RAMPRATE_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | Numeric
Wind | Low Reasonability Ramp Rate Limit |  |  | UPDATE 02/2012 | Parameters - Wind |  | MW/min | WIND | LR_RAMP_RATE_LMT |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | Numeric
Wind | SEASONAL RATINGS - SPRING |  |  |  | Parameters - Wind |  |  | Not in table | Not in table
Wind | Seasonal Net Max Sustainable Rating - Spring |  |  | UPDATE 02/2012 | Parameters - Wind |  | MW | WIND | SEASON_NET_MAX_SUST_RTG_SP |  | 1.Seasonal Net Max Sustainable Rating - Spring > Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Numeric
Wind | Seasonal Net Min Sustainable Rating - Spring |  |  | UPDATE 02/2012 | Parameters - Wind |  | MW | WIND | SEASON_NET_MIN_SUST_RTG_SP |  | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Numeric
Wind | Seasonal Net Max Emergency Rating - Spring |  |  | UPDATE 02/2012 | Parameters - Wind |  | MW | WIND | SEASON_NET_MAX_EMGY_RTG_SP |  | 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Numeric
Wind | Seasonal Net Min Emergency Rating - Spring |  |  | UPDATE 02/2012 | Parameters - Wind |  | MW | WIND | SEASON_NET_MIN_EMGY_RTG_SP |  | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Numeric
Wind | SEASONAL RATINGS - SUMMER |  |  |  | Parameters - Wind |  |  | Not in table | Not in table
Wind | Seasonal Net Max Sustainable Rating - Summer |  |  | UPDATE 02/2012 | Parameters - Wind |  | MW | WIND | SEASON_NET_MAX_SUST_RTG_SM |  | 1.Seasonal Net Max Sustainable Rating - Summer > Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Numeric
Wind | Seasonal Net Min Sustainable Rating - Summer |  |  | UPDATE 02/2012 | Parameters - Wind |  | MW | WIND | SEASON_NET_MIN_SUST_RTG_SM |  | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit | R | Numeric
Wind | Seasonal Net Max Emergency Rating - Summer |  |  | UPDATE 02/2012 | Parameters - Wind |  | MW | WIND | SEASON_NET_MAX_EMGY_RTG_SM |  | 1.Seasonal Net Max Emergency Rating - Summer > Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Numeric
Wind | Seasonal Net Min Emergency Rating - Summer |  |  | UPDATE 02/2012 | Parameters - Wind |  | MW | WIND | SEASON_NET_MIN_EMGY_RTG_SM |  | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Numeric
Wind | SEASONAL RATINGS - FALL |  |  |  | Parameters - Wind |  |  | Not in table | Not in table
Wind | Seasonal Net Max Sustainable Rating - Fall |  |  | UPDATE 02/2012 | Parameters - Wind |  | MW | WIND | SEASON_NET_MAX_SUST_RTG_FL |  | 1.Seasonal Net Max Sustainable Rating - Fall > Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Numeric
Wind | Seasonal Net Min Sustainable Rating - Fall |  |  | UPDATE 02/2012 | Parameters - Wind |  | MW | WIND | SEASON_NET_MIN_SUST_RTG_FL |  | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall. >= Low Reasonability Limit | R | Numeric
Wind | Seasonal Net Max Emergency Rating - Fall |  |  | UPDATE 02/2012 | Parameters - Wind |  | MW | WIND | SEASON_NET_MAX_EMGY_RTG_FL |  | 1.Seasonal Net Max Emergency Rating - Fall > Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Numeric
Wind | Seasonal Net Min Emergency Rating - Fall |  |  | UPDATE 02/2012 | Parameters - Wind |  | MW | WIND | SEASON_NET_MIN_EMGY_RTG_FL |  | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Numeric
Wind | SEASONAL RATINGS - WINTER |  |  |  | Parameters - Wind |  |  | Not in table | Not in table
Wind | Seasonal Net Max Sustainable Rating - Winter |  |  | UPDATE 02/2012 | Parameters - Wind |  | MW | WIND | SEASON_NET_MAX_SUST_RTG_WT |  | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Numeric
Wind | Seasonal Net Min Sustainable Rating - Winter |  |  | UPDATE 02/2012 | Parameters - Wind |  | MW | WIND | SEASON_NET_MIN_SUST_RTG_WT |  | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric
Wind | Seasonal Net Max Emergency Rating - Winter |  |  | UPDATE 02/2012 | Parameters - Wind |  | MW | WIND | SEASON_NET_MAX_EMGY_RTG_WT |  | 1.Seasonal Net Max Emergency Rating - Winter > Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Numeric
Wind | Seasonal Net Min Emergency Rating - Winter |  |  | UPDATE 02/2012 | Parameters - Wind |  | MW | WIND | SEASON_NET_MIN_EMGY_RTG_WT |  | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric
Wind | UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES |  |  |  | Parameters - Wind |  |  | Not in table | Not in table
Wind | 0°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
Wind | 5°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
Wind | 10°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R
Wind | 15°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 20°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 25°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 30°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 35°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 40°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 45°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 50°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 55°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 60°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 65°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 70°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 75°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 80°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 85°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 90°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 95°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 100°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 105°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 110°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 115°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | 120°f | Passed for value not being entered. error on audit | 04/23/2012 Updated Table to DERATING_WIND 03/09/2012 Updated Validation | ADD 04/2012 | Parameters - Wind | Parameters_WIND.View | MW | DERATING_WIND | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric | R |  | 1. Done
Wind | Operational Parameters - WIND |  |  |  | Operational Parameters - Wind |  |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Resource Type Selected is 'WIND units' | C
Wind | GENERATOR DETAILS |  |  |  | Operational Parameters - Wind |  |  | Not in table | Not in table
Wind | Unit Name |  | Do not show Message on Audit or Delta | ADD 02/2012 | Operational Parameters - Wind |  | List | WIND | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character
Wind | Resource Name (Unit Code/Mnemonic) |  |  | ADD 02/2012 | Operational Parameters - Wind |  | Automatic | WIND | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | Character
Wind | RESOURCE PARAMETERS |  |  |  | Operational Parameters - Wind |  |  | Not in table | Not in table
Wind | Minimum On Line Time |  | Check | UPDATE 02/2012 | Operational Parameters - Wind |  | hours | WIND | MIN_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum On Line Time >= 0 | R | Integer
Wind | Minimum Off Line Time |  | Check | UPDATE 02/2012 | Operational Parameters - Wind |  | hours | WIND | MIN_OFFLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum Off Line Time >= 0 | R | Integer
Wind | Hot Start Time |  | Corrected | UPDATE 02/2012 | Operational Parameters - Wind |  | hours | WIND | HOTSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot Start Time >= 0 3. Hot Start Time <= Intermediate Start Time | O | Integer
Wind | Intermediate Start Time |  | Corrected | UPDATE 02/2012 | Operational Parameters - Wind |  | hours | WIND | INTERMSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate Start Time >= 0 3. Cold Start Time >= Intermediate Start Time >= Hot Start Time | O | Integer
Wind | Cold Start Time |  | Corrected | UPDATE 02/2012 | Operational Parameters - Wind |  | hours | WIND | COLDSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Cold Start Time >= 0 3. Cold Start Time >= Intermediate Start Time | O | Integer
Wind | Max Weekly Starts |  | Check | UPDATE 02/2012 | Operational Parameters - Wind |  |  | WIND | MAXWKLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Integer
Wind | Max On Line Time |  | Corrected | UPDATE 02/2012 | Operational Parameters - Wind |  | hours | WIND | MAX_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Max OnLine Time > 0 | R | Integer
Wind | Max Daily Starts |  | Check | UPDATE 02/2012 | Operational Parameters - Wind |  |  | WIND | MAXDLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Daily Start >= 0 3. Max Daily Start <= 999 | R | Integer
Wind | Max Weekly Energy |  | Corrected | UPDATE 02/2012 | Operational Parameters - Wind |  | MWh | WIND | MAXWKLYENRGY |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Energy >= 0 3. Max Weekly Energy < 1e10 | R | Numeric
Wind | Hot-to-Intermediate Time |  | Check | UPDATE 02/2012 | Operational Parameters - Wind |  | hours | WIND | HOT_TO_INTMDT_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot-to-Intermediate Time >= 0 | R | Integer
Wind | Intermediate-to-Cold Time |  | Check | UPDATE 02/2012 | Operational Parameters - Wind |  | hours | WIND | INTMDT_TO_COLD_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate-to-Cold Time >= 0 | R | Integer
Wind | Operational Parameters - Wind - NRRC |  |  |  | Operational Parameters - Wind - NRRC |  |  | Not in table | Not in table
Wind | GENERATOR DETAILS |  |  |  | Operational Parameters - Wind - NRRC |  |  | Not in table | Not in table
Wind | Unit Name |  | Do not show Message on Audit or Delta | ADD 02/2012 | Operational Parameters - Wind - NRRC |  | List | WIND | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character
Wind | Resource Name (Unit Code/Mnemonic) |  |  | ADD 02/2012 | Operational Parameters - Wind - NRRC |  | List | RAMP_RATES_NRRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character
Wind | NORMAL RAMP RATE CURVE |  |  |  | Operational Parameters - Wind - NRRC |  |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit.
Wind | MW Number |  |  |  | Operational Parameters - Wind - NRRC |  | List | RAMP_RATES_NRRC | MW_NUMBER_NRRC
Wind | NRRC Code |  |  | UPDATE 02/2012 | Operational Parameters - Wind - NRRC |  | Automatic | RAMP_RATES_NRRC | UNIT_MW_NRRC |  | Capture Unit Code and UNIT MW Number and NRRC, prepopulate this field with UNIT_CODE_UNIT_MW_NUMBER_NRRC. | R | Character
Wind | NRRC MW |  | PHASE II Updated 03/06/2012 Added Step 5 and 6 | UPDATE 02/2012 | Operational Parameters - Wind - NRRC |  | MW | RAMP_RATES_NRRC | MW_RATING_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric
Wind | Upward Ramprate |  | Check | UPDATE 02/2012 | Operational Parameters - Wind - NRRC |  | MW/min | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric
Wind | Downward Ramprate |  | Check | UPDATE 02/2012 | Operational Parameters - Wind - NRRC |  | MW/min | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric
Wind | Operational Parameters - Wind - ERRC |  |  |  | Operational Parameters - Wind - ERRC |  |  | Not in table | Not in table
Wind | GENERATOR DETAILS |  |  |  | Operational Parameters - Wind - ERRC |  |  | Not in table | Not in table
Wind | Unit Name |  | Do not show Message on Audit or Delta | ADD 02/2012 | Operational Parameters - Wind - ERRC |  | List | WIND | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character
Wind | Resource Name (Unit Code/Mnemonic) |  |  | ADD 02/2012 | Operational Parameters - Wind - ERRC |  | List | RAMP_RATES_ERRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character
Wind | EMERGENCY RAMP RATE CURVE |  |  |  | Operational Parameters - Wind - ERRC |  |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit.
Wind | MW Number |  |  |  | Operational Parameters - Wind - ERRC |  | List | RAMP_RATES_ERRC | MW_NUMBER_ERRC
Wind | ERRC Code |  |  | UPDATE 02/2012 | Operational Parameters - Wind - ERRC |  | Automatic | RAMP_RATES_ERRC | UNIT_MW_ERRC |  | Capture Unit Code and Unit MW Number and prepopulate this field with Unit CODE_UNIT_MW_NUMBER_ERRC. | R | Character
Wind | ERRC MW |  | PHASE II Updated 03/06/2012 Added Step 5 and 6 | UPDATE 02/2012 | Operational Parameters - Wind - ERRC |  | MW | RAMP_RATES_NRRC | MW_RATING_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Numeric
Wind | Upward Ramprate |  | Check | UPDATE 02/2012 | Operational Parameters - Wind - ERRC |  | MW/min | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric
Wind | Downward Ramprate |  | Check | UPDATE 02/2012 | Operational Parameters - Wind - ERRC |  | MW/min | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Numeric
Wind | Reactive Capability - WIND |  |  |  | Reactive Capability - Wind |  |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type selected is 'WIND '. If the Unit Info-Wind tab shows multiple groups of turbines in a Unit, then the Reactive Curve tab must show the values for multiple groups, Produce an error if the corresponding data is missing in the Reactive Capability-Wind Tab. | C
Wind | GENERATOR DETAILS |  |  |  | Reactive Capability - Wind |  |  | Not in table | Not in table
Wind | Resource Name (Unit Code/Mnemonic) |  |  | ADD 02/2012 | Reactive Capability - Wind |  | Automatic | REACT_CAP_WIND | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character
Wind | REACTIVE CAPABILITY CURVES DETAILS |  |  |  | Reactive Capability - Wind |  |  | Not in table | Not in table
Wind | Reactive Capability Data Provided Below Is Gross/Net Values? | Passed for flag not checked error on audit | 04/02/2012 - Updated RARF Field Name, DB Field and removed Net from Drop down List in data Validation | ADD 04/2012 | Reactive Capability - Wind | Wind_ReactiveCapability.View | List | REACT_CAP_WIND | REACT_CAPB_DATA_GROSS_NET_VAL |  | Select from the list: GROSS |  | Dropdown List | 1. Done
Wind | Reactive Capability Data Provided is from NDCRC Test Data? | Passed for flag not checked error on audit |  | ADD 04/2012 | Reactive Capability - Wind | Wind_ReactiveCapability.View | Y/N | REACT_CAP_WIND | REACT_CAPB_NDCRC_TEST_DATA |  | Select from the list: Y or N |  | Dropdown List | 1. Done
Wind | If Reactive Capability Data Provided Is From NDCRC test Data Then Enter The Date On Which The Test Was Performed. |  |  | ADD 04/2012 | Reactive Capability - Wind | Wind_ReactiveCapability.View | mm/dd/yyyy | REACT_CAP_WIND | REACT_CAPB_NDCRC_TEST_DATA_DT |  | This field is optional. Format should be: MM/DD/YYYY | O | Date | 1. Done
Wind | Mw1 |  |  |  | Reactive Capability - Wind |  | MW | REACT_CAP_WIND | MW1 |  | 1. MW1 >=0.1 2.MW1<MW2. 3. X(1) <= WMN(Unit Minimal output or LRL) where X(1) represents MW1( Generate a Warning Only when this rule fails). This is a WARNING ONLY | R | Numeric
Wind | Lagging MVAR Limit Associated With Mw1 Output |  |  |  | Reactive Capability - Wind |  | MVAR | REACT_CAP_WIND | MVAR1LAG |  | 1. Lagging MVAR limit associated with MW1 output >=0. Generate a Warning only if LAG value is negative 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3) Generate a Warning only if LAG value is negative 4) Lagging MVAR must always be greater than the Leading MVAR | R | Numeric
Wind | Leading MVAR Limit Associated With Mw1 Output |  |  |  | Reactive Capability - Wind |  | MVAR | REACT_CAP_WIND | MVAR1LEAD |  | 1. Leading MVAR limit associated with MW1 output <=0 .Generate a Warning only if LEAD value is positive 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3) Generate a Warning only if LEAD value is positive | R | Numeric
Wind | Mw2 |  |  |  | Reactive Capability - Wind |  | MW | REACT_CAP_WIND | MW2 |  | 1. MW2 >0 2. MW2<MW3 | R | Numeric
Wind | Lagging MVAR Limit Associated With Mw2 Output |  |  |  | Reactive Capability - Wind |  | MVAR | REACT_CAP_WIND | MVAR2LAG |  | 1. Lagging MVAR limit associated with MW2 output >=0 . Generate a Warning only if LAG value is negative 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Generate a Warning only if LAG value is negative 4. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric
Wind | Leading MVAR Limit Associated With Mw2 Output |  |  |  | Reactive Capability - Wind |  | MVAR | REACT_CAP_WIND | MVAR2LEAD |  | 1.Leading MVAR limit associated with MW2 output <=0 .Generate a Warning only if LEAD value is positive 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Generate a Warning only if LEAD value is positive | R | Numeric
Wind | Mw3 |  |  |  | Reactive Capability - Wind |  | MW | REACT_CAP_WIND | MW3 |  | 1. MW3 >0 2.MW3<MW4 | R | Numeric
Wind | Lagging MVAR Limit Associated With Mw3 Output |  |  |  | Reactive Capability - Wind |  | MVAR | REACT_CAP_WIND | MVAR3LAG |  | 1Lagging MVAR limit associated with MW3 output >=0 .Generate a Warning only if LAG value is negative 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Generate a Warning only if LAG value is negative 4.Lagging MVAR must always be greater than the Leading MVAR | R | Numeric
Wind | Leading MVAR Limit Associated With Mw3 Output |  |  |  | Reactive Capability - Wind |  | MVAR | REACT_CAP_WIND | MVAR3LEAD |  | 1. Leading MVAR limit associated with MW3 output <=0 .Generate a Warning only if LEAD value is positive 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Generate a Warning only if LEAD value is positive | R | Numeric
Wind | Mw4 |  |  |  | Reactive Capability - Wind |  | MW | REACT_CAP_WIND | MW4 |  | 1. MW4<MW5 2. X(n) > = WMX (Unit Max output or HRL), where n is the last MW value in the curve. If the curve has 4 points, X(n) is X(4) [ Generate an Error When this rule fails. 3)For wind units that have multiple groups of turbines, Produce a Warning Only when the rule#2 fails (MW4 should be >= HRL) . For Units that have single group of turbine, produce an Error when the rule fails (MW4 should be >= HRL) | R | Numeric
Wind | Lagging MVAR Limit Associated With Mw4 Output |  |  |  | Reactive Capability - Wind |  | MVAR | REACT_CAP_WIND | MVAR4LAG |  | 1. Lagging MVAR limit associated with MW4 output >=0.Generate a Warning only if LAG value is negative 2. Lagging MVAR must always be greater than the Leading MVAR | R | Numeric
Wind | Leading MVAR Limit Associated With Mw4 Output |  |  |  | Reactive Capability - Wind |  | MVAR | REACT_CAP_WIND | MVAR4LEAD |  | Leading MVAR limit associated with MW3 output <=0 .Generate a Warning only if LEAD value is positive | R | Numeric
Wind | Maximum Lagging Operating Capability (MVAR) |  |  |  | Reactive Capability - Wind |  | MVAR | REACT_CAP_WIND | NETMAXLAG |  | Net Maximum Lagging Operating Capability >=0 | R | Numeric
Wind | Maximum Leading Operating Capability (MVAR) |  |  |  | Reactive Capability - Wind |  | MVAR | REACT_CAP_WIND | NETMAXLEAD |  | Net Maximum Leading Operating Capability <=0 | R | Numeric
Wind | Manufacturer's Capability Curve Submitted? |  |  |  | Reactive Capability - Wind |  | Y/N | REACT_CAP_WIND | MFR_CAP_CURVE |  | Select from Y or N | R | Dropdown List
Wind | Planning - WIND |  |  |  | Planning - Wind |  |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type selected is 'WIND '.This tab is unit specific and is required for all wind units. All the fields in this tab should be required. For all the UNITS in the Unit info-WIND tab , there should be corresponding data in Planning-WIND Tab | C
Wind | Unit Name |  | Do not show Message on Audit or Delta | ADD 02/2012 | Planning - Wind |  | List | WIND | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character
Wind | Type of Turbine |  | Corrected DB_FIELD 03/01/2012 | ADD 02/2012 | Planning - Wind |  | List | WIND | TUR_TYPE |  | Dropdown list | R | Dropdown list
Wind | PLANNING DETAILS |  |  |  | Planning - Wind |  |  | Not in table | Not in table
Wind | What is the Mva Base That the Following Data Is Based On? |  |  |  | Planning - Wind |  | MVA | WIND | MVABASE |  | 1) This field is required 2) Value must be Float 3) Generate a Warning if MVABASE > 2500 4)[ If MVABASE value is within +/- 25% range of Unit Name Plate Rating] OR [MVABASE value = 100, then it is OK.If MVABASE value is outside the +/- 25% range of Unit Name Plate Rating, then Generate a Warning that the MVABSE is outside the typical +/- 25% variation of unit name plate rating | R | Float
Wind | What Is The Kv Base That The Following Data Is Based On? |  |  |  | Planning - Wind |  | KV | WIND | KVBASE |  | 1) This field is required 2) Value must be >0 and <1000 3) Generate a Warning if KVBASE>40 4) If KVBASE value is within +/- 25% range of Unit KV value in the unit-information tab then it is OK.If If KVBASE value is outside the typical +/- 25% variation of Unit KV value in the unit-information tab then Generate a Warning that the KVBASE is outside the typical +/- 25% variation of Unit KV value | R | Float
Wind | Direct Axis Subtransient Reactance, X"di (unsaturated) |  |  |  | Planning - Wind |  | p.u. | WIND | DIRECT_AXIS_SUBSTNT_REACTANCE |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float
Wind | Direct Axis Transient Reactance, X'di (unsaturated) |  |  |  | Planning - Wind |  | p.u. | WIND | DIRECT_AXIS_TRANSNT_REACTANCE |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float
Wind | Positive Sequence Z (unsaturated) |  |  |  | Planning - Wind |  | R in p.u. | WIND | POSITIVE_SEQ_Z_R_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1
Wind | Positive Sequence Z (unsaturated) |  |  |  | Planning - Wind |  | X in p.u. | WIND | POSITIVE_SEQ_Z_X_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Wind | Negative Sequence Z (unsaturated) |  |  |  | Planning - Wind |  | R in p.u. | WIND | NEGATIVE_SEQ_Z_R_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1
Wind | Negative Sequence Z (unsaturated) |  |  |  | Planning - Wind |  | X in p.u. | WIND | NEGATIVE_SEQ_Z_X_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Wind | Does Zero Sequence Z exist? | Passed for flag not checked error on audit |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | Y/N | Wind | DOES_ZERO_SEQ_EXIST |  | Drop down list select Y/N | R | Dropdown List
Wind | Zero Sequence Z (unsaturated) |  |  |  | Planning - Wind |  | R in p.u. | WIND | ZERO_SEQ_Z_R_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 . Generate a Warning when value is > 1.0 P.U
Wind | Zero Sequence Z (unsaturated) |  |  |  | Planning - Wind |  | X in p.u. | WIND | ZERO_SEQ_Z_X_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Wind | Direct Axis Subtransient Reactance, X"dv (saturated) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | 1. Done
Wind | Direct Axis Transient Reactance, X'dv (saturated) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | 1. Done
Wind | Positive Sequence Z (saturated) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | R in p.u. | WIND | POSITIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | 1. Done
Wind | Positive Sequence Z (saturated) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | X in p.u. | WIND | POSITIVE_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | R | Float | 1. Done
Wind | Negative Sequence Z (saturated) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | R in p.u. | WIND | NEGATIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | R | Float | 1. Done
Wind | Negative Sequence Z (saturated) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | X in p.u. | WIND | NEGATIVE_SEQ_Z_X-SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | 1. Done
Wind | Zero Sequence Z (saturated) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | R in p.u. | WIND | ZERO_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U | R | Float | 1. Done
Wind | Zero Sequence Z (saturated) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | X in p.u. | WIND | ZERO_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R | Float | 1. Done
Wind | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  | 1. Done
Wind | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  | 1. Done
Wind | Zero Sequence Resistance In P.u. (100 Mva Base) |  | 04/24/2012 Remove field from database and form. No validation. | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | ZERO_SEQ_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  | 1. Done
Wind | Zero Sequence Reactance In P.u. (100 Mva Base) |  | 04/24/2012 Remove field from database and form. No validation. | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | ZERO_SEQ_Reactance_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  | 1. Done
Wind | GENERATOR AUXILIARY LOAD |  |  |  | Planning - Wind |  |  | Not in table | Not in table
Wind | Average Amount Of Auxiliary Real Power |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | MW | WIND | AUX_MWTOTAL |  | 1) This field is optional 2) Data type is float 3) Value must be < Parameters - GEN - High Reasonability Limit 4) Warn if value > (High Reasonability Limit) * .75 5) Error if value > (High Reasonability Limit) * .66 | R | Float | 1. Done
Wind | Average Amount Of Auxiliary Reactive Power |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | MWAR | WIND | AUX_MVARTOTAL |  | 1) This field is optional 2) Data type is Float 3) Value must be < Reactive Capability - GEN - Maximum Lagging Operating Capability (MVAR) 4) Warn if value > ( Maximum Lagging Operating Capability) * .75 5) Error if value > ( Maximum Lagging Operating Capability) * .66 | R | Float | 1. Done
Wind | Auxiliary Load Power Factor |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | AUX_LOAD_PWR_FACT |  | Between .8 and 1.0 |  |  | 1. Done
Wind | GENERATION AUXILIARY LOAD CHARACTERISTICS FOR MW LOAD |  |  |  | Planning - Wind |  |  | Not in table | Not in table
Wind | Large Motor, Percent Of Total Mw Load |  | 05/03/2012 removed percent from label on form | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | LRG_MTR_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | 1. Done
Wind | Small Motor, Percent Of Total Mw Load |  | 05/03/2012 removed percent from label on form | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | SML_MTR_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | 1. Done
Wind | Resistive (heating) Load, Percent Of Total Mw Load |  | 05/03/2012 removed percent from label on form | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | RESISTIVE_LOAD_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | 1. Done
Wind | Discharge Lighting, Percent Of Total Mw Load |  | 05/03/2012 removed percent from label on form | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | DISCHARGE LIGHT_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | 1. Done
Wind | Other, Percent Of Total Mw Load |  | 05/03/2012 removed percent from label on form | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | OTH_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | 1. Done
Wind | GENERATION AUXILIARY LOAD CHARACTERISTICS FOR MVAR LOAD |  |  |  | Planning - Wind |  |  | Not in table | Not in table
Wind | Large Motor, Percent Of Total MVAR Load |  | 05/03/2012 removed percent from label on form | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | LRG_MTR_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | 1. Done
Wind | Small Motor, Percent Of Total MVAR Load |  | 05/03/2012 removed percent from label on form | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | SML_MTR_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | R | Numeric | 1. Done
Wind | Discharge Lighting, Percent Of Total MVAR Load |  | 05/03/2012 removed percent from label on form | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | DISCHARGE LIGHT_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | 1. Done
Wind | Other, Percent Of Total MVAR Load |  | 05/03/2012 removed percent from label on form | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | OTH_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C | Numeric | 1. Done
Wind | TURBINE STEP-UP TRANSFORMER DATA |  |  |  | Planning - Wind |  |  | Not in table | Not in table
Wind | High Side Voltage Level (nominal) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | Kv | WIND | HIGH_SIDE_VT_LEVL |  | 1) This field is required 2) Data type must be real 3) Generate an Error if not between 345 and 69 | R | Real | 1. Done
Wind | Low Side Voltage Level (nominal) |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | KV | WIND | LOW_SIDE_VT_LEVL |  | 1) This field is required 2) Data type must be real 3) Generate an Error if not < 69 | R | Real | 1. Done
Wind | High Side Voltage Connection |  | 05/23/2012 Updated validation #2 | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | List | WIND | HIGH_SIDE_VT_CONNT |  | 1) This field is required 2) Data type must be from list (Wye, Wye - Grounded or Delta) 3) Generate an Error if blank | R | Real | 1. Done
Wind | Low Side Voltage Connection |  | 05/23/2012 Updated validation #2 | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | List | WIND | LOW_SIDE_VT_CONNT |  | 1) This field is required 2) Data type must be from list (Wye, Wye - Grounded or Delta) 3) Generate an Error if blank | R | Real | 1. Done
Wind | Impedance Z |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | IMPEDANCE_Z |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0 | R | Real | 1. Done
Wind | X/R Ratio |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | X_R_RATIO |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 1 | R | Real | 1. Done
Wind | Zero Sequence Z |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | ZERO_SEQ_Z |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0 | R | Real | 1. Done
Wind | Zero Sequence X/R Ratio |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | ZERO_SEQ_X_R_RATIO |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 1 | R | Real | 1. Done
Wind | Base Mva For Transformer Data |  |  | ADD 04/2012 | Planning - Wind | PLANNING_WIND.View | MVA | WIND | BASE_MVA_TRANSFORMER_DATA |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank, Generate Warning if > 2000 | R | Real | 1. Done
Wind | PSSE MODELS : THE FOLLOWING FILES ARE REQUIRED TO BE SUBMITTED IF NOT LISTED IN THE WIND TURBINE DYNAMIC MODELS AVAILABLE AT ERCOT OR IF ADDITIONAL EQUIPMENT HAS BEEN ADDED TO THE SITE REQUIRING MODEL UPDATES. PLEASE INCLUDE ALL PSSE FILES IN A ZIP OR COMPRESSED FOLDER ALONG WITH YOUR RARF SUBMITTAL SERVICE REQUEST. |  |  |  | Planning - Wind |  |  | Not in table | Not in table
Wind | PSSE Compatible Wind Generator Models |  |  |  | Planning - Wind |  |  | Not in table | Not in table
Wind | Dynamic Reactive Device Form |  |  |  | Planning - Wind |  |  | Not in table | Not in table
Wind | Private Network - Unit - Wind |  |  |  | Private Network - Unit - Wind |  |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Resource Type selected is non-cc non-wind Generation Resources | C
Wind | GENERATOR DETAILS |  |  |  | Private Network - Unit - Wind |  |  | Not in table | Not in table
Wind | Unit Name |  | Do not show Message on Audit or Delta | ADD 02/2012 | Private Network - Unit - Wind |  | List | WIND | UNIT_NAME | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | 1. This field is not null. Data type: Character. | R | Character | 1. Done
Wind | SITE CODE |  |  | ADD 02/2012 | Private Network - Unit - Wind |  | Automatic | WIND | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters |  |  | 1. Done
Wind | Resource Name (Unit Code/Mnemonic) |  |  | ADD 02/2012 | Private Network - Unit - Wind |  | Automatic | WIND | UNIT_CODE | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | Character | B,DVB | 1. Done
Wind | PRIVATE NETWORK - UNIT INFORMATION |  |  |  | Private Network - Unit - Wind |  |  | Not in table | Not in table | This tab is conditional. Required if the Generation Resource Type selected is non-cc non-wind Generation Resources | 3. Should not allow spaces
Wind | Average Amount Of Self-Serve Private Load |  |  |  | Private Network - Unit - Wind |  | MW | WIND | AVG_LD_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric
Wind | Average Amount Of Self-Serve Private Reactive Load |  |  |  | Private Network - Unit - Wind |  | MVAR | WIND | AVG_LD_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric
Wind | Expected Typical Private Network Net Interchange |  |  |  | Private Network - Unit - Wind |  | MW | WIND | NET_INTERCHNG_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric
Wind | Expected Typical Private Network Net Reactive Interchange |  |  |  | Private Network - Unit - Wind |  | MVAR | WIND | NET_INTERCHNG_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric
Wind | Private Network Gross Unit Capability |  |  |  | Private Network - Unit - Wind |  | MW | WIND | GROSS_CAPBLTY_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric
Wind | Private Network Gross Unit Reactive Capability |  |  |  | Private Network - Unit - Wind |  | MVAR | WIND | GROSS_CAPBLTY_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric
Wind | If Unit trips, does Load trip? |  |  |  | Private Network - Unit - Wind |  | Y/N | WIND | LOAD_TRIP_FLG |  | Select from Y or N. | C | Dropdown List
Wind | If yes, approximate percentage of Load that will trip? |  | 05/03/2012 removed percent from label on form |  | Private Network - Unit - Wind |  |  | WIND | LOAD_TRIP_PCT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' | C | Numeric
Wind | Protection - Wind |  |  |  | Protection - Wind |  |  | Not in table | Not in table |  | Not all the fields need to be complete. Only the fields that have Data.
Wind | GENERATOR DETAILS |  |  |  | Protection - Wind |  |  | Not in table | Not in table
Wind | Unit Name |  | Do not show Message on Audit or Delta | ADD 02/2012 | Protection - Wind |  | List | WIND | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | 1. Done
Wind | SITE CODE |  | Removed from Form 03/05/2012 | ADD 02/2012 | Protection - Wind |  | Automatic | WIND | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R | Character | 1. Done
Wind | Resource Name (Unit Code/Mnemonic) |  |  | ADD 02/2012 | Protection - Wind |  | Automatic | WIND | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | 1. Done
Wind | PLANT UNDERVOLTAGE PROTECTION |  |  |  | Protection - Wind |  |  | Not in table | Not in table
Wind | Breaker Interruption Time |  |  |  | Protection - Wind |  | cycles | WIND | BREAKER_INTERRUP |  | 1) this field is required 2) Data type must be Integer | R | Integer
Wind | Instantaneous Undervoltage Trip |  |  |  | Protection - Wind |  | p.u. | Wind | UVOLT_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | O | Float
Wind | Instantaneous Under voltage Trip - Time 1 Time 2 Time 3 Time 4 |  |  |  | Protection - Wind |  | sec | Wind | UVOLT_TRIP_TIME1 UVOLT_TRIP_TIME2 UVOLT_TRIP_TIME3 UVOLT_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage SETTINGS defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | R | Float
Wind | Instantaneous Undervoltage Trip - Under voltage 1 Under voltage 2 Under voltage 3 |  |  |  | Protection - Wind |  | p.u. | Wind | UVOLT_TRIP_VOLT1 UVOLT_TRIP_VOLT2 UVOLT_TRIP_VOLT3 UVOLT_TRIP_VOLT4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Under voltage 1 is required, Under voltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | R | Float
Wind | Instantaneous Overvoltage Trip |  |  |  | Protection - Wind |  | p.u. | Wind | OVOLT_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values 4)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | O | Float
Wind | Instantaneous Overvoltage Trip Time 1 Time 2 Time 3 Time 4 |  |  |  | Protection - Wind |  | sec | Wind | OVOLT_TRIP_TIME1 OVOLT_TRIP_TIME2 OVOLT_TRIP_TIME3 OVOLT_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage SETTINGS defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | R | Float
Wind | Instantaneous Overvoltage Trip - Overvoltage 1 Overvoltage 2 Overvoltage 3 Overvoltage 4 |  |  |  | Protection - Wind |  | p.u. | Wind | OVOLT_TRIP_VOLT1 OVOLT_TRIP_VOLT2 OVOLT_TRIP_VOLT3 OVOLT_TRIP_VOLT4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Overvoltage 1 is required, Overvoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | R | Float
Wind | PLANT OVERFREQUENCY PROTECTION |  |  |  | Protection - Wind |  |  | Not in table | Not in table
Wind | Instantaneous Underfrequency Trip |  |  |  | Protection - Wind |  | Hz | Wind | UFREQ_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float | O | Float
Wind | Instantaneous Underfrequency Trip Time 1 Time 2 Time 3 Time 4 |  |  |  | Protection - Wind |  | sec | Wind | UFREQ_TRIP_TIME1 UFREQ_TRIP_TIME2 UFREQ_TRIP_TIME3 UFREQ_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R | Float
Wind | Instantaneous Underfrequency Trip - Under frequency 1 Under frequency 2 Under frequency 3 Under frequency 4 |  |  |  | Protection - Wind |  | Hz | Wind | UFREQ_TRIP_HZ1 UFREQ_TRIP_HZ2 UFREQ_TRIP_HZ3 UFREQ_TRIP_HZ4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR . Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Under frequency 1 is required, Under frequency 2,3,4 are optional 5)Frequency settings should exist if time settings are defined – Plant Frequency Protection tab | R | Float
Wind | Instantaneous Overfrequency Trip |  |  |  | Protection - Wind |  | Hz | Wind | OFREQ_TRIP_INSTANT |  | 1) This field is OPTIONAL 2) Data type must be Float | O | Float
Wind | Instantaneous Overfrequency Trip Time 1 Time 2 Time 3 Time 4 |  |  |  | Protection - Wind |  | sec | Wind | OFREQ_TRIP_TIME1 OFREQ_TRIP_TIME2 OFREQ_TRIP_TIME3 OFREQ_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | R | Float
Wind | Instantaneous Overfrequency Trip - Overfrequency 1 Overfrequency 2 Overfrequency 3 Overfrequency 4 |  |  |  | Protection - Wind |  | Hz | Wind | OFREQ_TRIP_HZ1 OFREQ_TRIP_HZ2 OFREQ_TRIP_HZ3 OFREQ_TRIP_HZ4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Over frequency 1 is required, Over frequency 2,3,4 are optional 5)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | R | Float
Wind | TURBINE VRT CAPABILITY |  |  |  | Protection - Wind
Wind | Does the Resource Have the Manufacturer's Technical Document / Simulation Results / Test Result, Etc. Describing The Turbine Technology & Vrt OPTIons Purchased With Turbine, If Any |  |  |  | Protection - Wind |  |  | Not in table | Not in table
Wind | Do Personnel (onsite Operator/engineer Etc.) Have Control To Enable/disable Or Change The Settings For Voltage Ride-through |  |  |  | Protection - Wind |  |  | Not in table | Not in table |  | Select from the list: Y or N | R | Dropdown List
Wind | Does The Resource Use Dynamic Reactive Devices (svc/statcom, Etc.) At The Wind Farm? - (note: Capacitor Banks Used For Conventional Reactive Support Cannot Be Considered As Dynamic Reactive Devices) - If Yes, Please Provide Supporting Documentation. (manufacturer's Technical Document, Pss/e Model Etc.) |  |  |  | Protection - Wind |  |  | Not in table | Not in table |  | 1) This field is required 2) Data type must 'Y' or 'N' 3) Generate an Warning if blank, if 'Y', test results must be attached | C | Dropdown List
Wind | Does the Resource Have the Turbine Voltage & Frequency Protection Settings As Per Manufacturer - Technical Document And/or Spec Sheet |  |  |  | Protection - Wind |  |  | Not in table | Not in table |  | 1) This field is required 2) Data type must 'Y' or 'N' 3) Generate an Warning if blank, if 'Y', test results must be attached | C | Dropdown List
Wind | Does The Resource Have Plant Voltage Protection? If Yes, Please Provide Supporting Documentation. |  |  |  | Protection - Wind |  |  | Not in table | Not in table |  | Select from the list: Y or N |  | Dropdown List
Wind | Does The Resource Have Feeder Voltage Protection? If Yes, Please Provide Supporting Documentation. |  |  |  | Protection - Wind |  |  | Not in table | Not in table |  | Select from the list: Y or N |  | Dropdown List
Wind | Collector System - WIND |  | Corrected Tab name 03/26/2012 |  | Collector System - Wind |  |  | Not in table | Not in table
Wind | Site Code |  | 04/19/2012 Added field to Mapping but not added to Form |  | Collector System - Wind |  |  | SITECODES | SITE_CODE
Wind | GENERATOR DETAILS |  | Corrected Tab name 03/26/2012 |  | Collector System - Wind |  |  | Not in table | Not in table
Wind | Resource Name (Unit Code/Mnemonic) |  | 05/17/2012 Update #3 validation Added field in form 03/26/2012 |  | Collector System - Wind |  | Automatic | COLLECTOR_SYS | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters for split gen resources
Wind | COLLECTION SYSTEM DETAILED MODEL |  | Corrected Tab name 03/26/2012 |  | Collector System - Wind |  |  | Not in table | Not in table
Wind | Cable Type |  | 05/15/2012 changed validation #3 to an ERROR message. Corrected Tab name 03/26/2012 | ADD 04/2012 | Collector System - Wind | CollectorSystem.View |  | COLLECTOR_SYS | CABLE_TYPE |  | 1) This field is required 2) Data type must string 3) Generate an error if blank | R | String
Wind | Voltage Level kV |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System - Wind | CollectorSystem.View | kv | COLLECTOR_SYS | VT_LEVEL_KV |  | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | T | Float
Wind | POSITIVE SEQUENCE DATA |  | Corrected Tab name 03/26/2012 |  | Collector System - Wind |  |  | Not in table | Not in table
Wind | R/kft |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System - Wind | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_R_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank | R | Float
Wind | X/kft |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System - Wind | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_X_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank | R | String
Wind | Charging Bc/kft |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System - Wind | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_CHRG_BC_KFT |  | 1) This field is required 2) Data type must float 3) Generate an error if blank | R | Float
Wind | ZERO SEQUENCE DATA |  | Corrected Tab name 03/26/2012 |  | Collector System - Wind |  |  | Not in table | Not in table
Wind | R0/kft |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System - Wind | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | ZERO_R0_KFT |  | 1) This field is required 2) Data type must float 3) Generate an errorif blank | R | Float
Wind | X0/kft |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System - Wind | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | ZERO_X0_KFT |  | 1) This field is required 2) Data type must float 3) Generate an error if blank | R | Float
Wind | Collector System-Wind Seg Data |  | Corrected Tab name 03/26/2012 |  | Collector System-Wind Seg Data |  |  | Not in table | Not in table
Wind | Site Code |  | 04/19/2012 Added field to Mapping but not added to Form |  | Collector System-Wind Seg Data |  |  | SITECODES | SITE_CODE
Wind | GENERATOR DETAILS |  | Corrected Tab name 03/26/2012 |  | Collector System-Wind Seg Data |  |  | Not in table | Not in table
Wind | Resource Name (Unit Code/Mnemonic) |  | 05/17/2012 Update #3 validation Added field in form 03/26/2012 |  | Collector System-Wind Seg Data |  | Automatic | CABLE_SEG_DATA | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters for split gen resources
Wind | Cable Type |  | Corrected Tab name 03/26/2012 |  | Collector System-Wind Seg Data |  |  | Not in table | Not in table
Wind | Cable Type |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System-Wind Seg Data | CollectorSystem_SegData.View | List | CABLE_SEG_DATA | CABLE_TYPE |  | 1) This field is required 2) Data type must string 3) Generate an error if blank | R | String
Wind | WIND SEGAMENT DETAILS |  | Corrected Tab name 03/26/2012 |  | Collector System-Wind Seg Data |  |  | Not in table | Not in table
Wind | From |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System-Wind Seg Data | CollectorSystem_SegData.View | Integer | CABLE_SEG_DATA | CABLE_SEG_DATA_FROM |  | 1) This field is required 2) Data type must integer 3) Generate an error if blank | R | Integer
Wind | To |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System-Wind Seg Data | CollectorSystem_SegData.View | Integer | CABLE_SEG_DATA | CABLE_SEG_DATA_TO |  | 1) This field is required 2) Data type must integer 3) Generate an error if blank | R | Integer
Wind | Circuit Number |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System-Wind Seg Data | CollectorSystem_SegData.View | Integer | CABLE_SEG_DATA | CIRCT_NUM |  | 1) This field is required 2) Data type must integer 3) Generate an error if blank | R | Integer
Wind | Voltage Level |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System-Wind Seg Data | CollectorSystem_SegData.View | kV | CABLE_SEG_DATA | VT_LEVL |  | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0. | T | Float
Wind | Cable Segment Length |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System-Wind Seg Data | CollectorSystem_SegData.View | in kft | CABLE_SEG_DATA | CABLE_SEG_LENTH |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank | R | Float
Wind | Number of Turbines on cable segment |  | 05/15/2012 changed validation #3 to an ERROR message. | ADD 04/2012 | Collector System-Wind Seg Data | CollectorSystem_SegData.View | Integer | CABLE_SEG_DATA | NUM_TURBIN_ON_CABLE_SEG |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank | R | Integer
Transmission | Line Data |  | Corrected Tab name 03/26/2012 |  | Line Data |  | Not in table | Not in table | Not in table
Transmission | DESCRIPTION OF CHANGE |  |  |  | Line Data |  | List | LINE | CHANGE_DESCRIPTION |  | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Alpha
Transmission | LINE (ANY LENGTH) DETAILS |  |  |  | Line Data |  |  | Not in table | Not in table
Transmission | Line Name |  |  |  | Line Data |  | enter all caps | LINE | ERCOT_LINE_NAME |  | 1) This field is required 2) This field may not have any special characters, except an underscore "_" and a dash "-" 3) Warn if > 14 characters. Warning! ERCOT Line Name () should not be > 14 characters long or the name will be truncated in the model which requires uniqueness. 4) Line Name can not be duplicated in a Station | T | Alpha
Transmission | Line Voltage Level |  |  |  | Line Data |  | kV | LINE | LINE_VOLT_LVL |  | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value must be < 345 4) The value must be > 1 | T | Float
Transmission | Resistance in P.U. (100 MVA Base) |  |  |  | Line Data |  | p.u. | LINE | RESISTANCE |  | 1) Field is required If value is < 0.0001 and Internal Line = 'Y' then Warning! Resistance should be less than 0.0001 If value is < 0.0001 and Internal Line = 'N' then Warning! Resistance should be less than 0.0001 3) If Line Data - Line Voltage Level = 69kV, value must be <= 1.5 If Line Data - Line Voltage Level = 138kV or 345kV, value must be <= 0.5 WARN if value is outside of these conditions 4) If the Zero Impedance Lines are contained within a single substation, then they should be removed from the Line tab and the updated connections should be shown in the Breaker/Switch tab. "ERROR! Internal zero impedance lines should be modeled on the breaker/switch tab" If Zero Impedance Lines are between two substations, produce a warning if line ratings are entered as 9999. "ERROR! Invalid MVA Rating between substations" | T | Float
Transmission | Reactance in P.U. (100 MVA Base) |  |  |  | Line Data |  | p.u. | LINE | REACTANCE |  | 1) Field is required If value is < 0.0001 and Internal Line = 'Y' then Warning! Reactance should be less than 0.0001 If value is < 0.0001 and Internal Line = 'N' then Warning! Reactance should be less than 0.0001 If Line Data - Line Voltage Level = 69kV, value must be <=1.0 If Line Data - Line Voltage Level = 138kV, value must be <=0.1 If Line Data - Line Voltage Level = 345kV, value must be <=.05 WARN if value is outside of these conditions 3)Error if Reactance value is > 1. Error! Reactance (value) > 1.0. Reactance should be expressed in terms of per unit (e.g. not percentage). 4) If the Zero Impedance Lines are contained within a single substation, then they should be removed from the Line tab and the updated connections should be shown in the Breaker/Switch tab. "ERROR! Internal zero impedance lines should be modeled on the breaker/switch tab" | T | Float
Transmission | Charging Susceptance in PU (100 MVA Base) |  |  |  | Line Data |  | p.u. | LINE | CHARGING_SUSC |  | 1) Field is required 2) Value must be >= 0 If Line Data - Line Voltage Level = 69kV, value must be >=.00001<=0.3 If Line Data - Line Voltage Level = 138kV, value must be >=.00001<=0.5 If Line Data - Line Voltage Level = 345kV, value must be >=.00001<=2.2. Generate a Warning if Rule fails 3) If the Zero Impedance Lines are contained within a single substation, then they should be removed from the Line tab and the updated connections should be shown in the Breaker/Switch tab. ERROR! Internal zero impedance lines should be modeled on the breaker/switch tab. | T | Float
Transmission | Zero Sequence Line Resistance In P.u. (100mva Base) |  |  | ADD 04/2012 | Line Data | Line_Information.View | p.u. | LINE | ZERO_SEQ_LINE_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R
Transmission | Zero Sequence Line Reactance In P.u. (100mva Base) |  |  | ADD 04/2012 | Line Data | Line_Information.View | p.u. | LINE | ZERO_SEQ_LINE_REACTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 | R
Transmission | Zero Sequence Charging Susceptance In P.u. (100mva Base) |  | 2012-03-08 | ADD 04/2012 | Line Data | Line_Information.View | p.u. | LINE | ZERO_ SEQ_ CHRG_ SUSECPTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R
Transmission | Type (overhead / underground) |  | Removed Validation #3 per planing group. |  | Line Data |  | List | LINE | TYPE |  | 1) Field is required 2) Value must be at from the following list: OVERHEAD, UNDERGROUND, BOTH | T | Alpha
Transmission | Segment Length |  |  |  | Line Data |  | miles | LINE | SEGMENT_LENGTH |  | 1) Field is required 2) Value must > 0 3) Formula on Line Data - Segment Length: The formula to determine the length of a line based on the Reactance (X) and the Charging Susceptance (Chg) is 486 * SQRT(X_pu * Chg_pu). Generate a Warning when Segment length is not within the 25% variation of the calculated value. 4) Update the Warning message to include the text " This is applicable for Overhead lines only" | T | Float
Transmission | TO STATION |  |  |  | Line Data |  |  | Not in table | Not in table
Transmission | EROCT STATION TO - Station Code Mnemonic |  |  |  | Line Data |  | enter all caps | LINE | ERCOT_CODE_TO |  | 1) This field is Optional 2) Warn if left blank 3) This field must match ERCOT records (unless new) .Substation Code invalid message should be warning only if the PUN flag is 'yes'. 4.If the Internal Line Flag is 'Y', then the TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic can be same. If the internal Line Flag is 'N', TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic should be distinct . Error message should be "'Error! TO and FROM Station Code ( ) should not be duplicated if Internal Line Flag = "N". 5) If the internal Line Flag is 'N', ,FROM Station Code Mnemonic cannot be listed as a TO Station Code Mnemonic on any other lines. The Warning would occur on the secondary side (eg: they had DIESEL on the FROM station on the first line, and DIESEL on the TO Station on the second line then the TO station would produce the Warning) or (eg: DIESEL is on the TO station on the 3rd line and DIESEL on the FROM station on the 4th line then the FROM station would produce the Warning). | T | Alpha
Transmission | Internal Line |  |  |  | Line Data |  | Y/N | LINE | INTERNAL_LINE_TO_FLG |  | 1) This field is required 2) Value must be of the following: 'Y', 'N' | T | Alpha
Transmission | TSP Name |  |  |  | Line Data |  | List | LINE | TSPNAME_TO |  | 1) This field is conditionally required if TO STATION - Internal Line - 'N' 2) This field must match ERCOT records (drop down in RARF) | T | Alpha
Transmission | Connected Device 1 thru 10 |  |  |  | Line Data |  | enter all caps | LINE_DEVICES | DEVICE_NAME |  | 1) This field is required 2) May not be >= than 17 characters. Warning! Device Name () should not be > 17 characters long or the name will be truncated in the model which requires uniqueness. 3) May not have duplicates within the TO or FROM Station 4) May not contain special characters except for an underscore "_" and a dash "-" | T | Alpha
Transmission | Bus Number (PTI Bus Number) |  |  |  | Line Data |  | # | LINE | BUS_NUM_TO |  | 1) This field is optional 2) This field must be between 1 - 99,999 | T | Integer
Transmission | Weather Zone / Weather Station (used for Dynamic Ratings) |  |  |  | Line Data |  | List | LINE | WEATHERZONE_TO |  | 1) This field is conditionally required if "Line Rating (Static or Dynamic)" = 'DYNAMIC' 2) Value must be from the following list: COAST, EAST, FAR_WEST, NORTH, NORTH_C, SOUTH_C, SOUTHERN, WEST, KABI, KAUS, KBRO, KCRP, KDFW, KGLS, KIAH, KJCT, KLRD, KLFK, KMAF, KMWL, KSJT, KSAT, KTYR, KVCT, KACT, KSPS, KINK, KPRX | T | Alpha
Transmission | FROM Station |  |  |  | Line Data |  |  | Not in table | Not in table
Transmission | ERCOT FROM Station Code Mnemonic |  |  |  | Line Data |  | enter all caps | LINE | ERCOT_CODE_FROM |  | 1) This field is required 2) Must match ERCOT records (unless new) 3) Value must be <= 8 characters .Warning! Station Code () should not be > 8 characters long or the name will be truncated in the model which requires uniqueness. 4. If the Internal Line Flag is 'Y', then the TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic can be same. If the internal Line Flag is 'N', TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic should be distinct. Error message should be "'Error! TO and FROM Station Code ( ) should not be duplicated if Internal Line Flag = "N". 5) If the internal Line Flag is 'N', ,FROM Station Code Mnemonic cannot be listed as a TO Station Code Mnemonic on any other lines. The Warning would occur on the secondary side (eg: they had DIESEL on the FROM station on the first line, and DIESEL on the TO Station on the second line then the TO station would produce the Warning) or (eg: DIESEL is on the TO station on the 3rd line and DIESEL on the FROM station on the 4th line then the FROM station would produce the Warning). | T | Alpha
Transmission | Connected Device 1 thru 10 |  |  |  | Line Data |  | enter all caps | LINE_DEVICES | DEVICE_NAME |  | 1) This field is required 2) May not have duplicates within the TO or FROM Station 3) May not contain special characters except for an underscore "_" and a dash "-" 4) May not be > than 17 characters. Warning! Device Name () should not be > 17 characters long or the name will be truncated in the model which requires uniqueness. | T | Alpha
Transmission | Bus Number (PTI Bus Number) |  |  |  | Line Data |  | integer | LINE | BUSNUMBR_FROM |  | 1) This field is optional 2) This field must be between 1 - 99,999 3) Warn if left blank | T | Integer
Transmission | Weather Zone / Weather Station (used for Dynamic Ratings) |  |  |  | Line Data |  | # | LINE | WEATHERZONE_FROM |  | 1) This field is conditionally required if "Line Rating (Static or Dynamic)" = 'DYNAMIC' 2) Value must be from the following list: COAST, EAST, FAR_WEST, NORTH, NORTH_C, SOUTH_C, SOUTHERN, WEST, KABI, KAUS, KBRO, KCRP, KDFW, KGLS, KIAH, KJCT, KLRD, KLFK, KMAF, KMWL, KSJT, KSAT, KTYR, KVCT, KACT, KSPS, KINK, KPRX | T | Alpha
Transmission | Line Code |  |  | ADD 02/2012 | Line Data |  | List | LINE | LINE_CODE |  | Concantenate (Site Code_Substation Code_ERCOT_LINE_NAME) | R
Transmission | COMMENTS |  |  |  | Line Data |  |  | LINE | COMMENTS_LINE
Transmission | EFFECTIVE DATE: |  |  |  | Line Data |  | mm/dd/yyyy | LINE | EFF_DATE |  | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T | Date
Transmission | Line Temperture |  |  |  | Line Temperture |  |  | Not in table | Not in table
Transmission | DESCRIPTION OF CHANGE |  | Added 03/26/2012 | Add 04/2012 | Line Temperture | Line_TempDetails.View | List | LINE_TEMP | CHANGE_DESCRIPTION |  | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Alpha
Transmission | Line Name |  |  | ADD 02/2012 | Line Temperture |  | Automatic | LINE_TEMP | ERCOT_LINE_NAME |  | 1) This field is required 2) This field may not have any special characters, except an underscore "_" and a dash "-" 3) Warn if > 14 characters. Warning! ERCOT Line Name () should not be > 14 characters long or the name will be truncated in the model which requires uniqueness. 4) Line Name can not be duplicated in a Station
Transmission | Line Code |  |  | ADD 02/2012 | Line Temperture |  | Automatic | LINE_TEMP | LINE_CODE |  | Concantenate (Site Code_Substation Code_ERCOT_LINE_NAME)
Transmission | Line Rating |  |  | ADD 02/2012 | Line Temperture |  | Static or Dynamic | LINE_TEMP | LINE_RATING |  | 1) Field is required 2) Field must be from the following list: STATIC, DYNAMIC | T | Alpha
Transmission | Nominal |  |  |  | Line Temperture |  |  | Not in table | Not in table
Transmission | Continuous Rating |  |  |  | Line Temperture |  | MVA | LINE | CONTINUOUS_RTG |  | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be <= Nominal (Static) - 2-hr Emergency Rating 3) Value must be <= Nominal (Static) - 15-min Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - Continuous Rating AND value must be >= 115 °F Continuous Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Integer
Transmission | 2-hr Emergency Rating |  |  |  | Line Temperture |  | MVA | LINE | EMGCY_RTG_2HR |  | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be >= Nominal (Static) - Continuous Rating 3) Value must be <= Nominal (Static) - 15-min Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 2-hr Emergency Rating AND value must be >= 115 °F 2-hr Emergency Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Integer
Transmission | 15-min Rating |  |  |  | Line Temperture |  | MVA | LINE | RTG_15MIN |  | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be >= Nominal (Static) - Continuous Rating 3) Value must be >= Nominal (Static) - 2-hr Emergency Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 15-min Rating AND value must be >= 115 °F 15-min Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Integer
Transmission | Planning Rate C |  | 05/03/2012 Add new field to Line Table also needs to be mapped. Field already existed in form. 03/09/2012 Updated Validation | ADD 04/2012 | Line Temperture | Line_TempDetails.View | MVA | Line | PLANNING_RATE_C |  | This field is required Numeric value Must be >= Nominal Emergency Rating (2HR Rating) | R | Model Adminstration
Transmission | Line Temperture |  |  |  | Line Temperture |  |  | LINE_TEMP | LINE_TEMP |  | Degree of Temperature
Transmission | 20 °F - Continuous Rating - 115 °F Continuous Rating |  |  |  | Line Temperture |  | MVA | LINE_TEMP | CONTINUOUS_RTG |  | 1) These field are conditionally required. If Line Rating (Static or Dynamic) = Dynamic this field is required 2) Line Rating (Static or Dynamic) = Static, this field must be blank 3) If required, these values must be <= the subsequent dynamic rating. For example: 20 °F - Continuous Rating >= 25 °F - Continuous Rating 25 °F - Continuous Rating >= 30 °F - Continuous Rating 4) If required, within each temp rating, the following must apply Continuous Rating <= 2-hr Emergency Rating <= 15-min rating | T | Integer
Transmission | 20 °F - 2-hr Emergency Rating - 115 °F 2-hr Emergency Rating |  |  |  | Line Temperture |  | MVA | LINE_TEMP | EMGCY_RTG_2HR |  | 1) These field are conditionally required. If Line Rating (Static or Dynamic) = Dynamic this field is required 2) Line Rating (Static or Dynamic) = Static, this field must be blank 3) If required, these values must be >= the subsequent dynamic rating. For example: 20 °F - 2-hr Emergency Rating >= 25 °F - 2-hr Emergency Rating 25 °F - 2-hr Emergency Rating >= 30 °F - 2-hr Emergency Rating 4) If required, within each temp rating, the following must apply Continuous Rating <= 2-hr Emergency Rating <= 15-min rating | T | Integer
Transmission | 20 °F - 15-min Rating - 115 °F 15-min Rating |  |  |  | Line Temperture |  | MVA | LINE_TEMP | RTG_15MIN |  | 1) These field are conditionally required. If Line Rating (Static or Dynamic) = Dynamic this field is required 2) Line Rating (Static or Dynamic) = Static, this field must be blank 3) If required, these values must be >= the subsequent dynamic rating. For example: 20 °F - 2-hr 15-min Rating >= 25 °F - 15-min Rating 25 °F - 2-hr 15-min Rating >= 30 °F - 15-min Rating 4) If required, within each temp rating, the following must apply Continuous Rating <= 2-hr Emergency Rating <= 15-min rating | T | Integer
Transmission | Planning Rate C |  | 05/03/2012 Updated validation rule 03/09/2012 Updated Validation | ADD 04/2012 | Line Temperture | Line_TempDetails.View | MVA | LINE_TEMP | PLANNING_RATE_C |  | 1)Numeric value 2) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be >=Tempature Emergency Rating (2HR Rating) else (if Line Rating (Static or Dynamic) = Static, this field must be blank). | R | Float
Transmission | Breaker_Switch Data |  |  |  | Breaker Switch Data |  |  | Not in table | Not in table
Transmission | DESCRIPTION OF CHANGE |  |  |  | Breaker Switch Data |  | List | BREAKER_SWITCH | CHANGE_DESCRIPTION | CHANGE_DESCRIPTION | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Alpha
Transmission | BREAKER / SWITCH |  |  |  | Breaker Switch Data |  |  | Not in table | Not in table
Transmission | Switch Name |  |  |  | Breaker Switch Data |  | enter all caps | BREAKER_SWITCH | SWITCH_NAME |  | 1) This field is required 2) Value may contain no special characters except an underscore "_" and a dash "-" 3) Must be <=14 characters. Warning! Switch Name () should not be >14 characters long or the name will be truncated in the model which requires uniqueness. 4) Switch Name can not be duplicated in a station | T | Alpha
Transmission | ERCOT Station Code Mnemonic |  |  |  | Breaker Switch Data |  | enter all caps | BREAKER_SWITCH | SUBSTATION_CODE | SWITCH_NAME | 1) This field is required 2) Must match ERCOT records (unless new). Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters. Warning! Station Code () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) substation code should be in Upper case letters. Generate an error if the rule fails | T | Alpha
Transmission | Switch Code |  |  | UPDATE 02/2012 | Breaker Switch Data |  | Automatic | BREAKER_SWITCH | BREAKER_CODE | SUBSTATION_CODE | Concantenate (Site Code_Substation Code_Switch Name)
Transmission | Is this a Fault Isolating Device (e.g. Circuit Breaker) |  |  |  | Breaker Switch Data |  | Y/N | BREAKER_SWITCH | FAULT_ISO_DEV_FLG | FAULT_ISO_DEV_FLG | 1) This is a required field 2) Values must from the following list: 'Y', 'N' | T | Alpha
Transmission | Normal Operating Status (when in-service) |  |  |  | Breaker Switch Data |  | Oper/Closed | BREAKER_SWITCH | NORM_OP_STATUS | NORM_OP_STATUS | 1) This field is required 2) Value must be from the following list: 'OPEN', 'CLOSED' 3) Generate a warning when the Normal Operating Status is 'OPEN' | T | Alpha
Transmission | Voltage Level |  |  |  | Breaker Switch Data |  | kV | BREAKER_SWITCH | VOLT_LVL | VOLT_LVL | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | T | Float
Transmission | Static Ratings for Planning |  |  |  | Breaker Switch Data |  |  | Not in table | Not in table
Transmission | Continuous Rating |  |  | ADD 04/2012 | Breaker Switch Data | Breaker_Switch.View | MVA | BREAKER_SWITCH | CONTINUOUS_RTG |  | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be <= Nominal (Static) - 2-hr Emergency Rating 3) Value must be <= Nominal (Static) - 15-min Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - Continuous Rating AND value must be >= 115 °F Continuous Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Integer
Transmission | 2-hr Emergency Rating |  |  | ADD 04/2012 | Breaker Switch Data | Breaker_Switch.View | MVA | BREAKER_SWITCH | EMGCY_RTG_2HR |  | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be >= Nominal (Static) - Continuous Rating 3) Value must be <= Nominal (Static) - 15-min Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 2-hr Emergency Rating AND value must be >= 115 °F 2-hr Emergency Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Integer
Transmission | 15 Min Rating |  |  | ADD 04/2012 | Breaker Switch Data | Breaker_Switch.View | MVA | BREAKER_SWITCH | RTG_15MIN |  | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be >= Nominal (Static) - Continuous Rating 3) Value must be >= Nominal (Static) - 2-hr Emergency Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 15-min Rating AND value must be >= 115 °F 15-min Rating 5) Produce an error when invalid MVA ratings are entered as 9999. ERROR! Invalid MVA Rating between substations. | T | Integer
Transmission | Side 1 / Side 2 - Directly connected device name(s) |  |  |  | Breaker Switch Data |  | enter all caps | BREAKER_SWITCH_SIDE | DEVICE_NAME |  | 1) This field is required 2) Value may contain no special characters except an underscore "_" and a dash "-" 3) Must be <=17 characters. Must be <=17 characters. Warning! Device Names () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. 4) At least one connected device is required on each side of the Breaker/Switch. Generate an error if at least one connected device is missing on both sides Generate a Warning when at least one connected device is missing on any one side. | T | Alpha
Transmission | COMMENTS |  |  |  | Breaker Switch Data |  |  | BREAKER_SWITCH | COMMENTS_BRKSWITCH
Transmission | EFFECTIVE DATE: |  |  |  | Breaker Switch Data |  | mm/dd/yyyy | BREAKER_SWITCH | EFF_DATE |  | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T | Date
Transmission | Capacitor or Reactor Data |  |  |  | Capacitor and Reactor Data |  |  | Not in table | Not in table
Transmission | DESCRIPTION OF CHANGE |  |  |  | Capacitor and Reactor Data |  | List | CAPREACT | CHANGE_DESCRIPTION |  | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Alpha
Transmission | Capacitor or Reactor |  |  |  | Capacitor and Reactor Data |  | List | Not in table | Not in table |  | 1) This field is required 2) Value must be from the following list: 'C', 'R' | T | Alpha
Transmission | Device Name |  |  |  | Capacitor and Reactor Data |  | enter all caps | CAPREACT | DEVICE_NAME |  | 1) This field is required 2) Value may contain no special characters except an underscore "_" and a dash "-" 3) Must be <=14 characters. Warning! Device Name () should not be >14 characters long or the name will be truncated in the model which requires uniqueness. 4) Device Name can not be duplicated in a Station | T | Alpha
Transmission | ERCOT Station Code Mnemonic |  |  | UPDATE 02/2012 | Capacitor and Reactor Data |  | enter all caps | CAPREACT | SUBSTATION_CODE |  | 1) This field is required 2) Must match ERCOT records (unless new).Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3)This field may not have any special characters, except an underscore "_" and a dash "-" 4) Value must be <= 8 characters. Warning! Station Code () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) substation code should be in Upper case letters. Generate an error if the rule fails | T | Alpha
Transmission | Device Code |  |  | UPDATE 02/2012 | Capacitor and Reactor Data |  | Automatic | CAPREACT | DEVICE_CODE |  | Concantenate (Site Code_Substation Code_Device Code)
Transmission | Capacitor or Reactor |  |  |  | Capacitor and Reactor Data |  | List | CAPREACT | CAPACITOR_REACTOR_FLG |  | 1) This field is required 2) Value must be from the following list: 'C', 'R' | T | Alpha
Transmission | Nominal MvAR |  |  |  | Capacitor and Reactor Data |  | MVAR | CAPREACT | NOMINAL_MVAR |  | 1) This field is required 2) If the Capacitor or Reactor field is 'C' , the value should be > 0 , if it is 'R', value should be < 0 | T | Float
Transmission | Voltage Level Kv |  |  |  | Capacitor and Reactor Data |  | kV | CAPREACT | VOLT_LVL_KV |  | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | T | Float
Transmission | Bus Number (PTI Bus Number) |  |  |  | Capacitor and Reactor Data |  | # | CAPREACT | PTI_BUSNUM |  | 1) This field is optional 2) This field must be between 1 - 99,999 | T | Float
Transmission | Automatic Voltage Regulation |  |  |  | Capacitor and Reactor Data |  | Y/N | CAPREACT | AUTO_VOLT_FLG |  | 1) This field is required 2) Value must be from the following list: 'Y', 'N' | T | Alpha
Transmission | Voltage Level of Busbar being regulated |  |  |  | Capacitor and Reactor Data |  | kV | CAPREACT | BUSBAR_VOLT |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | T | Float
Transmission | Desired Regulating voltage |  |  |  | Capacitor and Reactor Data |  | kV | CAPREACT | DES_REG_VOLT |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) The value may not exceed 345. (REMOVED) 3) The value must be > 0 4) The value must >= Minimum Regulating Voltage 5) The value must <=Maximum Regulating Voltage 6) Value should be within the range of 10% of the base kV..anything beyond should be a Warning. | T | Float
Transmission | Minimum Regulating Voltage |  |  |  | Capacitor and Reactor Data |  | kv | CAPREACT | MIN_REG_VOLT |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) The value may not exceed 345(REMOVED) 3) The value must be > 0 4) The value must be <= Maximum Regulating Voltage 5) Warning if value exceeds 50% from Maximum Regulating Voltage 6) Value should be within the range of 10% of the base kV..anything beyond should be a Warning. | T | Float
Transmission | Maximum Regulating Voltage |  |  |  | Capacitor and Reactor Data |  | kv | CAPREACT | MAX_REG_VOLT |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 3) The value must be > 0 4) The value must be >= Minimum Regulating Voltage 5) Warning if value exceeds 50% from Minimum Regulating Voltage 6) Value should be within the range of 10% of the base kV..anything beyond should be a Warning. | T | Float
Transmission | Zero Sequence Reactance Increment In p.u. |  | 03/08/2012 Removed Validation #3 per plaaning group. | ADD 04/2012 | Capacitor and Reactor Data | Capacitor_Reactor.View | p.u. | CAPREACT | ZERO_SEQ_REACTANCE_INCRMENT_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 | R
Transmission | Device Name(s) - that this reactive device is directly connected to |  |  |  | Capacitor and Reactor Data |  | enter all caps | CAPREACT_DEVICE | CONNECTED_DEVICE_NAME |  | 1) This field is optional 2) May not contain special characters except for an underscore "_" and a dash "-" 3) ) May not be > than 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. 4)This field should be unique. Every Device entry needs to have a unique “Device Name(s) – that this reactive device is directly connected to". No two capacitors should have the same controlling breaker or switch. 5) 'Connected Device in Capacitor Reactor should have a Controlling Breaker/Switch in Breaker/switch Tab. Audit report should generate an error if the rule fails. For all other equipment that is not a Capacitor/Reactor, they can have connectivity references to transformers, lines, etc. However, for the Capacitor/Reactors, the EMS needs to have a controlling switch modeled, else they would always be "On | T | Alpha
Transmission | COMMENTS |  |  |  | Capacitor and Reactor Data |  |  | CAPREACT | COMMENTS_CAPREACT
Transmission | EFFECTIVE DATE: |  |  |  | Capacitor and Reactor Data |  | mm/dd/yyyy | CAPREACT | EFF_DATE |  | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T | Date
Transmission | Static Var Compensator Data |  |  |  | Static Var Compensator Data |  |  | Not in table | Not in table
Transmission | DESCRIPTION OF CHANGE |  |  |  | Static Var Compensator Data |  | List | STATIC_VAR_COMP | CHANGE_DESCRIPTION |  | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Alpha
Transmission | STATIC VAR COMPENSATOR |  |  |  | Static Var Compensator Data |  |  | Not in table | Not in table
Transmission | SVC Name |  |  |  | Static Var Compensator Data |  | enter all caps | STATIC_VAR_COMP | SVC_NAME |  | 1) This field is required 2) May not be > than 14 characters..Warning! SVC Name () should not be >14 characters long or the name will be truncated in the model which requires uniqueness. 3) May not contain special characters except for an underscore "_" and a dash "-" 4) Device Name can not be duplicated in a Station | T | Alpha
Transmission | ERCOT Station Name (Station Code or Station Mnemonic) |  |  |  | Static Var Compensator Data |  | enter all caps | STATIC_VAR_COMP | SUBSTATION_CODE |  | 1) This field is required 2) Must match ERCOT records (unless new).Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) Must be <= 8 characters. Warning! Station Name () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. | T | Alpha
Transmission | SVC CODE |  |  | UPDATE 02/2012 | Static Var Compensator Data |  | Automatic | STATIC_VAR_COMP | SVC_CODE |  | Concantenate (Site Code_Substation Code_SVC Name)
Transmission | SVC Base Voltage Level |  |  |  | Static Var Compensator Data |  | kV | STATIC_VAR_COMP | SVC_BASE_VOLT |  | 1) This field is required 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | T | Float
Transmission | Fixed Mvar (var injection At Nominal Voltage) |  |  | UPDATE 02/2012 | Static Var Compensator Data |  | MVAR | STATIC_VAR_COMP | FIXED_MVAR |  | 1) This field is required | T | Float
Transmission | Minimum Admittance Limits (100 MVA Base) |  |  | UPDATE 02/2012 | Static Var Compensator Data |  | p.u. | STATIC_VAR_COMP | MIN_ADM_LIMIT |  | 1) This field is required 2) Value must be <= Maximum Admittance | T | Float
Transmission | Maximum Admittance Limits (100 MVA Base) |  |  | UPDATE 02/2012 | Static Var Compensator Data |  | p.u. | STATIC_VAR_COMP | MAX_ADM_LIMIT |  | 1) This field is required 2) Value must be >= Minimum Admittance | T | Float
Transmission | Minimum Steady State Reactive Power Limits |  |  |  | Static Var Compensator Data |  | MVAR | STATIC_VAR_COMP | MIN_STD_STATE_REACT |  | 1) This field is required 2) Value must be >= Maximum Steady State Reactive Power Limits | T | Float
Transmission | Maximum Steady State Reactive Power Limits |  |  |  | Static Var Compensator Data |  | MVAR | STATIC_VAR_COMP | MAX_STD_STATE_REACT |  | 1) This field is required 2) Value must be >= Minimum Steady State Reactive Power Limits | T | Float
Transmission | Minimum Threshold (post Contingency) Reactive Power Limits |  |  |  | Static Var Compensator Data |  | MVAR | STATIC_VAR_COMP | MIN_THRESH_REACT |  | 1) This field is required 2) Value must be <= Maximum Threshold (post contingency) Reactive Power Limits | T | Float
Transmission | Maximum Threshold (post Contingency) Reactive Power Limits |  |  | UPDATE 02/2012 | Static Var Compensator Data |  | MVAR | STATIC_VAR_COMP | MAX_THRESH_REACT |  | 1) This field is required 2) Value must be <= Maximum Steady State Reactive Power Limits | T | Float
Transmission | Minimum Voltage Threshold |  |  | UPDATE 02/2012 | Static Var Compensator Data |  | kV | STATIC_VAR_COMP | MIN_VOLT_THRESH |  | 1) This field is required 2) Value must be <= Maximum Voltage Threshold (100 MVA Base) 3) The value may not exceed 370 3) The value must be > 0 4) Warn if Max / Min exceed 50% of one another | T | Float
Transmission | Maximum Voltage Threshold |  |  | UPDATE 02/2012 | Static Var Compensator Data |  | kV | STATIC_VAR_COMP | MAX_VOLT_THRESH |  | 1) This field is required 2) Value must be >= Minimum Voltage Threshold (100 MVA Base) 3) The value may not exceed 370 4) The value must be > 0 5) Warn if Max / Min exceed 50% of one another | T | Float
Transmission | Device Name(s) - that this reactive device is directly connected to |  |  |  | Static Var Compensator Data |  | enter all caps | STATIC_VAR_COMP_DEVICES | SWITCH_DEVICE_NAME |  | 1) This field is optional 2) May not contain special characters except for an underscore "_" and a dash "-" 3) May not be > than 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. | T | Alpha
Transmission | COMMENTS |  |  |  | Static Var Compensator Data |  |  | STATIC_VAR_COMP | COMMENTS_STATIC VAR_COMP
Transmission | EFFECTIVE DATE: |  |  |  | Static Var Compensator Data |  | mm/dd/yyyy | STATIC_VAR_COMP | EFF_DATE |  | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T | Date
Transmission | Series Device Data |  |  |  | Series Device Data |  |  | Not in table | Not in table
Transmission | DESCRIPTION OF CHANGE |  |  |  | Series Device Data |  | List | SERIES_DEVICE_DATA | CHANGE_DESCRIPTION |  | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Alpha
Transmission | SERIES DEVICE DATA |  |  |  | Series Device Data |  |  | Not in table | Not in table
Transmission | Series Device Name |  |  |  | Series Device Data |  | enter all caps | SERIES_DEVICE_DATA | SD_NAME |  | 1) This field is required 2) No special characters except and underscore 3) Warn if >= 14 characters. First 14 characters must be unique. Warning! Series Device Name() should not be >= 14 characters long or the name will be truncated in the model which requires uniqueness. 4) Device Name can not be duplicated in a Station | T | Alpha
Transmission | Ercot Station Code Mnemonic |  |  |  | Series Device Data |  | enter all caps | SERIES_DEVICE_DATA | SUBSTATION_CODE |  | 1) This field is required 2) Must match ERCOT records (unless new).Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters. Warning! Station Code () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. | T | Alpha
Transmission | SD Code |  |  | UPDATE 02/2012 | Series Device Data |  | Automatic |  |  |  | Concantenate (Site Code_Substation Code_SD Name)
Transmission | Voltage Level |  |  |  | Series Device Data |  | kV | SERIES_DEVICE_DATA | VOLATGE |  | 1) This field is required 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | T | Float
Transmission | Resistance |  |  |  | Series Device Data |  | p.u. | SERIES_DEVICE_DATA | RESISTANCE |  | 1) This value is required 2) Value must be > 0 | T | Float
Transmission | Reactance |  |  |  | Series Device Data |  | p.u. | SERIES_DEVICE_DATA | REACTANCE |  | 1) This value is required 2) Value may be negative. Allow negative Reactance (to represent Series Capacitors) 3)Error if Reactance value is > 1. Error! Reactance (value) > 1.0. Reactance should be expressed in terms of per unit (e.g. not percentage). | T | Float
Transmission | Continuous Rating |  |  |  | Series Device Data |  | MVA | SERIES_DEVICE_DATA | CONTINUOUS_RTG |  | 1) This field is required 2) Value must be <= 2-hr Emergency Rating 3) Value must be <= 15-min Rating | T | Float
Transmission | 2-hr Emergency Rating |  |  |  | Series Device Data |  | MVA | SERIES_DEVICE_DATA | EMGCY_RTG_2HR |  | 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be <=15-min Rating | T | Float
Transmission | 15-min Rating |  |  |  | Series Device Data |  | MVA | SERIES_DEVICE_DATA | RTG_15MIN |  | 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be >= 2-hr Emergency Rating | T | Float
Transmission | Side 1 |  |  |  | Series Device Data |  |  | Not in table | Not in table
Transmission | Side 1 - Connected Switching Device Name(s) |  |  |  | Series Device Data |  | enter all caps | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME |  | 1) This field is required 2) May not have duplicates within the TO or FROM Station. Warning Only 3) May not contain special characters except for an underscore "_" and a dash "-" 4) May not be > than 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. | T | Alpha
Transmission | Side 1 - Bus Number (PTI Bus Number) |  |  |  | Series Device Data |  | # | SERIES_DEVICE_DATA | SIDE1_PTI_BUS_NUM |  | 1) This field is optional 2) This field must be between 1 - 99,999 | T | Integer
Transmission | Side 2 |  |  |  | Series Device Data |  |  | Not in table | Not in table
Transmission | Side 2 - Connected Switching Device Name(s) |  |  |  | Series Device Data |  | enter all caps | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME |  | 1) This field is required 2) May not have duplicates within the TO or FROM Station 3) May not contain special characters except for an underscore "_" and a dash "-" 4) May not be > than 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. | T | Alpha
Transmission | Side 2 - Bus Number (PTI Bus Number) |  |  |  | Series Device Data |  | # | SERIES_DEVICE_DATA | SIDE2_PTI_BUS_NUM |  | 1) This field is optional 2) This field must be between 1 - 99,999 | T | Integer
Transmission | COMMENTS |  |  |  | Series Device Data |  |  | SERIES_DEVICE_DATA | SD_COMMENTS
Transmission | EFFECTIVE DATE: |  |  |  | Series Device Data |  | mm/dd/yyyy | SERIES_DEVICE_DATA | EFF_DATE |  | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T | Date
Transmission | Transformer Data |  |  |  | Transformer Data |  |  | Not in table | Not in table
Transmission | DESCRIPTION OF CHANGE |  |  |  | Transformer Data |  | List | TRANSFORMER | CHANGE_DESCRIPTION |  | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Alpha
Transmission | TRANSFORMER DETAILS |  |  |  | Transformer Data |  |  | Not in table | Not in table
Transmission | Transformer Name |  |  |  | Transformer Data |  | enter all caps | TRANSFORMER | TRANSFORMER_NAME |  | 1) This field is required 2) May not contain special characters except for an underscore "_" and a dash "-" 3) Warn if >= 14 characters. First 14 characters must be unique. Warning! Transformer Name () should not be >14 characters long or the name will be truncated in the model which requires uniqueness. 4) l Device name must be unique for each Device code for a substation in a SITE | T | Alpha
Transmission | ERCOT Station Name (Station Code or Station Mnemonic) |  |  |  | Transformer Data |  | enter all caps | TRANSFORMER | SUBSTATION_CODE |  | 1) This field is required 2) Must match ERCOT records. Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters. Warning! Station Name () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) substation code should be in Upper case letters. Generate an error if the rule fails | T | Alpha
Transmission | Transformer Code |  |  | UPDATE 02/2012 | Transformer Data |  | Automatic | TRANSFORMER | TRANSFORMER_CODE |  | Concantenate (Site Code_Substation Code_Transformer Name)
Transmission | Transformer Test Report Attached? |  |  |  | Transformer Data |  | Y/N | Not in table | Not in table |  | Select from the list: Y or N | R | Dropdown List
Transmission | Is this transformer in Master / Follower of Current Balancing configuration? |  |  |  | Transformer Data |  | Y/N | TRANSFORMER | MASTER_FOLLOW_FLG |  | 1) This field is required 2) Value must be in the following list: 'Y', 'N' | T | Alpha
Transmission | Master Name (can be same as this transformer) |  |  |  | Transformer Data |  | enter all caps | TRANSFORMER | MASTER_NAME |  | 1) This field is conditionally required if Transformer Data - Is this transformer in Master / Follower of Current Balancing configuration? = 'Y' 2) Warn if >= 14 characters. First 14 characters must be unique. Warning! Master Name () should not be >=14 characters long or the name will be truncated in the model which requires uniqueness. 3) May not contain special characters except for an underscore "_" and a dash "-" 4) Either the Master Name or the Follower Name MUST = Transformer Data - Transformer Name | T | Alpha
Transmission | Follower Name (can be same as this transformer) |  |  |  | Transformer Data |  | enter all caps | TRANSFORMER | FOLLOWER_NAME |  | 1) This field is conditionally required if Transformer Data - Is this transformer in Master / Follower of Current Balancing configuration? = 'Y' 2) May not contain special characters except for an underscore "_" and a dash "-" 3) Either the Master Name or the Follower Name MUST = Transformer Data - Transformer Name 4) Warn if >= 14 characters. First 14 characters must be unique. Warning! Follower Name () should not be >=14 characters long or the name will be truncated in the model which requires uniqueness. | T | Alpha
Transmission | Generation Step-Up Transformer? |  |  |  | Transformer Data |  | Y/N | TRANSFORMER | GSU_TRANSFORMER_FLG |  | 1) This field is required 2) Value must be in the following list: 'Y', 'N' | T | Alpha
Transmission | Zero Sequence Data - Winding Connection Code (1-9) |  | 05/15/2012 Updated Validation to Required. 04/24/2012 Change Column name on RARF Form and removed p.u. lable | ADD 04/2012 | Transformer Data | Transformer_Info.View | p.u. | TRANSFORMER | ZERO_SEQ_DATA_WINDING_CON_CODE |  | 1) This field is Required 2) Data type must be string | R | real
Transmission | Zero Sequence Grounding Resistance For An Impedance Grounded Transformer In P.u. (100 Mva Base) |  |  | ADD 04/2012 | Transformer Data | Transformer_Info.View | p.u. | TRANSFORMER | ZERO_SEQ_GRUND_RESISTANCE_IMPEDANCE_GRUND_TRANS_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R
Transmission | Zero Sequence Grounding Reactance For An Impedance Grounded Transformer In P.u. (100 Mva Base) |  |  | ADD 04/2012 | Transformer Data | Transformer_Info.View | p.u. | TRANSFORMER | ZERO_SEQ_GRUND_REACTANCE_IMPEDANCE_GRUND_TRANS_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R
Transmission | Zero Sequence Resistance In P.u. (100 Mva Base) |  |  | ADD 04/2012 | Transformer Data | Transformer_Info.View | p.u. | TRANSFORMER | ZERO_SEQ_TRANS_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R
Transmission | Zero Sequence Reactance In P.u. (100 Mva Base) |  |  | ADD 04/2012 | Transformer Data | Transformer_Info.View | p.u. | TRANSFORMER | ZERO_SEQ_TRANS_REACTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R
Transmission | Positive Sequence Resistance (100 MVA Base) |  |  | UPDATE 02/2012 | Transformer Data |  | p.u. | TRANSFORMER | SERIES_ RESIST |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R
Transmission | Positive Sequence Reactance (100 MVA Base) |  |  | UPDATE 02/2012 | Transformer Data |  | p.u. | TRANSFORMER | SERIES_ REACT |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R
Transmission | Continuous Rating |  |  |  | Transformer Data |  | MVA | TRANSFORMER | CONTINUOUS_RTG |  | 1) This field is required 2) Value must be <= 2-hr Emergency Rating 3) Value must be <= 15-min Rating 4) Transformer Continuous MVA Rating should be >=HRL or unit will be curtailed down to transformer rating" 5) Continuous must have valid mva rating (eg: will get an ERROR if 9999.00) | T | Integer
Transmission | 2-hr Emergency Rating |  |  |  | Transformer Data |  | MVA | TRANSFORMER | EMGCY_RTG_2HR |  | 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be <= 15-min Rating 4) 2hr-rating must have valid mva rating (9999.00 mva will produce a WARNING) | T | Integer
Transmission | 15-min Rating |  |  |  | Transformer Data |  | MVA | TRANSFORMER | RTG_15MIN |  | 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be >= 2-hr Emergency Rating 4) 15min rating must have valid mva rating(9999.00 mva will produce a WARNING), also if 2hr is 9999.00 then the only valid entry for 15min is 9999.00 or it will give an ERROR. | T | Integer
Transmission | Unit(s) associated with this transformer |  |  |  | Transformer Data |  | enter all caps | TRANSFORMER_UNITS | TRANSFORMER_UNIT_CODE |  | 1) This field is conditionally required - if Generation Step-up = 'Y', this is required 2) Value(s) must be <=17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. 3) Warn if the unit name is not in the Unit Info - GEN or Unit Info - CC or Unit Info - Wind 4) Generate an ERROR when Non GSU Transformers that have entered associated units. | T | Alpha
Transmission | HIGH SIDE VOLTAGE INFORMATION |  |  |  | Transformer Data |  |  | Not in table | Not in table
Transmission | High Side Voltage Level (no-load) |  |  |  | Transformer Data |  | kV | TRANSFORMER | HIGH_NOLOAD |  | 1) This field is required 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 5) The value must be >= Low Voltage Level (no-load) | T | Float
Transmission | High Side Voltage Level (PTI) |  |  |  | Transformer Data |  | # | TRANSFORMER | HIGH_PTI |  | 1) This field is optional 2) This field must be between 1 - 99,999 | T | Integer
Transmission | High Side Voltage Connection - Wye or Delta |  |  |  | Transformer Data |  | List | TRANSFORMER | HIGH_CONNECTION |  | 1) This field is required 2) Value must be of the following: 'Wye', 'Delta' | T | Alpha
Transmission | High Side Voltage Connected devices (list on separate lines) |  |  |  | Transformer Data |  |  | TRANSFORMER_DEVICES | DEVICE_NAME |  | 1) This field is required a) Error: if High Side Voltage >= 60kV and Low Side Voltage >1kV b) Warn: if High Side Voltage < 60kV and Low Side Voltage = 1kV 2) No special characters except an underscore or a dash 3) Warn if >= 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. 4) connected devices listed in transformer tab should exist in the breaker switch tab. Generate an error when the rule fails | T | Alpha
Transmission | High Side Manufactured Nominal Voltage |  |  |  | Transformer Data |  | kV | TRANSFORMER | HIGH_MANU_VOLT |  | 1) This field is required 2) If value > 60kV Accepted if value (using 5%) Deviates < ¦3.45¦ kV from 69 Deviates < ¦6.9¦ kV from 138 Deviates < ¦17.25¦ kV from 345 Warn if value (using >= 5% and <10%) Deviates > = ¦3.45¦ but deviates < ¦6.9¦ from 69 Deviates >= ¦6.9¦ but deviates < 13.8 from 138 Deviates >= ¦17.25¦ but deviates < 34.5 from 345 Error if value (using > =10%) Deviates >= ¦6.9¦ kV from 69 Deviates >= ¦13.8¦kV from 138 Deviates >= ¦34.5¦kV from 345 3) Warn if value > 345 4) The value must be > 0 5) High Side Manufactured Nominal Voltage >= Low Side Manufactured Nominal Voltage 6) High Side Manufactured Nominal Voltage should be > Voltage at Lowest Tap Position and < Voltage at Highest Tap Position 7) Transformer High Side Manufactured Nominal Voltage should equal to Voltage at Highest Tap - Step Size voltage to reach Nominal Tap. | T | Float
Transmission | LOW SIDE VOLTAGE INFORMATION |  |  |  | Transformer Data |  |  | Not in table | Not in table
Transmission | Low Side Voltage Level (no-load) |  |  |  | Transformer Data |  | kV | TRANSFORMER | LOW_NOLOAD |  | 1) This field is required 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 5) The value must be <= High Voltage Level (no-load) 6) If Generator Step-up Transformer = 'Y' AND Low Side Voltage Level (no-load) > 1kV AND Then the Low Side Voltage Level (no-load) must be equal to Unit Info - GEN / CC / WIND - Unit Generating Voltage | T | Float
Transmission | Low Side Voltage Level (PTI) |  |  |  | Transformer Data |  | # | TRANSFORMER | LOW_PTI |  | 1) This field is optional 2) This field must be between 1 - 99,999 | T | Integer
Transmission | Low Side Voltage Connection - Wye or Delta |  |  |  | Transformer Data |  | List | TRANSFORMER | LOW_CONNECTION |  | 1) This field is required 2) Value must be of the following: 'Wye', 'Delta' | T | Alpha
Transmission | Low Side Voltage Connected device(s) (list on separate lines) |  |  |  | Transformer Data |  |  | TRANSFORMER_DEVICES | DEVICE_NAME |  | 1) This field is required a) Error: if High Side Voltage >= 60kV and Low Side Voltage >1kV b) Warn: if High Side Voltage < 60kV and Low Side Voltage = 1kV 2) Warn if >= 17 characters. 3) No special characters except an underscore "_" or a dash "-" 4) connected devices listed in transformer tab should exist in the breaker switch tab. Generate an error when the rule fails | T | Alpha
Transmission | Low Side Manufactured Nominal Voltage |  |  |  | Transformer Data |  | kV | TRANSFORMER | LOW_MANU_VOLT |  | 1) This field is required 2) If the value >= 69kv: Accepted if value (using 5%) Deviates < ¦3.45¦ kV from 69 Deviates < ¦6.9¦ kV from 138 Deviates < ¦17.25¦ kV from 345 Warn if value (using >= 5% and <10%) Deviates > = ¦3.45¦ but deviates < ¦6.9¦ from 69 Deviates >= ¦6.9¦ but deviates < 13.8 from 138 Deviates >= ¦17.25¦ but deviates < 34.5 from 345 Error if value (using > =10%) Deviates >= ¦6.9¦ kV from 69 Deviates >= ¦13.8¦kV from 138 Deviates >= ¦34.5¦kV from 345 3) Warn if value > 345 4) The value must be > 0 5) High Side Manufactured Nominal Voltage >= Low Side Manufactured Nominal Voltage 6) Low Side Manufactured Nominal Voltage should equal (Voltage at Lowest Tap) + (Step size voltage to reach Nominal tap) | T | Float
Transmission | VOLTAGE REGULATION |  |  |  | Transformer Data |  |  | Not in table | Not in table
Transmission | Automatic Voltage Regulation |  |  |  | Transformer Data |  | Y/N | TRANSFORMER | AUTO_VOLT_REG |  | 1) This field is required 2) Value must be from the following list: 'Y', 'N' 3) AVR is expected to be 'Y' when total number of tap positions >=16. Warn if "Automatic Voltage Regulation" = 'N' and Total Number of Tap Positions>=16 | T | Alpha
Transmission | Does Transformer have a Load Tap Changer? |  |  |  | Transformer Data |  | Y/N | TRANSFORMER | LOADTAP_CHNGR_FLG |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) Value must be from the following list: 'Y', 'N' 3) Load Tap Changer is expected to be 'Y' when total number of tap positions >=16. Warn if "Load Tap Changer" = 'N' and Total Number of Tap Positions>=16 | T | Alpha
Transmission | Location of Tap Changer High or Low |  |  |  | Transformer Data |  | List | TRANSFORMER | LOCN_TAP_CHNGR |  | 1) This field is conditionally required if 'Does Transformer have a Load Tap Changer ?' = 'Y' 2) Value must be of the following: 'HIGH', 'LOW' 3) Load Tap Changer should be 'Y' when AVR is 'Y'. Generate an error if Load Tap Changer is 'N' and AVR = 'Y'. | T | Alpha
Transmission | Base Kv of Regulated Side |  |  |  | Transformer Data |  | kV | TRANSFORMER | REG_KV_BASE |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 5) The value must be >= Low Voltage Level (no-load) | T | Float
Transmission | Target Kv of Regulated Side |  |  |  | Transformer Data |  | kV | TRANSFORMER | REG_KV_TARGET |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) Value must be > 0 | T | Float
Transmission | Acceptable Deviation of Target Voltage in Percent |  | 05/03/2012 removed percent from label on form |  | Transformer Data |  |  | TRANSFORMER | ACCEPT_DEV_VOLT_TARGET |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) Value must not exceed 50% | T | Percentage
Transmission | COMMENTS |  |  |  | Transformer Data |  |  | TRANSFORMER | COMMENTS_TRANSFORMER
Transmission | EFFECTIVE DATE: |  |  |  | Transformer Data |  | mm/dd/yyyy | TRANSFORMER | EFF_DATE |  | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T | Date
Transmission | Transformer Tap Settings |  |  |  | TRANSFORMER TAP SETTINGS |  |  | Not in table | Not in table | Not in table
Transmission | DESCRIPTION OF CHANGE |  | Added 03/26/2012 | Add 04/2012 | Transformer Tap Settings | Transformer_HighTaps.View and Transformer_LowTaps.View | List | TRANSFORMER_TAP_SETTINGS | CHANGE_DESCRIPTION |  | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | T | Alpha
Transmission | Transformer Code |  |  | Added to RARF Form for 02/2012 | Transformer Tap Settings |  | Automatic | TRANSFORMER_TAP_SETTINGS | TRANSFORMER_CODE |  | Concantenate (Site Code_Substation Code_Transformer Name)
Transmission | High-Low Flag |  |  | Added to RARF Form for 02/2012 | Transformer Tap Settings |  | List | TRANSFORMER_TAP_SETTINGS | LOW_HIGH_FLG |  | 1) This field is conditioally reguired.This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be of the following: High or Low
Transmission | TAP SETTINGS |  |  |  | Transformer Tap Settings |  |  | Not in table | Not in table
Transmission | Tap position at Manufactured Nominal Voltage |  |  |  | Transformer Tap Settings |  | # | TRANSFORMER_TAP_SETTINGS | MANU_VOLT_TAP_POS |  | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field must be left blank if Low Voltage Level = 1 2) Note: this value may be negative 3. Value must be between Lowest and Highest Tap position 4)All tap information is required if it exists on either the LTC or Fixed side. | T | Integer
Transmission | Total Number of Tap Positions |  |  |  | Transformer Tap Settings |  | # | TRANSFORMER_TAP_SETTINGS | TOTAL_NUM |  | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be >= 2 3) Warn if value >= 16 and "Automatic Voltage Regulation" = 'N' Warn if value >=16 and "Load Tap Changer" = 'N' | T | Integer
Transmission | Normal Tap Position |  |  |  | Transformer Tap Settings |  | # | TRANSFORMER_TAP_SETTINGS | NORMAL_POS |  | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out. Note that it is valid for both, Low and High Tap settings to be filled out. Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be >= Low Tap Settings - Lowest Tap Position 3) Value must be <= Low Tap Settings - Highest Tap Position 4) Note: this value may be negative | T | Integer
Transmission | Lowest Tap Position |  |  |  | Transformer Tap Settings |  | # | TRANSFORMER_TAP_SETTINGS | LOWEST_POS |  | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be <= Low Tap Settings - Highest Tap Position 3) Note: this value may be negative | T | Integer
Transmission | Voltage at Lowest Tap Position |  |  |  | Transformer Tap Settings |  | kV | TRANSFORMER_TAP_SETTINGS | LOWEST_VOLT |  | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be <= Low Tap Settings - Voltage at Highest Tap Position 3) Value must be < High Tap Settings - Voltage at Lowest Tap Position 4) Value must be >= 0 | T | Float
Transmission | Highest Tap Position |  |  |  | Transformer Tap Settings |  | # | TRANSFORMER_TAP_SETTINGS | HIGHEST_POS |  | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out. Note that it is valid for both, Low and High Tap settings to be filled out. Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be >= Low Tap Settings - Low Tap Position 3) Note: this value may be negative | T | Integer
Transmission | Voltage at Highest Tap Position |  |  |  | Transformer Tap Settings |  | kV | TRANSFORMER_TAP_SETTINGS | HIGHEST_VOLT |  | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out. Note that it is valid for both, Low and High Tap settings to be filled out. Second Condition: This field may be left blank if Low Voltage Level = 1 2) Value must be >= Low Tap Settings - Voltage at Lowest Tap Position 3) Value must be <= High Tap Settings - Voltage at Highest Tap Position 4) Value must be >= 0 | T | Float
Transmission | Size of each Voltage Step |  |  |  | Transformer Tap Settings |  | kV | TRANSFORMER_TAP_SETTINGS | STEP_VOLT |  | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field may be left blank if Low Voltage Level = 1 2) Value must > 0 3) Warn if < 0.002 * Low Side Voltage Level (no-load) 4) Warn if > 0.05 * Low Side Voltage Level (no-load) | T | Float
Transmission | Load Data |  |  |  | Load Data |  |  | Not in table | Not in table
Transmission | DESCRIPTION OF CHANGE |  |  |  | Load Data |  | List | LOADS | CHANGE_DESCRIPTION
Transmission | Load Data |  | Added 03/26/2012 |  | Load Data |  |  | Not in table | Not in table
Transmission | Ercot Station Code Mnemonic |  |  |  | Load Data |  | enter all caps | LOADS | SUBSTATION_CODE |  | 1) This field is required 2) Must match ERCOT records. Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters 5) substation code should be in Upper case letters. Generate an error if the rule fails | L | Alpha
Transmission | Load Name |  |  |  | Load Data |  | enter all caps | LOADS | LOAD_NAME |  | 1) This field is required 2) May not contain special characters except for an underscore "_" and a dash "-" 2) Warn if >= 14 characters. First 14 characters must be unique. 3)Warning! ERCOT Load Name() should not be >= 14 characters long or the name will be truncated in the model which requires uniqueness. 4) Load Name can not be duplicated in a Station | L | Alpha
Transmission | Load Code |  |  | UPDATE 02/2012 | Load Data |  | Automatic | LOADS | LOAD_CODE |  | Concantenate (Site Code_Substation Code_Lode Name
Transmission | Load Voltage Level |  |  |  | Load Data |  | kV | LOADS | VOLATGE |  | 1) This field is required 2) Value must be >= 0 3) If the value >= 69kv it must be 69,138, or 345 | T | Float
Transmission | PTI Bus Number |  |  |  | Load Data |  | # | LOADS | PTI_BUS_NUM |  | 1) This field is optional 2) This field must be between 1 - 99,999 | T | Integer
Transmission | Average Load Under Normal Operations |  |  |  | Load Data |  | MW | LOADS | AVG_LOAD |  | 1) This field is required 2) It should be >0 and generate a warning if = 0 | T | Float
Transmission | Average Mvar Under Normal Operations |  |  |  | Load Data |  | MVAR | LOADS | AVG_MVAR |  | 1) This field is required 2) It should be >0 and generate a warning if = 0 | T | Float
Transmission | Connected Devices |  |  |  | Load Data |  |  | Not in table | Not in table
Transmission | Device Name(s) - that this load is physically connected to |  |  |  | Load Data |  |  | LOAD_DEVICES | LOAD_DEVICE_NAME |  | 1) This field is required 2) No special characters except an underscore or a dash 3) Warn if >= 17 characters. First 17 characters must be unique. Warning! ERCOT Device Name() should not be >=17 characters long or the name will be truncated in the model which requires uniqueness. 4) 'Connected Device that this load is directly connected to' Field in Load Data Tab should be defined either in the Breaker/Switch Tab(if the connected device is a switch Name) or in the Transformer Tab(if the connected device is a Transformer Name). Produce an Error when connected device is missing in the Breaker_switch Tab. 'Error! Unique controlling device must also exist in the 'BREAKER_SWITCH Tab' | T | Alpha
Transmission | Comments |  |  |  | Load Data |  |  | LOADS | LOAD_COMMENTS
Transmission | Effective Date: |  |  |  | Load Data |  | MM/DD/YYYY | LOADS | EFF_DATE |  | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | T | Date
Transmission | PUN LOAD |  |  |  | PUN Load |  |  | Not in table | Not in table
Transmission | Station Details |  |  |  | PUN Load |  |  | Not in table | Not in table
Transmission | Station Code |  | 03/27/2012 updated | ADD 04/2012 | PUN Load | PUN_LOAD.View | enter all caps | PUN_LOAD | SUBSTATION_CODE |  | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Not null 3) All caps
Transmission | Load Name |  | 03/27/2012 updated | ADD 04/2012 | PUN Load | PUN_LOAD.View | List | PUN_LOAD | PUN_LOAD_NAME |  | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Value should following the following convention SiteCode_LoadName. Load Name (Load Name) should be as it appears in the ERCOT Model 3) Not Null | L | Alpha
Transmission | Load Code |  | 03/27/2012 updated | ADD 04/2012 | PUN Load | PUN_LOAD.View | Automatic | PUN_LOAD | PUN_LOAD_CODE |  | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Not null
Transmission | 168 HR Data |  |  |  | PUN Load |  |  | Not in table | Not in table
Transmission | Hour Ending |  | 03/27/2012 updated | ADD 04/2012 | PUN Load | PUN_LOAD.View | Automatic | PUN_LOAD | HOUR_ENDING |  | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Not null
Transmission | Day of Week |  | 03/27/2012 updated | ADD 04/2012 | PUN Load | PUN_LOAD.View | Automatic | PUN_LOAD | DAY |  | 1) These fields are conditionally required if "Private Network - Private Network?" = 'Y' and for each Load identified 2) Not Null
Transmission | MW |  | 03/27/2012 updated | ADD 04/2012 | PUN Load | PUN_LOAD.View |  | PUN_LOAD | MW |  | 1) This field is conditionally required if "Private Network - Private Network?" = 'Y' 2) Not null. Must be numeric. 3) Value must be >= 0 (for zero load, place a 0 in that space)
Note on H1: This column represents the name of the SQL file/view that uses the field. The name is the same for Delta and Aufit reports unless otherwise noted. The full filename convention is dbo.[RARFAUDIT or DELTA].[Source Report Name].sql

## Sheet10 (hidden)
Field/Section Type: R- Required( Not null),O= Optional ,C =Conditional
Validation Type: B = Basic Validation , DVB = Data Validation based on Business Rules , DVE = Data Validation with the existing record in ERCOT
Format /Data type: Numeric, Integer , Character, Date, Dropdown List
Source--> Represents the source of the Validation Rules
RARF FORM TYPE | RARF DATA FIELD | Field Updates | Change Description | RARF Tab | Source Report Name | Label | TABLE | DB Field | Business Rules/Basic UI validations | Field/ Tab Type | Data type
Distributed Generation | Site Information | 04/24/2012 combined into General_Site_ESIID Information sheet 04/12/2012 Updated RARF TAB |  | Site Info - DG General Information - DG |  |  | Not in table | Not in table
Distributed Generation | Primary Contact | 04/24/2012 combined into General_Site_ESIID Information sheet |  | General Information |  |  | Not in table | Not in table
Distributed Generation | Printed Name: | 04/24/2012 combined into General_Site_ESIID Information sheet |  | General Information |  |  | Not in table | FORM_COMP_DT |  | R | Character
Distributed Generation | Title: | 04/24/2012 combined into General_Site_ESIID Information sheet |  | General Information |  |  | Not in table | FORM_COMP_DT |  | R | Character
Distributed Generation | Phone Number: | 04/24/2012 combined into General_Site_ESIID Information sheet |  | General Information |  |  | Not in table | FORM_COMP_DT |  | R | Character
Distributed Generation | E-mail Address: | 04/24/2012 combined into General_Site_ESIID Information sheet |  | General Information |  |  | Not in table | FORM_COMP_DT |  | R | Character
Distributed Generation | Fax Number: | 04/24/2012 combined into General_Site_ESIID Information sheet |  | General Information |  |  | Not in table | FORM_COMP_DT |  | O | Character
Distributed Generation | Secondary Contact | 04/24/2012 combined into General_Site_ESIID Information sheet |  | General Information |  |  | Not in table | Not in table
Distributed Generation | Printed Name: | 04/24/2012 combined into General_Site_ESIID Information sheet |  | General Information |  |  | Not in table | Not in table
Distributed Generation | Title: | 04/24/2012 combined into General_Site_ESIID Information sheet |  | General Information |  |  | Not in table | Not in table
Distributed Generation | Phone Number: | 04/24/2012 combined into General_Site_ESIID Information sheet |  | General Information |  |  | Not in table | Not in table
Distributed Generation | E-mail Address: | 04/24/2012 combined into General_Site_ESIID Information sheet |  | General Information |  |  | Not in table | Not in table
Distributed Generation | Fax Number: | 04/24/2012 combined into General_Site_ESIID Information sheet |  | General Information |  |  | Not in table | Not in table
Distributed Generation | Unit Info - DG | 04/24/2012 combined into General_Site_ESIID Information sheet |  | Unit Info - DG |  |  | Not in table | Not in table
Distributed Generation | Generator Details |  |  | Unit Info - DG |  |  | Not in table | Not in table
Distributed Generation | Unit Name |  | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | all caps | NON_MODELED | UNIT_NAME | 1.This field is not null. Data type: Character. 2.All letters should be capital 3. Should not allow spaces | R | Character | PASSED
Distributed Generation | Unit Code |  | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | Automatic | NON_MODELED | UNIT_CODE | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Character | PASSED
Distributed Generation | Unit Dates |  |  | Unit Info - DG |  |  | Not in table | Not in table | 2.All letters should be capital
Distributed Generation | Unit Start Date |  | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | mm/dd/yyyy | NON_MODELED | UNIT_MRD_ST_DT | This field is not null. Format should be: MM/DD/YYYY | R | Date | PASSED
Distributed Generation | Unit End Date |  | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | mm/dd/yyyy | NON_MODELED | UNIT_END_DT | This field is optional. Format should be: MM/DD/YYYY | O | Date | PASSED
Distributed Generation | Fuel Information |  |  | Unit Info - DG |  |  | Not in table | Not in table
Distributed Generation | Name Plate Rating | 05/01/2012 Updated LABEL to MW | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | MW | NON_MODELED | NAME_PLT_RTG_MW | 1. Not Null 2. Numeric Value | R | Numeric | PASSED
Distributed Generation | Technology Type | 05/01/2012 UPDATED to match form | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | List | NON_MODELED | TECHNOLOGY_TYPE | 1. Select from drop down list: (FS) Fossil Fuel Steam , (GT) Gas Turbine, (H) Hydro, (W) Wind, (S) Solar, (X) Other 2. Not null | R | Dropdown List | PASSED
Distributed Generation | Name Plate Rating |  | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | MVA | NON_MODELED | NAME_PLT_RTG_MVA | 1. Not Null 2. Numeric Value | R | Numeric | PASSED
Distributed Generation | Renewable |  | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | Y/N | NON_MODELED | RENEWABLE_FLG | 1. Select from the list: Y or N 2. Not Null | R | Dropdown List | PASSED
Distributed Generation | Renewable/Offset |  | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | List | NON_MODELED | RENEWABLE_OFFSET | 1. Select from the list: NA, RN, OS 2. Not Null | R | Dropdown List | PASSED
Distributed Generation | If Wind, Number of Turbines |  | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | # | NON_MODELED | NUM_WIND_TURBINES | 1. Data type: Integer 2. N/A is not valid. Leave blank if unknown. |  |  | PASSED
Distributed Generation | Physical Unit Type |  | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | List | NON_MODELED | PHYS_UNIT_TYPE | 1. Select from drop down list: CA, CC, CE, CS, CT, FC, GT, HY, IC, NA, OT, PS, PV, ST, WT 2. Not null | R | Dropdown List | PASSED
Distributed Generation | Primary Fuel Type |  | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | List | NON_MODELED | PRIM_FUELTYPE | 1. Select from drop down list: AB, BFG, BIT, BL, DFO, GEO, JF, KER, LFG, LIG, MSW, NA, NG, NUC, OBG, OBL, OBS, OG, OO, OTH, PC, PG, RFO, SLW, STM, SUB, SUN, T, TDF, WAT, WDL, WDS, WH, WND, WOC 2. Not null | R | Dropdown List | PASSED
Distributed Generation | Secondary Fuel Type |  | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | List | NON_MODELED | SEC_FUELTYPE | 1. Select from drop down list: AB, BFG, BIT, BL, DFO, GEO, JF, KER, LFG, LIG, MSW, NA, NG, NUC, OBG, OBL, OBS, OG, OO, OTH, PC, PG, RFO, SLW, STM, SUB, SUN, T, TDF, WAT, WDL, WDS, WH, WND, WOC 2. Not null | R | Dropdown List | PASSED
Distributed Generation | Private Network Info |  |  | Unit Info - DG |  |  | Not in table | Not in table
Distributed Generation | Private Network / Cogen |  | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | Y/N | NON_MODELED | PUN_FLG | 1. Select from the list: Y or N 2. Not Null | R | Dropdown List | PASSED
Distributed Generation | Amount of Self Serve for Cogen |  | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | MW | NON_MODELED | AMT_SELFSRV_COGEN | Required if Private Network / Cogen is 'Y' | R | Dropdown List | PASSED
Distributed Generation | Private Network Net Interchange |  | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | MW | NON_MODELED | PRIVATE_NWK_NET_INTERCHANGE | Required if Private Network / Cogen is 'Y' | R | Dropdown List | PASSED
Distributed Generation | Private Network Gross Unit MW |  | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | MW | NON_MODELED | PRIVATE_NET_GROSS_UNT_MW | Required if Private Network / Cogen is 'Y' | R | Dropdown List | PASSED
Distributed Generation | Private Network Gross Unit MVAR |  | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | MVAR | NON_MODELED | PRIVATE_NET_GROSS_UNT_MVAR | Required if Private Network / Cogen is 'Y' | R | Dropdown List | PASSED
Distributed Generation | Generic Info |  |  | Unit Info - DG |  |  | Not in table | Not in table
Distributed Generation | Generic Fuel Category | 05/01/2012 UPDATED to match form 03/9/2012 Corrected Field name | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | List | NON_MODELED | GEN_FUEL_CAT | 1. Select from drop down list: 1) Coal and Lignite 2) Combined Cycle greater than 90 MW 3) Combined Cycle less than or equal to 90 MW 4) Diesel (and all other diesel or gas-fired Resources) 5) Gas Steam Non-reheat Boiler or Boiler without air-preheater 6) Gas Steam Reheat Boiler 7) Gas Steam Supercritical Boiler 8) Hydro 9) Nuclear 10) Other Renewable (i.e. non-hydro renewable Resources) 11) Power Storage 12) Simple Cycle greater 13) Simple Cycle less than or equal to 90 MW 2.Not null | R | Dropdown List | PASSED
Distributed Generation | Generic Start-up / Operating Category | 05/01/2012 UPDATED to match form 03/9/2012 Corrected Field name | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | List | NON_MODELED | GEN_STUP_OPER_CAT | 1. Select from drop down list: 1) Base Load 2) Gas-Cyclic 3) Gas-Intermediate 4) Gas-Peaking 5) Renewable (Including Hydro) 2. Not null | R | Dropdown List | PASSED
Distributed Generation | Resource Owner Data |  |  | Unit Info - DG |  |  | Not in table | Not in table
Distributed Generation | Resource Entity Name |  | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View | all caps | NON_MODELED | RE_NAME | 1. Not null 2. Do not allow any special characters except spaces and dashes. | R | Character | PASSED
Distributed Generation | Resource Entity Duns Number |  | ADD 04/2012 | Unit Info - DG | DG_UnitInfo.View |  | NON_MODELED | RE_DUNS | 1. Not null 2. Must match with the data existing in Siebel 3. Data type: varchar (as sometimes the value contains # with a leading zero) 4. Either a 9 or 13 digit DUNS number | R | Character | PASSED
Note on G6: This column represents the name of the SQL file/view that uses the field. The name is the same for Delta and Aufit reports unless otherwise noted. The full filename convention is dbo.[RARFAUDIT or DELTA].[Source Report Name].sql

## Sheet11 (hidden)
CC | SITE CODE | REMOVED FROM CC FORM | ADD 02/2012 |  | Private Network - Unit - CC |  | Automatic | CCUNIT | SITE_CODE | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
Wind | SITE CODE | Removed from Form 03/05/2012 | ADD 02/2012 |  | Protection - Wind |  | Automatic | WIND | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk
Distributed Generation | General Information - ALL | 05/23/2012 REMOVED FIELD 04/24/2012 combined into General_Site_ESIID Information sheet |  | General Information - DG | General Information |  |  | Not in table | Not in table |  |  | R
Distributed Generation | Submittal Information | 05/23/2012 REMOVED FIELD 04/24/2012 combined into General_Site_ESIID Information sheet |  | General Information - DG | General Information | GeneralInformation.View |  | Not in table | Not in table
Distributed Generation | Resource Entity DUNS #: | 05/23/2012 REMOVED FIELD 04/24/2012 combined into General_Site_ESIID Information sheet | ADD 04/2012 | General Information - DG | General Information | GeneralInformation.View |  | SITECODES & RE_RARF | RE_DUNS |  | 1. Not null 2. Must match with the data existing in Siebel 3. Data type: varchar (as sometimes the value contains # with a leading zero) 4. Either a 9 or 13 digit DUNS number | R | Character | B,DVE
Distributed Generation | Generator Site Code | 05/23/2012 REMOVED FIELD 04/24/2012 combined into General_Site_ESIID Information sheet 05/23/2012 REMOVED FIELD 04/12/2012 Updated RARF TAB | ADD 04/2012 |  | Site Info - DG General Information - DG | DG_SiteInfo.View | all caps | SITECODES | SITE_CODE |  | 1. Not null 2. All should be capital letters | R | Character | B,DVB
Distributed Generation | Address | 05/23/2012 REMOVED FIELD 04/24/2012 combined into General_Site_ESIID Information sheet 04/12/2012 Updated RARF TAB | ADD 04/2012 |  | Site Info - DG General Information - DG | DG_SiteInfo.View |  | SITECODES | STREET_ADDRESS |  | Not null | R | Character | B
Distributed Generation | State | 05/23/2012 REMOVED FIELD 04/24/2012 combined into General_Site_ESIID Information sheet 04/12/2012 Updated RARF TAB | ADD 04/2012 |  | Site Info - DG General Information - DG | DG_SiteInfo.View |  | SITECODES | STATE |  | Not null | R | Character | B
Distributed Generation | County | 05/23/2012 REMOVED FIELD 04/24/2012 combined into General_Site_ESIID Information sheet 04/12/2012 Updated RARF TAB | ADD 04/2012 |  | Site Info - DG General Information - DG | DG_SiteInfo.View |  | SITECODES | COUNTY |  | Not null | R | Character | B
Distributed Generation | Site In-Service Date | 05/23/2012 REMOVED FIELD 04/24/2012 combined into General_Site_ESIID Information sheet 04/12/2012 Updated RARF TAB | ADD 04/2012 |  | Site Info - DG General Information - DG | DG_SiteInfo.View | mm/dd/yyyy | SITECODES | SITE_IN_SRVC_DT |  | 1. Must be earlier than Site-Stop Service Date 2. mm/dd/yyyy format 3. Not null | R | Date | B,DVB
Distributed Generation | Site Stop Service Date | 05/23/2012 REMOVED FIELD 04/24/2012 combined into General_Site_ESIID Information sheet 04/12/2012 Updated RARF TAB | ADD 04/2012 |  | Site Info - DG General Information - DG | DG_SiteInfo.View | mm/dd/yyyy | SITECODES | SITE_STOP_SRVC_DT |  | 1. Must be later than Site In-Service Date 2. mm/dd/yyyy format | O | Date | B,DVB
Distributed Generation | Is generation behind a NOIE Settlement Meter Point? | 05/23/2012 REMOVED FIELD 05/02/2012 Removed valadation for this field and form also removed from form. 04/24/2012 combined into General_Site_ESIID Information sheet 04/12/2012 Updated RARF TAB | ADD 04/2012 |  | Site Info - DG General Information - DG | DG_SiteInfo.View | Y/N | SITECODES | RE_BHND_NOIE_SMP_FLG |  | 1. Select from the list: Y or N 2. Not Null | R | Dropdown List | B,DVB
Distributed Generation | TDSP Providing Service To Gen Site | 05/23/2012 REMOVED FIELD 04/24/2012 combined into General_Site_ESIID Information sheet 04/12/2012 Updated RARF TAB | ADD 04/2012 |  | Site Info - DG General Information - DG | DG_SiteInfo.View | List | SITECODES | TDSP_PROVIDING_SVC |  | Not null
Distributed Generation | TDSP DUNS Number | 05/23/2012 REMOVED FIELD 04/24/2012 combined into General_Site_ESIID Information sheet 04/12/2012 Updated RARF TAB | ADD 04/2012 |  | Site Info - DG General Information - DG | DG_SiteInfo.View | Automatic | SITECODES | TDSP_DUNS |  | 1. Not null 2. Data type: varchar (as sometimes the value contains # with a leading zero) 3. Either a 9 or 13 digit DUNS number | R | Integer | B,DVE
Distributed Generation | ESI-ID if H9 is "No" | 05/23/2012 REMOVED FIELD 05/02/2012 Removed valadation for this field and form also removed from form. 04/24/2012 combined into General_Site_ESIID Information sheet 04/12/2012 Updated RARF TAB | ADD 04/2012 |  | Site Info - DG General Information - DG | DG_SiteInfo.View |  | SITECODES | ESIID _NOT_BEHIND_NOIE_SETMENT_MTR_PNT |  | Not Required if Resource Behind NOIE Settlement point is 'Y' | C | Character | B,DVE
Distributed Generation | ERCOT Read | 05/23/2012 REMOVED FIELD 04/24/2012 combined into General_Site_ESIID Information sheet 04/12/2012 Updated RARF TAB | ADD 04/2012 |  | Site Info - DG General Information - DG | DG_SiteInfo.View | Y/N | SITECODES | ERCOT_READ |  | 1. Select from the list: Y or N 2. Not Null | R | Dropdown List | B,DVB
Distributed Generation | Number of EPS Primary meters | 05/23/2012 REMOVED FIELD 04/24/2012 combined into General_Site_ESIID Information sheet 04/12/2012 Updated RARF TAB | ADD 04/2012 |  | Site Info - DG General Information - DG | DG_SiteInfo.View | # | SITECODES | NUM_EPS_METERS |  | Not null | R | Integer | B
Distributed Generation | Is Resource claiming status as a Non-Modeled Generator as defined in ERCOT Protocol Section 2, Resource | 05/23/2012 REMOVED FIELD 04/24/2012 combined into General_Site_ESIID Information sheet 04/12/2012 Updated RARF TAB | ADD 04/2012 |  | Site Info - DG General Information - DG | DG_SiteInfo.View | Y/N | SITECODES | RE_CLAIM_NONMOD_STATUS |  | 1. Select from the list: Y or N 2. Not Null | R | Dropdown List | B,DVB
Distributed Generation | Is Resource >10 MW? | 05/23/2012 REMOVED FIELD 04/24/2012 combined into General_Site_ESIID Information sheet 04/12/2012 Updated RARF TAB | ADD 04/2012 |  | Site Info - DG General Information - DG | DG_SiteInfo.View | Y/N | SITECODES | RES_GREAT_TEN_MW |  | 1. Select from the list: Y or N 2. Not Null | R | Dropdown List | B,DVB
Generation | Zero Sequence Resistance In P.u. (100 Mva Base) | 04/24/2012 Remove field from database and form. No validation. | ADD 04/2012 |  | Planning - GEN | Audit - Planning_GEN.View Delta -Planning_GENERATION.View | p.u. | GENERATION | ZERO_SEQ_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Generation | Zero Sequence Reactance In P.u. (100 Mva Base) | 04/24/2012 Remove field from database and form. No validation. | ADD 04/2012 |  | Planning - GEN | Audit - Planning_GEN.View Delta -Planning_GENERATION.View | p.u. | GENERATION | ZERO_SEQ_Reactance_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
CC | Zero Sequence Resistance In P.u. (100 Mva Base) | 04/24/2012 Remove field from database and form. No validation. | ADD 04/2012 |  | Planning - CC | Planning_CC.View | p.u. | CCUNIT | ZERO_SEQ_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
CC | Zero Sequence Reactance In P.u. (100 Mva Base) | 04/24/2012 Remove field from database and form. No validation. | ADD 04/2012 |  | Planning - CC | Planning_CC.View | p.u. | CCUNIT | ZERO_SEQ_Reactance_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Wind | Zero Sequence Resistance In P.u. (100 Mva Base) | 04/24/2012 Remove field from database and form. No validation. | ADD 04/2012 |  | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | ZERO_SEQ_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team
Wind | Zero Sequence Reactance In P.u. (100 Mva Base) | 04/24/2012 Remove field from database and form. No validation. | ADD 04/2012 |  | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | ZERO_SEQ_Reactance_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | R |  |  | Planning Team

## SOLAR (hidden)
Field/Section Type: R- Required( Not null),O= Optional ,C =Conditional
Validation Type: B = Basic Validation , DVB = Data Validation based on Business Rules , DVE = Data Validation with the existing record in ERCOT
Format /Data type: Numeric, Integer , Character, Date, Dropdown List
Source--> Represents the source of the Validation Rules
RARF FORM TYPE | RARF DATA FIELD | Field Updates | Change Description |  | RARF Tab | Source Report Name | Label | TABLE | DB Field | EXCEL | Business Rules/Basic UI validations | Field/ Tab Type | Source | Destination Application
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | General and Site Information |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | This tab is Required for all Resource Entities (Load and Generation Resources) | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | This submittal is for | Updated 03/09/2012 validation rule to match view |  |  | General and Site Information |  |  | SITECODES | SUBMIT_REASON | Not null. Select from the list: New Site, Revision, Addition of Units, Deletion of Units | Not null. Select from the list: New Site, Revision, Addition of Unit(s), Deletion of Unit(s)* | R
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Submittal Information |  |  |  | General and Site Information |  |  | Not in table | Not in table | Not null. Select from the list: New Site, Revision, Addition of Units, Deletion of Units | Not null. Select from the list: New Site, Revision, Addition of Units, Deletion of Units | R | RARF Glossary Version 4.0 4/RARF Guide version 4.0/ Angela Moy
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Date Form Completed: |  |  |  | General and Site Information |  |  | SITECODES | FORM_COMP_DT | Optional | Not null. Equal to the System Date. Date Format should be mm/dd/yyyy | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Resource Entity Submitting Form: | 03/09/2012 Updated Validation | ADD 04/2012 |  | General and Site Information | GeneralInformation.View |  | RE_RARF | RE_NAME | 1. Not null. 2. Name must match ERCOT records (SIEBEL) | 1.This field is not null. 2. All should be capital letters 3.No Special characters except spaces and dashes. | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Resource Entity DUNS #: |  |  |  | General and Site Information |  |  | SITECODES & RE_RARF | RE_DUNS | 1. Not null. 2. DUNS number must match ERCOT records (SIEBEL) | Not null. Data type should be varchar (as sometimes the value contains # with a leading zero). Duns# is either 9 digit or 13 digit .Should match with RE Duns# IN Siebel | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Site Information |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | This tab is Conditional: Required if the Generation Type is ' WIND or CC or GEN' , where GEN is non-cc non-wind generation resources. This tab is not required for Load Resources. | C | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,MMS,Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Resource Site Name: |  |  |  | General and Site Information |  |  | SITECODES | SITE_NAME | 1. Not null. 2. Validate with ERCOT records (Lodestar). 3. All should be capital letters | 1.This field is not null. Validate with the existing record in ERCOT?? 2. All should be capital letters | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | EMS,Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Resource Site Code: | 05/02/2012 Updated Table that this field is mapped to, adding SITE_LOAD_SPLIT. |  |  | General and Site Information |  |  | SITECODES & SITE_LOAD_SPLIT | SITE_CODE | 1. Not null. 2. Validate with ERCOT records (Lodestar). 3. All should be capital letters | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Street Address: |  |  |  | General and Site Information |  |  | SITECODES | STREET_ADDRESS | Not null | Not null | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | City: |  |  |  | General and Site Information |  |  | SITECODES | CITY | Not null | Not null | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | State |  |  |  | General and Site Information |  |  | SITECODES | STATE | Not null | This is Required field (can not be null) Data type should be character, no numbers or commas are allowed. | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Zip Code |  |  |  | General and Site Information |  |  | SITECODES | ZIPCODE | Not null | This is a Required field and can not be null. Only numbers are allowed | R |  | Siebel
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | County: |  |  |  | General and Site Information |  |  | SITECODES | COUNTY | Not null | Not null | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Site In-Service Date: |  |  |  | General and Site Information |  |  | SITECODES | SITE_IN_SRVC_DT | 1. Must be earlier than Site-Stop Service Date. 2. mm/dd/yy format. 3. Not null. | Site-In Service Date is earlier than Site-Stop Service Date. Enter the date in mm/dd/yy format. This field is not null. | R | Lin Xu | Lodestar,MMS
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Site Stop Service Date: |  |  |  | General and Site Information |  |  | SITECODES | SITE_STOP_SRVC_DT | 1. Must be later than Site In-Service Date. 2. mm/dd/yy format. 3. Not null. | Site Stop Service Date should be later than Site-In Service Date. Format is mm/dd/yyy. This field is optional. NA is not valid , Leave it blank if not applicable. | O | Lin Xu | Lodestar,MMS
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Congestion Management Zone for 2003: |  |  |  | General and Site Information |  |  | SITECODES | CMZ_2003 | 1. Select from the list: North,South,Houston,West. 2. Not Null | Select from the list: North,South,Houston,West. This field is Required | O | RARF Glossary Version 4.0/ Angela Moy
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Resource owned by NOIE? |  |  |  | General and Site Information |  |  | SITECODES | RE_OWNED_NOIE_FLG | 1. Select from the list: Y or N 2. Not Null | Select from the list: Y or N | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Is Resource behind a NOIE Settlement Meter Point? |  |  |  | General and Site Information |  |  | SITECODES | RE_BHND_NOIE_SMP_FLG | 1. Select from the list: Y or N 2. Not Null | Select from the list: Y or N | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Number of EPS Primary meters: |  |  |  | General and Site Information |  |  | SITECODES | NUM_EPS_METERS | Not null | This field is required and it should be an integer | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Is Resource claiming status as a Non-Modeled Generator as defined in ERCOT Protocol Section 2, Resource | 05/23/2012 Updated validation Rule 04/12/2012 Updated RARF TAB | ADD 04/2012 |  | Site Info - DG General Information - DG | DG_SiteInfo.View | Y/N | SITECODES | RE_CLAIM_NONMOD_STATUS |  | 1. If Site_Code is in NON_MODELED then If RE_CLAIM_NONMOD_STATUS is null then Error Else if RE_CLAIM_NONMOD_STATUS not Y or N, Error If Site_Code is NOT in NON_MODELED then do not validate | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Is Resource >10 MW? | 05/23/2012 Updated validation Rule 04/12/2012 Updated RARF TAB | ADD 04/2012 |  | Site Info - DG General Information - DG | DG_SiteInfo.View | Y/N | SITECODES | RES_GREAT_TEN_MW |  | 1.If Site_Code is in NON_MODELED then If RE_CLAIM_NONMOD_STATUS is null then Error Else if RE_CLAIM_NONMOD_STATUS not Y or N, Error If Site_Code is NOT in NON_MODELED then do not validate . | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Primary Contact (name of person ERCOT can contact with questions regarding this form) |  |  |  | General and Site Information |  |  | Not in table | Not in table
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Printed Name: |  |  |  | General and Site Information |  |  | SITECODES | NAME_PC | Not null | Not null. Validate that the Authorized rep has valid digital certificate to access the User Interface | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Title: |  |  |  | General and Site Information |  |  | SITECODES | TITLE_PC | Not null | Not null | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Phone Number: |  |  |  | General and Site Information |  |  | SITECODES | PHONE_PC | Not null | Not null | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | E-mail Address: |  |  |  | General and Site Information |  |  | SITECODES | EMAIL_PC | Not null | Not null | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Fax Number: |  |  |  | General and Site Information |  |  | SITECODES | FAX_PC | Optional | Optional | O | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Secondary Contact (if available) |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | Optional
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Printed Name: |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | Optional
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Title: |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | Optional
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Phone Number: |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | Optional
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | E-mail Address: |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | Optional
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Fax Number: |  |  |  | General and Site Information |  |  | Not in table | Not in table |  | Optional
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | GEN Load Split -ESIID |  |  |  | GEN Load Split -ESIID |  |  | Not in table | Not in table
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | GENERATION SITE LOAD DETAILS |  |  |  | GEN Load Split -ESIID |  |  | Not in table | Not in table
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | ESIID_NUMBER |  | ADD 02/2012 to RARF FORM |  | GEN Load Split - ESIID |  |  | SITE_LOAD_SPLIT | ESIID_NUMBER | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2. Must have minimum of 2 ESI ID's entered 3. Data type is character | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Generate ESIID Number + 1 (ex. ESIID_1, ESIID_2, ESIID_3)
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | SITECODE_ESIID |  | ADD 02/2012 to RARF FORM |  | GEN Load Split - ESIID |  |  | SITE_LOAD_SPLIT | SITECODE_ESIID | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2.Concantanate SITE_CODE and ESIID_NUMBER | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Concantanate SITECODE_ESIID_Number
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Generation Load Split? | Corrected 02/29/2012 |  |  | GEN Load Split - ESIID |  | Y/N | SITECODES | GEN_LOAD_SPLIT_FLG | 1.This field is conditional. Required only if Generation Load Split is 'N'. 2. Not Required of Resource Behind NOIE Settlement point is 'Y' 2. Data type is character | Select from the list: Y or N | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | ERCOT Read Meter? |  |  |  | GEN Load Split - ESIID |  | Y/N | SITECODES | ERCOT_READ_FLG | 1. Select from the list: Y or N 2. Not Null | Select from the list: Y or N | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | SITECODE | 05/02/2012 Removed from form, column remains but data will now be populated from SITECODE tab | ADD 02/2012 |  | GEN Load Split - ESIID |  | Automatic | SITECODES & SITE_LOAD_SPLIT | SITE_CODE | 1. Not null. 2. Validate with ERCOT records (Lodestar). 3. All should be capital letters | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | ESI ID: | 05/02/2012 Updated Validation Rule | UPDATE 02/2012 |  | GEN Load Split - ESIID |  |  | SITE_LOAD_SPLIT | ESI_ID |  | 1.Data type is character 2.If Generation Load Split is 'N', ESIID is required. 3. If Generation Load Split is 'Y' then If RE_BHND_NOIE_SMP_FLG is 'Y' and Site_Code is in NON_MODELED, then no ESIID is required else ESIID is required | C | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | TDSP Providing Service To Resource: | Corrected |  |  | GEN Load Split - ESIID |  | List | SITE_LOAD_SPLIT | TDSP_PROVIDING_SVC | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Select From drop down list provided. | This field is conditional. Required only if If the Generation Load Split question is answered as 'N' . Validate with the existing record in ERCOT?? | C | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | TDSP DUNS Number: | 03/09/2012 Updated Validation |  |  | GEN Load Split - ESIID |  | Automatic | SITE_LOAD_SPLIT | TDSP_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Prepopulated with DUNS of TDSP provided in cell above | 1. Not null 2. Must match with the data existing in Siebel 3. Data type: varchar (as sometimes the value contains # with a leading zero) 4. Either a 9 or 13 digit DUNS number | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Fixed Load Splitting % | 05/03/2012 removed percent from label on form |  |  | GEN Load Split - ESIID |  |  | SITE_LOAD_SPLIT | FIXED_LD_SPLIT | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2. Must have minimum of 2 ESI ID's entered | 1.This field is optional/conditional. Required only if Gen Site is split among multiple ESI Id's.If entered, cross check the data with Lodestar. 2. Sum of the Fixed Load Splitting % (corresponding to each ESIID) should be 100. Generate an error if the rule fails | C/O | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Load Serving Entity |  |  |  | GEN Load Split - ESIID |  | List | SITE_LOAD_SPLIT | COMP_RETAILER | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Select From drop down list provided. | This field is optional/conditional. Required only if Gen Site is split among multiple ESI Id's. | C | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Load Serving Entity Duns# |  |  |  | GEN Load Split - ESIID |  | Automatic | SITE_LOAD_SPLIT | COMP_RETAILER_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Prepopulated with DUNS of Competitive Retailer provided in cell above | This field is optional/conditional. Required only if Gen Site is split among multiple ESI Id's. If entered it should be either 9 or 13 digit number AND should match with the existing record in Lodestar? | C | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 | Lodestar
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Private Network - Site |  |  |  | Private Network - Site |  |  | Not in table | Not in table
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | SITE DETAILS |  |  |  | Private Network - Site |  |  | Not in table | Not in table
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Private Network? | 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  | Y/N | SITECODES | PRIVATE_NTWK_SITE_FLG |  | Select from Y or N. Private Network Flag is not null | R
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | PRIVATE NETWORK - SITE INFORMATION |  |  |  | Private Network - Site |  |  | Not in table | Not in table |  | This tab is conditional : Required for all Private Use Networks
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Average Amount Of Self-serve Private Load | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  | MW | SITECODES | AVG_LD_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Average Amount Of Self-serve Private Reactive Load | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  | MVAR | SITECODES | AVG_LD_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Expected Typical Private Network Net Interchange | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  | MW | SITECODES | NET_INTERCHNG_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Expected Typical Private Network Net Reactive Interchange | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  | MVAR | SITECODES | NET_INTERCHNG_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Private Network Gross Unit Capability | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  | MW | SITECODES | GROSS_CAPBLTY_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Private Network Gross Unit Reactive Capability | 04/25/2012 Corrected table on mapping document to reflect correct table column is mapped to and removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  | MVAR | SITECODES | GROSS_CAPBLTY_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Load Characteristics For MW Load |  |  |  | Private Network - Site |  |  | Not in table | Not in table |  | This tab is conditional : Required for all Private Use Networks
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Large Motor, Percent Of Total | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  |  | SITECODES | PUN_MW_LARGEMTR_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Small Motor, Percent Of Total | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  |  | SITECODES | PUN_MW_SMALLMTR_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Resistive (heating) Load, Percent Of Total MW Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  |  | SITECODES | PUN_MW_RESISTIVE_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Discharge Lighting, Percent Of Total | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  |  | SITECODES | PUN_MW_DISCHARGE_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Other, Percent Of Total MW Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  |  | SITECODES | PUN_MW_OTHER_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Load Characteristics for MVAR Load |  |  |  | Private Network - Site |  |  | Not in table | Not in table |  | This tab is conditional : Required for all Private Use Networks
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Large Motor, Percent Of Total MVAR Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  |  | SITECODES | PUN_MVAR_LARGEMTR_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Small Motor, Percent Of Total MVAR Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  |  | SITECODES | PUN_MVAR_SMALLMTR_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | R
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Discharge Lighting, Percent Of Total MVAR Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  |  | SITECODES | PUN_MVAR_DISCHARGE_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C
General_Site_ESIID Information (GEN, WIND, CC, DG, SOLAR | Other, Percent Of Total MVAR Load | 05/17/2012 removed percent from form 04/25/2012 - Removed from gen, wind, cc, solar forms. Added to General_Site_ESIID Information form. |  |  | Private Network - Site |  |  | SITECODES | PUN_MVAR_OTHER_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' | C
Solar | UNIT INFO - Solar |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View |  | Not in table | Not in table
Solar | GENERATOR DETAILS |  |  |  | UNIT INFO - Solar |  |  | Not in table | Not in table
Solar | Unit Name |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | all caps | SOLAR | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R
Solar | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | Automatic | SOLAR | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C
Solar | Non Modeled Generation |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | Y/N | SOLAR | NON_MOD_GEN |  | 1.Select from the list: Y or N 2.Not Null
Solar | PUC Registration Number (Docket Number) |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View |  | SOLAR | PUC_NUM |  | This field is optional and it should be a number. NA is not valid , Leave it blank if not applicable.
Solar | ERCOT Interconnection Project Number - Only new Units |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View |  | SOLAR | ERCOT_INTRCONN_PROJ_NUM |  | 1.This field is optional. Required only for new units. Enter a Valid Number or leave it blank if not applicable 2. Cross check with the data entered in the field 'This submittal is for' in General Information Tab. If the value is 'New Site' then only this field is required.
Solar | NERC Number (NERC ID#) |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View |  | SOLAR | NERC_NUM |  | This field is optional. NA is not valid , Leave it blank if not applicable.
Solar | Qualifying facility |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | Y/N | SOLAR | QUAL_FACILITY_FLG |  | QF flag is not null. Select from the list: Y or N
Solar | SITE AND UNIT DATES |  |  |  | UNIT INFO - Solar |  |  | Not in table | Not in table
Solar | Transmission Only Date (POI) |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | mm/dd/yyyy | SOLAR | TRANS_ONLY_DT |  | 1.This field is optional. Format should be: MM/DD/YYYY 2. Data type must be Date.
Solar | Standard Generation Interconnection Agreement (SGIA) Signature Date |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | mm/dd/yyyy | SOLAR | SGIA_SIG_DT |  | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date.
Solar | Unit Start Date (Model Ready Date) | 03/13/2012 Updated Validation | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | mm/dd/yyyy | SOLAR | UNIT_MRD_ST_DT |  | This field is optional. Format should be: MM/DD/YYYY
Solar | Unit Commercial Date |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | mm/dd/yyyy | SOLAR | UNIT_START_DT |  | This field is not null. Format should be: MM/DD/YYYY Unit Start Date should be >= Site Start Date ( Site-Information Tab)
Solar | Unit End Date |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | mm/dd/yyyy | SOLAR | UNIT_END_DT |  | This field is optional. Format should be: MM/DD/YYYY
Solar | POINT OF INTERCONNECTION |  |  |  | UNIT INFO - Solar |  |  | Not in table | Not in table
Solar | SubStation Code/SubStation Mnemonic |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | all caps | SOLAR | SUBSTAT_CODE_SUB_MNEMONIC |  | 1) This field is not null (required). Data type must be Character. 2) Must match ERCOT records (unless new). Substation Code invalid message should be warning only if the PUN flag is 'yes'. 3) This field may not have any special characters, except an underscore "_" and a dash "-" . 4) Must be <= 8 characters. Warning! Substation Code should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) Substation code should be in Upper case letters. Generate an error if the rule fails.
Solar | Voltage Level |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | kV | SOLAR | VOL_LEV |  | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0.
Solar | PTI Bus Number |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | # | SOLAR | PTI_BUS_NUM |  | 1) This field isnot null (required). Data type must be Integer. 2) The value must be > 0.
Solar | FUEL INFORMATION |  |  |  | UNIT INFO - Solar |  |  | Not in table | Not in table
Solar | Primary Fuel Type |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | List | SOLAR | PRIM_FUELTYPE |  | 1)Resource Category is not null. 2)Select from the list: SUN,NA,NG and OT
Solar | Secondary Fuel Type |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | List | SOLAR | SEC_FUELTYPE |  | 1)Resource Category is not null. 2)Select from the list: SUN,NA,NG and OT
Solar | Fuel Transportation Type |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | List | SOLAR | FUEL_TRANSTYPE |  | NA
Solar | Resource Category |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | List | SOLAR | RES_CATG |  | 1)Resource Category is not null. 2)Select from the list: Solar
Solar | RATINGS AND DESIGNS |  |  |  | UNIT INFO - Solar |  |  | Not in table | Not in table
Solar | Renewable |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | Y/N | SOLAR | RENEWABLE_FLG |  | Renewable Flag is not null. Select from the list: Y or N
Solar | Renewable/Offset |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | List | SOLAR | RENEWABLE_OFFSET |  | Select from the list : RN, OS, NA. This field is not null.
Solar | Physical Unit Type |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | List | SOLAR | PHYS_UNIT_TYPE |  | Select from the list:CA, CC, CE, CS, CT, FC, GT, HY, IC, NA, OT, PS, PV, ST, WT. This field is not null.
Solar | Name Plate Rating |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | MVA | SOLAR | NAME_PLT_RTG |  | Name Plate Rating should be >= Real Power Rating
Solar | Real Power Rating |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | MW | SOLAR | RTG_MW |  | Real Power Rating should be > Reactive Power Rating
Solar | Reactive Power Rating |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | MVAR | SOLAR | RTG_MVAR |  | Name Plate Rating should be >= Reactive Power Rating
Solar | Unit Generating Voltage |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | kV | SOLAR | UNIT_KV |  | 1. This field is not null and it should be a number 2. Unit Generating voltage can not be below 4.16 KV
Solar | Governor Droop Setting | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View |  | SOLAR | GOV_DROOP |  | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if it is not between 0 and 25. Generate Warning if > 5 (protocol requirement).
Solar | Governor Dead-Band |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | Hz | SOLAR | GOV_DEAD_BND |  | 1) This field is required 2) Data type must be Numeric, Positive value. 3) Generate an Error if > 0.1. Generate Warning if > 0.03.
Solar | Design Max Ambient Temperature |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | degree F | SOLAR | DESIGN_MAX_AMB_TEMP |  | >100 <150
Solar | Design Min Ambient Temperature |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | degree F | SOLAR | DESIGN_MIN_AMB_TEMP |  | >-100 <32
Solar | GEOGRAPHIC LOCATION (CENTER OF PLANT) |  |  |  | UNIT INFO - Solar |  |  | Not in table | Not in table
Solar | Latitude Of Center Of Plant |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | decimal degrees (N) | SOLAR | LAT_CENTER_PLT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if Latitude < 25.0 or > 37.0.
Solar | Longitude Of Center Of Plant |  | ADD 04/2012 |  | UNIT INFO - Solar | Solar_UnitInfo.View | decimal degrees (W) | SOLAR | LONG_CENTER_PLT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if <93 or > 107 .
Solar | Unit Info - Solar Inverter |  |  |  | Unit Info - Solar Inverter |  |  | Not in table | Not in table
Solar | GENERATOR Details |  |  |  | Unit Info - Solar Inverter |  |  | Not in table | Not in table
Solar | Unit Name |  | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | List | SOLAR_INVERTER | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R
Solar | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | Automatic | SOLAR_INVERTER | UNIT_CODE |  | .This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C
Solar | Total Number of Inverters |  | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | # | SOLAR_INVERTER | TOTNUM_INVERTERS |  | 1.This is not null and it should be an Integer 2. Not null.
Solar | MODULE 1 - INVERTER DETAILS | Changed Data Field Name on RARF Form 03/26/2012 |  |  | Unit Info - Solar Inverter |  |  | Not in table | Not in table
Solar | Module 1 - Type of INVERTER (Manufacturer/Model) | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | all caps | SOLAR_INVERTER | GRP1_INV_TYPE |  | This field is not null and the Data type should be character.
Solar | Module 1 - MW Rating for this model of INVERTER | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | MW | SOLAR_INVERTER | GRP1_INV_MW_MDL_RTG |  | This field is not null and it should be an integer
Solar | Module 1 - Number of this type of INVERTER | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | # | SOLAR_INVERTER | GRP1_INV_NUM |  | 1. This field is optional. If entered it should be a character. If the data is entered for Group2, then reactive capability- Solar Tab should have values for this group. 2. Inverter groups of Inverters within a unit must be of the same type and size. RARF Audit report should generate a warning if this rule fails
Solar | MODULE 2 - INVERTER DETAILS | Changed Data Field Name on RARF Form 03/26/2012 |  |  | Unit Info - Solar Inverter |  |  | Not in table | Not in table
Solar | Module 2 - Type of INVERTER (Manufacturer/Model) | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | all caps | SOLAR_INVERTER | GRP2_INV_TYPE |  | This field is optional/conditional. Required if Type of Inverter info is entered for Group2 otherwise it is optional. Data type should be Integer. If the data is entered for Group2, then reactive capability-Solar Tab should have values for this group.
Solar | Module 2 - MW Rating for this model of INVERTER | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | MW | SOLAR_INVERTER | GRP2_INV_MW_MDL_RTG |  | 1. This field is optional. If entered it should be a character. If the data is entered for Group3, then reactive capability-Solar Tab should have values for this group. 2. Wind groups of Inverters within a unit must be of the same type and size. RARF Audit report should generate a warning if this rule fails
Solar | Module 2 - Number of this type of INVERTER | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | # | SOLAR_INVERTER | GRP2_INV_NUM |  | 1. Conditional required if Type of Inverter info is entered for Group2 2. Data type should be numeric.
Solar | MODULE 3 - INVERTER DETAILS | Changed Data Field Name on RARF Form 03/26/2012 |  |  | Unit Info - Solar Inverter |  |  | Not in table | Not in table
Solar | Module 3 - Type of INVERTER (Manufacturer/Model) | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | all caps | SOLAR_INVERTER | GRP3_INV_TYPE |  | 1. Conditional required if Type of Inverter info is entered for Group3 2. Data type should be numeric.
Solar | Group 3 - MW Rating for this model of INVERTER | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | MW | SOLAR_INVERTER | GRP3_INV_MW_MDL_RTG |  | This field is optional/conditional. Required if Type of Inverter info is entered for Group5 otherwise it is optional. Data type should be Integer. If the data is entered for Group5, then reactive capability-Solar Tab should have values for this group.
Solar | Group 3 - Number of this type of INVERTER | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | # | SOLAR_INVERTER | GRP3_INV_NUM |  | This field is optional/conditional. Required if Type of Inverter info is entered for Group4 otherwise it is optional. Data type should be Integer. If the data is entered for Group4, then reactive capability-Solar Tab should have values for this group.
Solar | MODULE 4 - INVERTER DETAILS | Changed Data Field Name on RARF Form 03/26/2012 |  |  | Unit Info - Solar Inverter |  |  | Not in table | Not in table
Solar | Module 4 - Type of INVERTER (Manufacturer/Model) | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | all caps | SOLAR_INVERTER | GRP4_INV_TYPE |  | 1. Optional. 2. Group4 reactive capability-Solar Tab should have values for this group.
Solar | Module 4 - MW Rating for this model of INVERTER | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | MW | SOLAR_INVERTER | GRP4_INV_MW_MDL_RTG |  | This field is optional/conditional. Required if Type of Inverter info is entered for Group5 otherwise it is optional. Data type should be Integer. If the data is entered for Group5, then reactive capability-Solar Tab should have values for this group.
Solar | Module 4 - Number of this type of INVERTER | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | # | SOLAR_INVERTER | GRP4_INV_NUM |  | 1. Conditional required if Type of Inverter info is entered for Group3 2. Data type should be numeric.
Solar | MODULE 5 - INVERTER DETAILS | Changed Data Field Name on RARF Form 03/26/2012 |  |  | Unit Info - Solar Inverter |  |  | Not in table | Not in table
Solar | Module 5 - Type of INVERTER (Manufacturer/Model) | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | all caps | SOLAR_INVERTER | GRP5_INV_TYPE
Solar | Module 5 - MW Rating for this model of INVERTER | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | MW | SOLAR_INVERTER | GRP5_INV_MW_MDL_RTG
Solar | Module 5 - Number of this type of INVERTER | Changed Data Field Name on RARF Form 03/26/2012 | ADD 04/2012 |  | Unit Info - Solar Inverter | Solar_Inverter_UnitInfo.View | # | SOLAR_INVERTER | GRP5_INV_NUM
Solar | Parameters - Solar |  |  |  | Parameters - Solar |  |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Type Selected is 'GEN' where GEN is non-CC non-wind Generation Resources. | C | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,MMS,NMMS
Solar | Generator Details |  |  |  | Parameters - Solar |  |  | Not in table | Not in table
Solar | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | List | SOLAR | UNIT_NAME | 1. Not Null. 2. Must not exceed 4 characters for Jointly Owned Units 3. Maximum of 8 character allowed | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Solar | Resource Name (Unit Code/Mnemonic) | 04/23/2012 Updated Table to DERATING_SOLAR | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | Automatic | SOLAR & DERATING_SOLAR | UNIT_CODE | 1. Not Null. 2. Enter Site Code and Unit Name for this field (Sitecode_Unit Name) 3. All letters must be capital | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Solar | Reasonability Limits |  |  |  | Parameters - Solar |  |  | Not in table | Not in table
Solar | High Reasonability Limit |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | HR_LMT | 1. High Reasonability Limit >0 2. HighReasonabilityLimit >= LowReasonablityLimit 3. Not Null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit | R | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Solar | Low Reasonability Limit |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | LR_LMT | 1. Low Reasonability Limit >0 for Non PUN sites 2. Low ReasonabilityLimit <= High ReasonablityLimit 3. PUN (Private Use Network) Sites LRL should equal zero or produce a Warning 4. Not Null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS
Solar | High Reasonability Ramp Rate Limit |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW/min | SOLAR | HR_RAMPRATE_LMT | 1. High Reasonability Ramp Rate Limit >= Low Reasonability Ramp Rate Limit. 2. Not null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS
Solar | Low Reasonability Ramp Rate Limit |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW/min | SOLAR | LR_RAMP_RATE_LMT | 1. Low Reasonability Ramp Rate Limit >=0. 2. Not null | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS
Solar | Seasonal Ratings Spring |  |  |  | Parameters - Solar |  |  | Not in table | Not in table
Solar | Seasonal Net Max Sustainable Rating - Spring |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MAX_SUST_RTG_SP | 1.Seasonal Net Max Sustainable Rating - Spring >= Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Spring > Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Lin Xu/Weihui | MMS,NMMS
Solar | Seasonal Net Min Sustainable Rating - Spring |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MIN_SUST_RTG_SP | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS,NMMS
Solar | Seasonal Net Max Emergency Rating - Spring |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MAX_EMGY_RTG_SP | 1.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Lin Xu/Weihui | MMS,NMMS
Solar | Seasonal Net Min Emergency Rating - Spring |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MIN_EMGY_RTG_SP | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit 2. Not Null | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS,NMMS
Solar | Seasonal Ratings Summer |  |  |  | Parameters - Solar |  |  | Not in table | Not in table
Solar | Seasonal Net Max Sustainable Rating - Summer |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MAX_SUST_RTG_SM | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Summer > Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | Seasonal Net Min Sustainable Rating - Summer |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MIN_SUST_RTG_SM | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit | R | Lin Xu | MMS
Solar | Seasonal Net Max Emergency Rating - Summer |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MAX_EMGY_RTG_SM | 1.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Summer > Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | Seasonal Net Min Emergency Rating - Summer |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MIN_EMGY_RTG_SM | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | Seasonal Ratings Fall |  |  |  | Parameters - Solar |  |  | Not in table | Not in table
Solar | Seasonal Net Max Sustainable Rating - Fall |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MAX_SUST_RTG_FL | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | Seasonal Net Min Sustainable Rating - Fall |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MIN_SUST_RTG_FL | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall. >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | Seasonal Net Max Emergency Rating - Fall |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MAX_EMGY_RTG_FL | 1.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Fall > Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | Seasonal Net Min Emergency Rating - Fall |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MIN_EMGY_RTG_FL | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | Seasonal Ratings Winter |  |  |  | Parameters - Solar |  |  | Not in table | Not in table
Solar | Seasonal Net Max Sustainable Rating - Winter |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MAX_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | Seasonal Net Min Sustainable Rating - Winter |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MIN_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 3. Not Null | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | Seasonal Net Max Emergency Rating - Winter |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MAX_EMGY_RTG_WT | 1.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit 4. Not Null | 1.Seasonal Net Max Emergency Rating - Winter > Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | Seasonal Net Min Emergency Rating - Winter |  | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | SOLAR | SEASON_NET_MIN_EMGY_RTG_WT | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 2. Not Null | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Lin Xu/Weihui | MMS
Solar | UNIT DE-RATING VALUES FOR DIFFERENT TEMPERATURES |  |  |  | Parameters - Solar |  |  | Not in table | Not in table
Solar | 0°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 5°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 10°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 15°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | Temperature (0°f thru 120°f) will go in to field DE_RATING_TEM and the MW Value will go in to UNIT_DERATING_TEMP_VAL
Solar | 20°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 25°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 30°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 35°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 40°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 45°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 50°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 55°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 60°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 65°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 70°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 75°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 80°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 85°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 90°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 95°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 100°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 105°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 110°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 115°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | 120°f | 04/23/2012 Updated Table to DERATING_SOLAR 03/09/2012 Updated Validation | ADD 04/2012 |  | Parameters - Solar | Parameters_Solar.View | MW | DERATING_SOLAR | DE_RATING_TEM & UNIT_DERATING_TEMP_VAL |  | UNIT_DERATING_TEMP_VAL is Required and Numeric
Solar | Operational Parameters - Solar |  |  |  | Operational Parameters - Solar |  |  | Not in table | Not in table |  | This tab is conditional. Required if the Generation Resource Type Selected is 'WIND units' | C | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | MMS,NMMS
Solar | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View |  | SOLAR | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Solar | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View |  | SOLAR | UNIT_CODE |  | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | Lodestar
Solar | RESOURCE PARAMETERS |  |  |  | Operational Parameters - Solar |  |  | Not in table | Not in table
Solar | Minimum On Line Time | Check | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View | hours | SOLAR | MIN_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum On Line Time >= 0 | R | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Solar | Minimum Off Line Time | Check | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View | hours | SOLAR | MIN_OFFLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Minimum Off Line Time >= 0 | R | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Solar | Hot Start Time | Corrected | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View | hours | SOLAR | HOTSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot Start Time >= 0 3. Hot Start Time <= Intermediate Start Time | O | Angela Moy/Jamil Daouk | NMMS
Solar | Intermediate Start Time | Corrected | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View | hours | SOLAR | INTERMSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate Start Time >= 0 3. Cold Start Time >= Intermediate Start Time >= Hot Start Time | O | Angela Moy/Jamil Daouk | NMMS
Solar | Cold Start Time | Corrected | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View | hours | SOLAR | COLDSTART |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Cold Start Time >= 0 3. Cold Start Time >= Intermediate Start Time | O | Angela Moy/Jamil Daouk | NMMS
Solar | Max Weekly Starts | Check | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View |  | SOLAR | MAXWKLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Lin Xu/Jamil Daouk | MMS,NMMS
Solar | Max On Line Time | Corrected | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View | hours | SOLAR | MAX_ONLINE_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Start >= 0 3. Max Weekly Start <= 999 | R | Lin Xu/Jamil Daouk | MMS,NMMS
Solar | Max Daily Starts | Check | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View |  | SOLAR | MAXDLYSTARTS |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Daily Start >= 0 3. Max Daily Start <= 999 | R | Lin Xu/Kittipong/Jamil Daouk | MMS,NMMS
Solar | Max Weekly Energy | Corrected | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View | MWh | SOLAR | MAXWKLYENRGY |  | 1. Warning! If decimal value is submitted, then MMS will round to integer 2. Max Weekly Energy >= 0 3. Max Weekly Energy < 1e10 | R | Lin Xu | MMS,NMMS
Solar | Hot-to-Intermediate Time | Check | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View | hours | SOLAR | HOT_TO_INTMDT_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Hot-to-Intermediate Time >= 0 | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
Solar | Intermediate-to-Cold Time | Check | ADD 04/2012 |  | Operational Parameters - Solar | Parameters_Solar.View | hours | SOLAR | INTMDT_TO_COLD_TIME |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Intermediate-to-Cold Time >= 0 | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Jamil Daouk | NMMS
Solar | Operational Parameters - Solar - NRRC |  |  | Operational Parameters - Solar - NRRC | Operational Parameters - Solar - NRRC |  |  | Not in table | Not in table
Solar | Generator Details |  |  | Operational Parameters - Solar - NRRC | Operational Parameters - Solar - NRRC |  |  | Not in table | Not in table
Solar | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 | Operational Parameters - Solar - NRRC | Operational Parameters - Solar - NRRC | NRRC_SOLAR.View | List | SOLAR | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Solar | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 | Operational Parameters - Solar - NRRC | Operational Parameters - Solar - NRRC | NRRC_SOLAR.View | List | RAMP_RATES_NRRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Solar | Normal Ramp Rate Curve |  |  |  | Operational Parameters - Solar - NRRC |  |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit.
Solar | MW Number |  |  |  | Operational Parameters - Solar - NRRC
Solar | NRRC Code |  | ADD 04/2012 | Operational Parameters - Solar - NRRC | Operational Parameters - Solar - NRRC | NRRC_SOLAR.View |  | RAMP_RATES_NRRC | UNIT_MW_NRRC |  | This Field is Not in the RARF: Capture Unit Code and MW Number and prepopulate this field with UNIT_CODE_MW_NUMBER_NRRC. | R
Solar | NRRC MW | PHASE II Updated 03/06/2012 Added Step 5 and 6 | ADD 04/2012 |  | Operational Parameters - Solar - NRRC | NRRC_SOLAR.View | MW | RAMP_RATES_NRRC | MW_NUMBER_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk | NMMS
Solar | Upward Ramprate | Check | ADD 04/2012 |  | Operational Parameters - Solar - NRRC | NRRC_SOLAR.View | MW/min | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Lin Xu/Kittipong | MMS,NMMS
Solar | Downward Ramprate | Check | ADD 04/2012 |  | Operational Parameters - Solar - NRRC | NRRC_SOLAR.View | MW/min | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Lin Xu/Kittipong | MMS,NMMS
Solar | Operational Parameters - Solar - ERRC |  |  |  | Operational Parameters - Solar- ERRC |  |  | Not in table | Not in table
Solar | Generator Details |  |  |  | Operational Parameters - Solar- ERRC |  |  | Not in table | Not in table
Solar | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 | Operational Parameters - Solar- ERRC | Operational Parameters - Solar- ERRC | ERRC_SOLAR.View | List | SOLAR | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Solar | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 | Operational Parameters - Solar- ERRC | Operational Parameters - Solar- ERRC | ERRC_SOLAR.View | List | RAMP_RATES_ERRC | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS
Solar | Emergency Ramp Rate Curve |  |  |  | Operational Parameters - Solar- ERRC |  |  | Not in table | Not in table |  | The ramp rates should not be negative or zero. If there is only one ramp rate then only one MW value needs to be filled in. If not all 10 MW values are used then use only MW1 through MWX. Ramp rates are required for every unit.
Solar | ERRC MW | PHASE II Updated 03/06/2012 Added Step 5 and 6 |  |  | Operational Parameters - Solar- ERRC |  | MW | RAMP_RATES_ERRC | MW_NUMBER_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. MW break point on RampRate Curve >= Low Reasonability Limit 3. MW break point on RampRate Curve <= High Reasonability Limit 4. MW break point must be provided in decending order, i.e. MW1 < MW2 < MW3 .. < .. MWn 5. MW1,MW2,MW3,MW4,MW5 all are unique. If there is only one ramp rate then only one MW value need to be filled in. This field should not be null 6. MW1 CAN NOT BE NULL AND MUST HAVE VALUE FOR RAMP UP OR RAMP DOWN | R | Nitika Mago/RARF Guide Version 4.0/Jamil Daouk | NMMS
Solar | MW Number |  | ADD 04/2012 | Operational Parameters - Solar- ERRC | Operational Parameters - Solar- ERRC | ERRC_SOLAR.View
Solar | ERRC Code |  | ADD 04/2012 | Operational Parameters - Solar- ERRC | Operational Parameters - Solar- ERRC | ERRC_SOLAR.View |  | RAMP_RATES_ERRC | UNIT_MW_ERRC |  | Capture Unit Code and MW Number and prepopulate this field with Unit Name_MW_NUMBER_ERRC. | R
Solar | Upward Ramprate | Check | ADD 04/2012 |  | Operational Parameters - Solar- ERRC | ERRC_SOLAR.View | MW/min | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Upward ramp value >= Low Reasonability Ramp Rate Limit 3. Upward ramp value <= High Reasonability Ramp Rate Limit | R | Lin Xu/Kittipong | MMS,NMMS
Solar | Downward Ramprate | Check | ADD 04/2012 |  | Operational Parameters - Solar- ERRC | ERRC_SOLAR.View | MW/min | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC |  | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Downward ramp value >= Low Reasonability Ramp Rate Limit 3. Downward ramp value <= High Reasonability Ramp Rate Limit | R | Lin Xu/Kittipong | MMS,NMMS
Solar | Reactive Capability - Solar |  |  |  | Reactive Capability - Solar |  |  | Not in table | Not in table
Solar | GENERATOR DETAILS |  |  |  | Reactive Capability - Solar |  |  | Not in table | Not in table
Solar | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | List | REACT_CAP_SOLAR | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R
Solar | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | Automatic | REACT_CAP_SOLAR | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C
Solar | Module # | Added 03/26/2012 |  |  | Reactive Capability - Solar |  | List | REACT_CAP_SOLAR | MOD_NO |  | 1. This field is not null. Data type: Character. 2. .Select from the list: Module1, Module2, Module3, Module4, Module5 | R
Solar | Module_Code | Added 03/26/2012 Hidded column on form |  |  | Reactive Capability - Solar |  | Automatic | REACT_CAP_SOLAR | GROUP_CODE |  | 1. This field is not null. Data type: Character. 2. .Concatanate: UNIT_CODE_MODULE_CODE | R
Solar | REACTIVE CAPABILITY CURVES DETAILS |  |  |  | Reactive Capability - Solar |  |  | Not in table | Not in table
Solar | Reactive Capability Data Provided Below is Gross/Net Values? | 04/02/2012 - Updated RARF Field Name, DB Field and removed Net from Drop down List in data Validation | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | List | REACT_CAP_SOLAR | REACT_CAPB_DATA_GROSS_NET_VAL |  | Select from the list: GROSS
Solar | Reactive Capability Data Provided Below is from NDCRC Test Data? |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | Y/N | REACT_CAP_SOLAR | REACT_CAPB_NDCRC_TEST_DATA |  | Select from the list: Y or N
Solar | If Reactive Capability Data Provided Below Is From Ndcrc Test Data Then Enter The Date On Which The Test Was Performed. |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | mm/dd/yyyy | REACT_CAP_SOLAR | REACT_CAPB_NDCRC_TEST_DATA_DT |  | This field is optional. Format should be: MM/DD/YYYY
Solar | MW1 |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MW | REACT_CAP_SOLAR | MW1 |  | 1. MW1 >=0 .1 2. MW1<MW2. 3. X(1) <= WMN(Unit Minimal output) where X(1) represents MW1( Generate a Warning Only when Business Rule#2 fails) | R
Solar | Lagging MVAR limit associated with MW1 output |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MVAR | REACT_CAP_SOLAR | MVAR1LAG |  | 1. Lagging MVAR limit associated with MW1 output >=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R
Solar | Leading MVAR limit associated with MW1 output |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MVAR | REACT_CAP_SOLAR | MVAR1LEAD |  | 1. Leading MVAR limit associated with MW1 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R
Solar | MW2 |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MW | REACT_CAP_SOLAR | MW2 |  | 1. MW2>0 2. MW2<MW3 | R
Solar | Lagging MVAR limit associated with MW2 output |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MVAR | REACT_CAP_SOLAR | MVAR2LAG |  | 1.Lagging MVAR limit associated with MW2 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R
Solar | Leading MVAR limit associated with MW2 output |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MVAR | REACT_CAP_SOLAR | MVAR2LEAD |  | 1. Leading MVAR limit associated with MW2 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R
Solar | MW3 |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MW | REACT_CAP_SOLAR | MW3 |  | 1. MW3 >0 2. MW3<MW4 | R
Solar | Lagging MVAR limit associated with MW3 output |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MVAR | REACT_CAP_SOLAR | MVAR3LAG |  | 1. Lagging MVAR limit associated with MW3 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R
Solar | Leading MVAR limit associated with MW3 output |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MVAR | REACT_CAP_SOLAR | MVAR3LEAD |  | 1.Leading MVAR limit associated with MW3 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R
Solar | MW4 |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MW | REACT_CAP_SOLAR | MW4 |  | 1. MW4 >0 2. MW4<MW5 3. X(n) > = WMX (Unit Max output) where n is the last MW value in the curve. If the curve has 4 points, X(n) is X(4) [ Generate a Warning Only When Business Rule#2 Fails] | R
Solar | Lagging MVAR limit associated with MW4 output |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MVAR | REACT_CAP_SOLAR | MVAR4LAG |  | 1. Lagging MVAR limit associated with MW4 output >=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must always be greater than the Leading MVAR | R
Solar | Leading MVAR limit associated with MW4 output |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MVAR | REACT_CAP_SOLAR | MVAR4LEAD |  | 1.Leading MVAR limit associated with MW4 output <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | R
Solar | MW5 - Unity Power Factor |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MW | REACT_CAP_SOLAR | MW5UNITYPF
Solar | If hydrogen cooled, indicate hydrogen pressure (psi) associated with your Reactive Curve submitted for ERCOT studies |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | PSI | GENERATION | HYDROCOOLED |  |  | O
Solar | Net Maximum Leading Operating Capability |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MVAR | REACT_CAP_SOLAR | NETMAXLEAD |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if < .3286(max capability in MW). | R
Solar | Net Maximum Lagging Operating Capability |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | MVAR | REACT_CAP_SOLAR | NETMAXLAG |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if < .3286(max capability in MW). | R
Solar | Has the Manufacturer's Capability Curve submitted? |  | ADD 04/2012 |  | Reactive Capability - Solar | Solar_ReactiveCapability.View | Y/N | REACT_CAP_SOLAR | MFR_CAP_CURVE
Solar | Ownership - Solar |  |  |  | Ownership - Solar |  |  | Not in table | Not in table
Solar | Generator Detail |  |  |  | Ownership - Solar |  |  | Not in table | Not in table
Solar | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | Ownership - Solar | Solar_Ownership.View |  | OWNERSHIP | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R
Solar | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | Ownership - Solar | Solar_Ownership.View |  | OWNERSHIP | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C
Solar | Ownership Percentages |  |  |  | Ownership - Solar |  |  | Not in table | Not in table |  | 2.All letters should be capital
Solar | Joint Ownership Code |  | ADD 04/2012 |  | Ownership - Solar | Solar_Ownership.View | Y/N | OWNERSHIP | J0CODE |  | 3. Should not allow spaces
Solar | Resource Entity Name | Update 03/13/2012 | ADD 04/2012 |  | Ownership - Solar | Solar_Ownership.View |  | OWNERSHIP | MKT_PRTCPT |  | 1. Not null 2. Do not allow any special characters except spaces and dashes.
Solar | Resource Duns Number |  | ADD 04/2012 |  | Ownership - Solar | Solar_Ownership.View |  | OWNERSHIP | MKT_PRTCPT_DUNS
Solar | Fixed Ownership | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Ownership - Solar | Solar_Ownership.View |  | OWNERSHIP | FIX_OWNRSHP_PCT
Solar | Master Owner (Y or N) |  | ADD 04/2012 |  | Ownership - Solar | Solar_Ownership.View | Y/N | OWNERSHIP | MASTR_OWNR_FLG
Solar | Ownership Start Date | 04/09/2012 Changed Validation to be an Optional 03/07/2012 Updated with Business Rule | ADD 04/2012 |  | Ownership - Solar | Solar_Ownership.View | mm/dd/yyyy | OWNERSHIP | OWNR_START_DT |  | This field is optional. Format should be: MM/DD/YYYY | R O
Solar | Ownership Start Date | 03/07/2012 Updated with Business Rule | ADD 04/2012 |  | Ownership - Solar | Solar_Ownership.View | mm/dd/yyyy | OWNERSHIP | OWNR_END_DT |  | This field is optional. Format should be: MM/DD/YYYY | O
Solar | Planning - Solar |  |  |  | Planning - Solar |  |  | Not in table | Not in table
Solar | GENERATION DETAILS |  |  |  | Planning - Solar |  |  | Not in table | Not in table
Solar | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | UNIT_NAME |  | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R
Solar | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | R
Solar | INVERTER TYPE | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | INVERTER_TYPE |  | Dropdown list | R
Solar | PLANNING DETAILS |  |  |  | Planning - Solar |  |  | Not in table | Not in table
Solar | What is the MVA base that the following data is based on? |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | MVA | SOLAR | MVABASE |  | 1) This field is required 2) Value must be Float 3) Generate a Warning if MVABASE > 2500 4)[ If MVABASE value is within +/- 25% range of Unit Name Plate Rating] OR [MVABASE value = 100, then it is OK.If MVABASE value is outside the +/- 25% range of Unit Name Plate Rating, then Generate a Warning that the MVABSE is outside the typical +/- 25% variation of unit name plate rating
Solar | What is the kV base that the following data is based on? |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | kV | SOLAR | KVBASE |  | 1) This field is required 2) Value must be >0 and <1000 3) Generate a Warning if KVBASE > 40 4) If KVBASE value is within +/- 25% range of Unit KV value in the unit-information tab then it is OK.If If KVBASE value is outside the typical +/- 25% variation of Unit KV value in the unit-information tab then Generate a Warning that the KVBASE is outside the typical +/- 25% variation of Unit KV value
Solar | Direct Axis Subtransient reactance, X"di (unsaturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | pu | SOLAR | DIRECT_AXIS_SUBSTNT_REACTANCE_UNSATURATED |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Solar | Direct Axis Transient reactance, X'di (unsaturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | pu | SOLAR | DIRECT_AXIS_TRANSNT_REACTANCE_UNSATURATED |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Solar | Positive Sequence Z (unsaturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | R in p.u. | SOLAR | POSITIVE_SEQ_Z_R_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1
Solar | Positive Sequence Z (unsaturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | X in p.u. | SOLAR | POSITIVE_SEQ_Z_X_UNSATURARTED_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Solar | Negative Sequence Z (unsaturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | R in p.u. | SOLAR | NEGATIVE_SEQ_Z_R_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning when value is > 1.0 P.U
Solar | Negative Sequence Z (unsaturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | X in p.u. | SOLAR | NEGATIVE_SEQ_Z_X_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Solar | Does Zero Sequence Z exist? |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | Y/N | SOLAR | DOES_ZERO_SEQ_EXIST |  |  | R | Planning Team
Solar | Zero Sequence Z (unsaturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | R in p.u. | SOLAR | ZERO_SEQ_Z_R_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U
Solar | Zero Sequence Z (unsaturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | X in p.u. | SOLAR | ZERO_SEQ_Z_X_UNSATURARTED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Solar | Direct Axis Subtransient reactance, X"dv (saturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | p.u. | SOLAR | DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Solar | Direct Axis Transient reactance, X'dv (saturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | p.u. | SOLAR | DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED |  | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Solar | Positive Sequence Z (saturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | R in p.u. | SOLAR | POSITIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1
Solar | Positive Sequence Z (saturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | X in p.u. | SOLAR | POSITIVE_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)
Solar | Negative Sequence Z (saturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | R in p.u. | SOLAR | NEGATIVE_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1
Solar | Negative Sequence Z (saturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | X in p.u. | SOLAR | NEGATIVE_SEQ_Z_X-SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Solar | Zero Sequence Z (saturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | R in p.u. | SOLAR | ZERO_SEQ_Z_R_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U
Solar | Zero Sequence Z (saturated) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | X in p.u. | SOLAR | ZERO_SEQ_Z_X_SATURATED_PU |  | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Solar | Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | p.u. | SOLAR | ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Solar | Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | p.u. | SOLAR | ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Solar | Zero Sequence Resistance In P.u. (100 Mva Base) | 04/24/2012 Remove field from database and form. No validation. | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | p.u. | SOLAR | ZERO_SEQ_RESISTANCE_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Solar | Zero Sequence Reactance In P.u. (100 Mva Base) | 04/24/2012 Remove field from database and form. No validation. | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | p.u. | SOLAR | ZERO_SEQ_Reactance_PU |  | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)]
Solar | Generator Auxiliary Load |  |  |  | Planning - Solar |  |  | Not in table | Not in table
Solar | Average Amount of Auxiliary Real Power |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | MW | SOLAR | AUX_MWTOTAL |  | 1) This field is optional 2) Data type is float 3) Value must be < Parameters - GEN - High Reasonability Limit 4) Warn if value > (High Reasonability Limit) * .75 5) Error if value > (High Reasonability Limit) * .66
Solar | Average Amount of Auxiliary Reactive Power |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | MVAR | SOLAR | AUX_MVARTOTAL |  | 1) This field is optional 2) Data type is Float 3) Value must be < Reactive Capability - GEN - Maximum Lagging Operating Capability (MVAR) 4) Warn if value > ( Maximum Lagging Operating Capability) * .75 5) Error if value > ( Maximum Lagging Operating Capability) * .66
Solar | Auxiliary Load Power Factor | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | AUX_LOAD_PWR_FACT |  | Between .8 and 1.0
Solar | Generation Auxiliary Load Characteristics for MW Load |  |  |  | Planning - Solar |  |  | Not in table | Not in table
Solar | Large Motor, percent of total MW load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | LRG_MTR_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
Solar | Small Motor, percent of total MW load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | SML_MTR_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
Solar | Resistive (Heating) Load, percent of total MW load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | RESISTIVE_LOAD_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
Solar | Discharge Lighting, percent of total MW load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | DISCHARGE LIGHT_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
Solar | Other, percent of total MW load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | OTH_PER_TOT_MW_LOAD |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y'
Solar | Generation Auxiliary Load Characteristics for MVAR Load |  |  |  | Planning - Solar |  |  | Not in table | Not in table
Solar | Large Motor, percent of total MVAR load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | LRG_MTR_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y'
Solar | Small Motor, percent of total MVAR load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | SML_MTR_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y'
Solar | Discharge Lighting, percent of total MVAR load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | DISCHARGE LIGHT_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y'
Solar | Other, percent of total MVAR load | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | OTH_PER_TOT_MVAR_LOAD |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y'
Solar | INVERTER STEP-UP TRANSFORMER DATA |  |  |  | Planning - Solar |  |  | Not in table | Not in table
Solar | High Side Voltage Level (nominal) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | kV | SOLAR | HIGH_SIDE_VT_LEVL |  | 1) This field is required 2) Data type must be real 3) Generate an Error if not between 345 and 69
Solar | Low Side Voltage Level (nominal) |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | kV | SOLAR | LOW_SIDE_VT_LEVL |  | 1) This field is required 2) Data type must be real 3) Generate an Error if not < 69
Solar | High Side Voltage Connection - Wye / Wye - Grounded / Delta |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | HIGH_SIDE_VT_CONNT |  | 1) This field is required 2) Data type must be from list (Wye, Wye - Grounded or Delta) 3) Generate an Error if blank
Solar | Low Side Voltage Connection - Wye / Wye - Grounded / Delta |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | LOW_SIDE_VT_CONNT |  | 1) This field is required 2) Data type must be from list (Wye, Wye - Grounded or Delta) 3) Generate an Error if blank
Solar | Impedance Z |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | p.u. | SOLAR | IMPEDANCE_Z |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0
Solar | X/r Ratio |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | X_R_RATIO |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 1
Solar | Zero Sequence Z |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | p.u. | SOLAR | ZERO_SEQ_Z |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0
Solar | Zero Sequence X/r Ratio |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | ZERO_SEQ_X_R_RATIO |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 1
Solar | Base Mva For Transformer Data |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | MVA | SOLAR | BASE_MVA_TRANSFORMER_DATA |  | 1) This field is required 2) Data type must be real 3) Generate an Error if blank, Generate Warning if > 2000
Solar | Inverter Limits In P.u. Of Nominal Output For Fault Duty Studies |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | p.u. | SOLAR | INVERTER_LIMT_PU_NOMINAL_FAULT_DUTY_STUDIES
Solar | VOLTAGE REGULATION |  |  |  | Planning - Solar |  |  | Not in table | Not in table
Solar | Automatic Voltage Regulation | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | Y/N | SOLAR | AUTO_VLT_REG |  | 1) This field is required 2) Value must be from the following list: 'Y', 'N'
Solar | Does Transformer Have A Load Tap Changer? | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | Y/N | SOLAR | TRANS_LOAD_TAPCHARGER |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) Value must be from the following list: 'Y', 'N' 3) Load Tap Changer is expected to be 'Y' when total number of tap positions >=16. Warn if "Load Tap Changer" = 'N' and Total Number of Tap Positions>=16
Solar | Location of Tap Changer High or Low | 03/28/2012 Removed High or Low from Field Name and removed validation Rule #3. Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | List | SOLAR | LOC_LOAD_TAPCHARGER |  | 1) This field is conditionally required if 'Does Transformer have a Load Tap Changer ?' = 'Y' 2) Value must be of the following: 'HIGH', 'LOW, BOTH, NONE' 3) Load Tap Changer should be 'Y' when AVR is 'Y'. Generate an error if Load Tap Changer is 'N' and AVR = 'Y'. | T | Planning
Solar | Base Kv Of Regulated Side | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | kV | SOLAR | BASE_LV_REG_SIDE |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 5) The value must be >= Low Voltage Level (no-load)
Solar | Target Kv Of Regulated Side | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | kV | SOLAR | TARG_KV_REG_SIDE |  | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) Value must be > 0
Solar | Acceptable Deviation Of Target Voltage | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View |  | SOLAR | DEVITON_TARG_VT |  | 1) This field is required 2) Data type must be real 3) Generate an Error if < 0
Solar | ONLY IF HIGH SIDE TAP EXISTS |  |  |  | Planning - Solar |  |  | Not in table | Not in table
Solar | Tap Position At Manufactured Nominal Voltage | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | Y/N | SOLAR | TAP_POS_MAN_NOMINAL_VT_HIGH |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
Solar | Total Number Of Tap Positions |  | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | Integer | SOLAR | TOT_NUM_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
Solar | Normal Tap Position | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | Integer | SOLAR | NORML_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
Solar | Lowest Tap Position | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | Integer | SOLAR | LOW_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
Solar | Voltage At Lowest Tap Position | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | kV | SOLAR | VT_LOWST_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be real 3) Generate an Warning if not within 15% of nominal on tapped side of transformer
Solar | Highest Tap Position | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | Integer | SOLAR | HIGH_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be int 3) Generate an Warning if not between +/- 33
Solar | Voltage At Highest Tap Position | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | kV | SOLAR | VT_HIGHST_TAP_POSITNS_HIGH |  | 1) This field is required 2) Data type must be real 3) Generate an Warning if not within 15% of nominal on tapped side of transformer
Solar | Size Of Each Voltage Level Step | Added Validation 03/27/2012 | ADD 04/2012 |  | Planning - Solar | PLANNING_Solar.View | kV | SOLAR | SIZE_EACH_VT_LEVL_STEP_HIGH |  | 1) This field is required 2) Data type must be real 3) Generate an Warning if not within 10% of nominal kV / number of taps
Solar | PSSE MODEL : THE FOLLOWING LIST OF FILES ARE REQUIRED TO BE SUBMITTED IF THIS IS AN INITIAL REGISTRATION OR IF THERE ARE CHANGES MODIFYING PREVIOUSLY SUBMITTED PSSE FILES. PLEASE INCLUDE ALL PSSE FILES IN A ZIP OR COMPRESSED FOLDER FILE ALONG WITH YOUR RARF SUBMITTAL IN THE SAME SERVICE REQUEST |  |  |  | Planning - Solar |  |  | Not in table | Not in table
Solar | Psse Compatible Solar Pv Generator Models |  |  |  | Planning - Solar |  | Y/N | Not in table | Not in table
Solar | Dynamic Reactive Device Form/models |  |  |  | Planning - Solar |  | Y/N | Not in table | Not in table
Solar | Protection - Solar |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View |  | Not in table | Not in table
Solar | GENERATOR DETAILS |  |  |  | Protection - Solar |  |  | Not in table | Not in table
Solar | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View |  | SOLAR | UNIT_NAME |  | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R
Solar | Resource Name (Unit Code/Mnemonic) |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View |  | SOLAR | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C
Solar | Breaker Interruption Time |  |  |  | Protection - Solar |  |  | Not in table | Not in table
Solar | Breaker Interruption Time |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | cycles | SOLAR | BREAKER_INTERRUP |  | 1) this field is required 2) Data type must be Integer | R
Solar | PLANT VOLTAGE PROTECTION |  |  |  | Protection - Solar |  |  | Not in table | Not in table
Solar | Instantaneous Undervoltage Trip |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | p.u. | SOLAR | UVOLT_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Solar | Undervoltage 1 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | p.u. | SOLAR | UVOLT_TRIP_VOLT1 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Solar | Time 1 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | UVOLT_TRIP_TIME1 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Solar | Undervoltage 2 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | p.u. | SOLAR | UVOLT_TRIP_VOLT2 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Solar | Time 2 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | UVOLT_TRIP_TIME2 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Solar | Undervoltage 3 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | p.u. | SOLAR | UVOLT_TRIP_VOLT3 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Solar | Time 3 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | UVOLT_TRIP_TIME3 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Solar | Undervoltage 4 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | p.u. | SOLAR | UVOLT_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Solar | Time 4 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | UVOLT_TRIP_VOLT4 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Solar | Instantaneous Overvoltage Trip |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | p.u. | SOLAR | OVOLT_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Solar | Overvoltage 1 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | p.u. | SOLAR | OVOLT_TRIP_VOLT1 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Solar | Time 1 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | OVOLT_TRIP_TIME1 |  | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Solar | Overvoltage 2 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | p.u. | SOLAR | OVOLT_TRIP_VOLT2 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Solar | Time 2 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | OVOLT_TRIP_TIME2 |  | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Solar | Overvoltage 3 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | p.u. | SOLAR | OVOLT_TRIP_VOLT3 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Solar | Time 3 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | OVOLT_TRIP_TIME3 |  | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Solar | Overvoltage 4 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | p.u. | SOLAR | OVOLT_TRIP_VOLT4 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u
Solar | Time 4 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | OVOLT_TRIP_TIME4 |  | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u
Solar | PLANT FREQUENCY PROTECTION |  |  |  | Protection - Solar |  |  | Not in table | Not in table
Solar | Instantaneous Underfrequency Trip |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Hz | SOLAR | UFREQ_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float
Solar | Underfrequency 1 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Hz | SOLAR | UFREQ_TRIP_HZ1 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab
Solar | Time 1 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | UFREQ_TRIP_TIME1 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Solar | Underfrequency 2 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Hz | SOLAR | UFREQ_TRIP_HZ2 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab
Solar | Time 2 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | UFREQ_TRIP_TIME2 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Solar | Underfrequency 3 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Hz | SOLAR | UFREQ_TRIP_HZ3 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab
Solar | Time 3 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | UFREQ_TRIP_TIME3 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Solar | Underfrequency 4 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Hz | SOLAR | UFREQ_TRIP_HZ4 |  | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab
Solar | Time 4 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | UFREQ_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Solar | Instantaneous Overfrequency Trip |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Hz | SOLAR | OFREQ_TRIP_INSTANT |  | 1) This field is optional 2) Data type must be Float
Solar | Overfrequency 1 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Hz | SOLAR | OFREQ_TRIP_HZ1 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab
Solar | Time 1 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | OFREQ_TRIP_TIME1 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Solar | Overfrequency 2 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Hz | SOLAR | OFREQ_TRIP_HZ2 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab
Solar | Time 2 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | OFREQ_TRIP_TIME2 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Solar | Overfrequency 3 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Hz | SOLAR | OFREQ_TRIP_HZ3 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab
Solar | Time 3 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | OFREQ_TRIP_TIME3 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Solar | Overfrequency 4 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Hz | SOLAR | OFREQ_TRIP_HZ4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab
Solar | Time 4 |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | sec | SOLAR | OFREQ_TRIP_TIME4 |  | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab
Solar | PV INVERTER VRT CAPABILITY |  |  |  | Protection - Solar |  |  | Not in table | Not in table
Solar | Provide Manufacturer's Technical Document / Simulation Results / Test Result, Etc. Describing The Solar Technology & Vrt OPTIons Purchased With Inverter, If Any |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Y/N | SOLAR | MAN_TECH_DOC_SIM_RESULTS
Solar | Do Personnel (onsite Operator/engineer Etc.) Have Control To Enable/disable Or Change The Settings For Voltage Ride-through |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Y/N | SOLAR | PERSONNEL_CHANGE_SET_CNTRL
Solar | Does The Resource Use Dynamic Reactive Devices (SVC/statcom, Etc.) At Solar Plant Facility? - (note: Capacitor Banks Used For Conventional Reactive Support Cannot Be Considered As Dynamic Reactive Devices) - If Yes, Please Provide Supporting Documentation. (manufacturer's Technical Document, Pss/e Model Etc.) |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Y/N | SOLAR | DYNAMIC_REACT_DEVICES
Solar | Provide Inverter Voltage & Frequency Protection Settings As Per Manufacturer - Technical Document And/or Spec Sheet |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Y/N | SOLAR | INVERTER_VOLTAGE_FREQ_PROT_SET
Solar | Does The Resource Have Plant Voltage Protection? If Yes, Please Provide Supporting Documentation. |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Y/N | SOLAR | RE_PLANT_VOLTAGE_PROT
Solar | Does The Resource Have Feeder Voltage Protection? If Yes, Please Provide Supporting Documentation. |  | ADD 04/2012 |  | Protection - Solar | Audit - Solar_Protection.View Delta - PROTECTION_Solar.View | Y/N | SOLAR | RE_VOLTAGE_FEEDER_PROT
Solar | Collector System - Solar | Corrected Tab name 03/26/2012 |  |  | Collector System - Solar |  |  | Not in table | Not in table
Solar | Site Code | 04/19/2012 Added field to Mapping but not added to Form |  |  | Collector System - Solar |  |  | SITECODES | SITE_CODE
SOLAR | Resource Name (Unit Code/Mnemonic) | 05/17/2012 Update #3 validation Added field in form 03/26/2012 |  |  | Collector System - Solar |  |  | COLLECTOR_SYS | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters for split gen resources | C
Solar | COLLECTION SYSTEM DETAILED MODEL | Corrected Tab name 03/26/2012 |  |  | Collector System - Solar |  |  | Not in table | Not in table
Solar | Cable Type | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Solar | CollectorSystem.View |  | COLLECTOR_SYS | CABLE_TYPE |  | 1) This field is required 2) Data type must string 3) Generate an Warning if blank
Solar | Voltage Level kV | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Solar | CollectorSystem.View | kV | COLLECTOR_SYS | VT_LEVEL_KV |  | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0
Solar | POSITIVE SEQUENCE DATA | Corrected Tab name 03/26/2012 |  |  | Collector System - Solar |  | Label | Not in table | Not in table
Solar | R/kft | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Solar | CollectorSystem.View | R/kft | COLLECTOR_SYS | POS_R_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank
Solar | X/kft | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Solar | CollectorSystem.View | X/kft | COLLECTOR_SYS | POS_X_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank
Solar | Charging Bc/kft | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Solar | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | POS_CHRG_BC_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank
Solar | ZERO SEQUENCE DATA | Corrected Tab name 03/26/2012 |  |  | Collector System - Solar |  | Label | Not in table | Not in table
Solar | R0/kft | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Solar | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | ZERO_R0_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank
Solar | X0/kft | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Solar | CollectorSystem.View | (p.u. on 100 MVA base) | COLLECTOR_SYS | ZERO_X0_KFT |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank
Solar | Collector System-Solar Seg Data | Corrected Tab name 03/26/2012 |  |  | Collector System - Seg Data Solar |  |  | Not in table | Not in table
Solar | Site Code | 04/19/2012 Added field to Mapping but not added to Form |  |  | Collector System - Seg Data Solar |  |  | SITECODES | SITE_CODE
Solar | CABLE TYPE | Corrected Tab name 03/26/2012 |  |  | Collector System - Seg Data Solar |  |  | Not in table | Not in table
Solar | Cable Type | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Seg Data Solar | CollectorSystem_SegData.View |  | CABLE_SEG_DATA | CABLE_TYPE |  | 1) This field is required 2) Data type must string 3) Generate an Warning if blank
SOLAR | Resource Name (Unit Code/Mnemonic) | Added 03/26/2012 |  |  | Collector System - Seg Data Solar |  |  | CABLE_SEG_DATA | UNIT_CODE |  | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | C
Solar | CABLE SEGAMENT DATA | Corrected Tab name 03/26/2012 |  |  | Collector System - Seg Data Solar |  |  | Not in table | Not in table
Solar | From | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Seg Data Solar | CollectorSystem_SegData.View | Integer | CABLE_SEG_DATA | CABLE_SEG_DATA_FROM |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank
Solar | To | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Seg Data Solar | CollectorSystem_SegData.View | Integer | CABLE_SEG_DATA | CABLE_SEG_DATA_TO |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank
Solar | Circuit Number | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Seg Data Solar | CollectorSystem_SegData.View | Integer | CABLE_SEG_DATA | CIRCT_NUM |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank
Solar | Voltage Level | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Seg Data Solar | CollectorSystem_SegData.View | kV | CABLE_SEG_DATA | VT_LEVL |  | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0.
Solar | Cable Segment Length | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Seg Data Solar | CollectorSystem_SegData.View | in kft | CABLE_SEG_DATA | CABLE_SEG_LENTH |  | 1) This field is required 2) Data type must float 3) Generate an Warning if blank
Solar | Number of Turbines On Cable Segment | Corrected Tab name 03/26/2012 | ADD 04/2012 |  | Collector System - Seg Data Solar | CollectorSystem_SegData.View | Integer | CABLE_SEG_DATA | NUM_TURBIN_ON_CABLE_SEG |  | 1) This field is required 2) Data type must integer 3) Generate an Warning if blank
Solar | Load Characteristics for MVAR Load |  |  |  | Private Network -Solar |  |  | Not in table | Not in table
Solar | Private Network - Unit - Solar |  |  |  | Private Network - Unit - Solar |  |  | Not in table | Not in table
Solar | GENERATOR DETAILS |  |  |  | Private Network - Unit - Solar |  |  | Not in table | Not in table
Solar | Unit Name | Do not show Message on Audit or Delta | ADD 04/2012 | Private Network - Unit - Solar | Private Network - Unit - Solar | Solar_PrivateNetwork.View | List | SITECODES | UNIT_NAME | 1. This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | 1. This field is not null. Data type: Character. | R | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS
Solar | SITE_CODE |  | ADD 04/2012 | Private Network - Unit - Solar | Private Network - Unit - Solar | Solar_PrivateNetwork.View | Automatic | SITECODES | SITE_CODE |  | 1. This field is not null. Validate with the existing record in ERCOT. Validate with the existing record in ERCOT. Generate an error if the Site Code submitted do not match with the existing records in ERCOT. 2. All should be capital letters
Solar | Resource Name (Unit Code/Mnemonic) | Do not show Message on Audit or Delta | ADD 04/2012 | Private Network - Unit - Solar | Private Network - Unit - Solar | Solar_PrivateNetwork.View | Automatic | SITECODES | UNIT_CODE | 1. Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2.All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 13 characters for split gen resources | Character | Lodestar
Solar | PRIVATE NETWORK - Unit Information |  |  |  | Private Network - Unit - Solar |  |  | Not in table | Not in table
Solar | Average Amount of Self-Serve private load |  | ADD 04/2012 |  | Private Network - Unit - Solar | Solar_PrivateNetwork.View | MW | SOLAR | AVG_LD_MW_UNIT
Solar | Average Amount of Self-Serve private reactive load |  | ADD 04/2012 |  | Private Network - Unit - Solar | Solar_PrivateNetwork.View | MVAR | SOLAR | AVG_LD_MVAR_UNIT
Solar | Expected Typical Private Network Net Interchange |  | ADD 04/2012 |  | Private Network - Unit - Solar | Solar_PrivateNetwork.View | MW | SOLAR | NET_INTERCHNG_MW_UNIT
Solar | Expected Typical Private Network Net Reactive Interchange |  | ADD 04/2012 |  | Private Network - Unit - Solar | Solar_PrivateNetwork.View | MVAR | SOLAR | NET_INTERCHNG_MVAR_UNIT
Solar | Private Network Gross Unit Capability |  | ADD 04/2012 |  | Private Network - Unit - Solar | Solar_PrivateNetwork.View | MW | SOLAR | GROSS_CAPBLTY_MW_UNIT
Solar | Private Network Gross Unit Reactive Capability |  | ADD 04/2012 |  | Private Network - Unit - Solar | Solar_PrivateNetwork.View | MVAR | SOLAR | GROSS_CAPBLTY_MVAR_UNIT
Solar | If Unit trips, does Load trip? |  | ADD 04/2012 |  | Private Network - Unit - Solar | Solar_PrivateNetwork.View | Y/N | SOLAR | LOAD_TRIP_FLG
Solar | If yes, approximate percentage of Load that will trip? | 05/03/2012 removed percent from label on form | ADD 04/2012 |  | Private Network - Unit - Solar | Solar_PrivateNetwork.View |  | SOLAR | LOAD_TRIP_PCT
Note on H6: This column represents the name of the SQL file/view that uses the field. The name is the same for Delta and Aufit reports unless otherwise noted. The full filename convention is dbo.[RARFAUDIT or DELTA].[Source Report Name].sql

## Sheet3 (hidden)
RARF DATA FIELD | RARF Tab | Label | Business Rules/Basic UI validations | Field/ Tab Type | Data type | Validation Type | Source | Destination Application | Comments
Zero Sequence Grounding Resistance For An Impedance Grounded Transformer In P.u. (100 Mva Base) | Transformer Data | p.u. | 1) This field is required and Data type is numeric 2) Value must be greater than or equal to 0.0 and less than or equal to 99999.0 | R |  |  | Model Adminstration
Zero Sequence Grounding Reactance For An Impedance Grounded Transformer In P.u. (100 Mva Base) | Transformer Data | p.u. | 1) This field is required and Data type is numeric 2) Value must be greater than or equal to 0.0 and less than or equal to 99999.0 | R |  |  | Model Adminstration
Zero Sequence Resistance In P.u. (100 Mva Base) | Transformer Data | p.u. | 1) This field is required and Data type is numeric 2) Generate a Warning if the per unit value entered is not >= 0.0 and <= 100.0 | R |  |  | Model Adminstration
Zero Sequence Reactance In P.u. (100 Mva Base) | Transformer Data | p.u. | 1) This field is required and Data type is numeric 2)Generate a Warning if the per unit value entered is not >= 0.0 and <= 100.0 | R |  |  | Model Adminstration
Positive Sequence Resistance (100 MVA Base) | Transformer Data | p.u. | ) This field is required and Data type is numeric 2) Generate a Warning if the per unit value entered is not > 0.0 and <= 2.0 3) Error If series_resist < 0 and Low_NoLoad !=1 4) Warning if Low_NoLoad != 1 and Resistance/Reactance ratio > 1 5) Error if Resistance value has precision less than 3 decimal places 6) Warning if Resistance value has precision less than 5 decimal places | R |  |  | Model Adminstration
Positive Sequence Reactance (100 MVA Base) | Transformer Data | p.u. | 1) This field is required and Data type is numeric 2) Generate a Warning if the per unit value entered is not > 0.0 and <= 2.0 3) Error If series_react < 0 and Low_NoLoad !=1 4) Error if series_react > 2.0 5) Error if Reactance value has precision less than 3 decimal places 6) Warning if Reactance value has precision less than 5 decimal places | R |  |  | Model Adminstration

## Sheet5 (hidden)
RARF FORM TYPE | RARF DATA FIELD | Field Updates | Change Description | RARF Tab | Source Report Name | Label | TABLE | DB Field | Business Rules/Basic UI validations | Field/ Tab Type | Data type | Validation Type
Generation | Large Motor, Percent Of Total Mw Load | 8/13/2013 changed field type to Conditional 05/03/2012 removed percent from label on form |  | Planning - GEN |  |  | GENERATION | AUXMW_LARGEMTR_PCT | 1)This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Percent | B,DVB
Generation | Small Motor, Percent Of Total Mw Load | 8/13/2013 changed field type to Conditional 05/03/2012 removed percent from label on form |  | Planning - GEN |  |  | GENERATION | AUXMW_SMALLMTR_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | C | Percent | B,DVB
Generation | Resistive (heating) Load, Percent Of Total Mw Load | 8/13/2013 changed field type to Conditional 05/03/2012 removed percent from label on form |  | Planning - GEN |  |  | GENERATION | AUXMW_RESISTIVE_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB
Generation | Discharge Lighting, Percent Of Total Mw Load | 8/13/2013 changed field type to Conditional 05/03/2012 removed percent from label on form |  | Planning - GEN |  |  | GENERATION | AUXMW_DISCHARGE_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB
Generation | Other, Percent Of Total Mw Load | 8/13/2013 changed field type to Conditional 05/03/2012 removed percent from label on form |  | Planning - GEN |  |  | GENERATION | AUXMW_OTHER_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB
Generation | Large Motor, Percent Of Total Mvar Load | 8/13/2013 changed field type to Conditional 05/03/2012 removed percent from label on form |  | Planning - GEN |  |  | GENERATION | AUXMVAR_LARGEMTR_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Reactive Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Percent | B,DVB
Generation | Small Motor, Percent Of Total Mvar Load | 8/13/2013 changed field type to Conditional 05/03/2012 removed percent from label on form |  | Planning - GEN |  |  | GENERATION | AUXMVAR_SMALLMTR_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Reactive Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | C | Percent | B,DVB
Generation | Discharge Lighting, Percent Of Total Mvar Load | 8/13/2013 changed field type to Conditional 05/03/2012 removed percent from label on form |  | Planning - GEN |  |  | GENERATION | AUXMVAR_DISCHARGE_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Reactive Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | C | Percent | B,DVB
Generation | Other, Percent Of Total Mvar Load | 8/13/2013 changed field type to Conditional 05/03/2012 removed percent from label on form |  | Planning - GEN |  |  | GENERATION | AUXMVAR_OTHER_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Reactive Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | C | Percent | B,DVB
CC | Large Motor, Percent Of Total Mw Load | 8/13/2013 changed field type to Conditional 05/03/2012 removed percent from label on form |  | Planning - CC |  |  | CCUNIT | AUXMW_LARGEMTR_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Percent | B,DVB
CC | Small Motor, Percent Of Total Mw Load | 8/13/2013 changed field type to Conditional 05/03/2012 removed percent from label on form |  | Planning - CC |  |  | CCUNIT | AUXMW_SMALLMTR_PCT | This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | C | Percent | B,DVB
CC | Resistive (heating) Load, Percent Of Total Mw Load | 8/13/2013 changed field type to Conditional 05/03/2012 removed percent from label on form |  | Planning - CC |  |  | CCUNIT | AUXMW_RESISTIVE_PCT | 1)This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB
CC | Discharge Lighting, Percent Of Total Mw Load | 8/13/2013 changed field type to Conditional 05/03/2012 removed percent from label on form |  | Planning - CC |  |  | CCUNIT | AUXMW_DISCHARGE_PCT | 1)This field is CONDITIONAL (Not required when Average Amount Of Real Power value is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB
CC | Other, Percent Of Total Mw Load | 8/13/2013 changed field type to Conditional 05/03/2012 removed percent from label on form |  | Planning - CC |  |  | CCUNIT | AUXMW_OTHER_PCT | 1)This field is CONDITIONAL (Not required when Average Amount Of Real Power value zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Percent | B,DVB
CC | Large Motor, Percent Of Total Mvar Load | 8/13/2013 changed field type to Conditional 05/03/2012 removed percent from label on form |  | Planning - CC |  |  | CCUNIT | AUXMVAR_LARGEMTR_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Reactive Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Percent | B,DVB
CC | Small Motor, Percent Of Total Mvar Load | 8/13/2013 changed field type to Conditional 05/03/2012 removed percent from label on form |  | Planning - CC |  |  | CCUNIT | AUXMVAR_LARGEMTR_PCT | 1)This field is CONDITIONAL (Not required when Average Amount Of Reactive Power Value is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | C | Percent | B,DVB
CC | Discharge Lighting, Percent Of Total Mvar Load | 8/13/2013 changed field type to Conditional 05/03/2012 removed percent from label on form |  | Planning - CC |  |  | CCUNIT | AUXMVAR_DISCHARGE_PCT | 1)This field is CONDITIONAL (Not required when Average Amount Of Reactive Power value is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | C | Percent | B,DVB
CC | Other, Percent Of Total Mvar Load | 8/13/2013 changed field type to Conditional 05/03/2012 removed percent from label on form |  | Planning - CC |  |  | CCUNIT | AUXMVAR_OTHER_PCT | 1)This field is CONDITIONAL (Not required when Average Amount Of Reactive Power value is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | C | Percent | B,DVB
Wind | Large Motor, Percent Of Total Mw Load | 8/13/2013 changed field type to Conditional and updated validation 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | LRG_MTR_PER_TOT_MW_LOAD | 1)This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Numeric | B,DVB
Wind | Small Motor, Percent Of Total Mw Load | 8/13/2013 changed field type to Conditional and updated validation 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | SML_MTR_PER_TOT_MW_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | C | Numeric | B,DVB
Wind | Resistive (heating) Load, Percent Of Total Mw Load | 8/13/2013 changed field type to Conditional and updated validation 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | RESISTIVE_LOAD_PER_TOT_MW_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Numeric | B,DVB
Wind | Discharge Lighting, Percent Of Total Mw Load | 8/13/2013 changed field type to Conditional and updated validation 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | DISCHARGE LIGHT_PER_TOT_MW_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Numeric | B,DVB
Wind | Other, Percent Of Total Mw Load | 8/13/2013 changed field type to Conditional and updated validation 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | OTH_PER_TOT_MW_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | C | Numeric | B,DVB
Wind | Large Motor, Percent Of Total MVAR Load | 8/13/2013 changed field type to Conditional and updated validation 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | LRG_MTR_PER_TOT_MVAR_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Reactive Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | C | Numeric | B,DVB
Wind | Small Motor, Percent Of Total MVAR Load | 8/13/2013 changed field type to Conditional and updated validation 05/03/2012 removed percent from label on form | Updated: 05/22/2013 This field is conditional.ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | SML_MTR_PER_TOT_MVAR_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Reactive Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | C | Numeric | B,DVB
Wind | Discharge Lighting, Percent Of Total MVAR Load | 8/13/2013 changed field type to Conditional and updated validation 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | DISCHARGE LIGHT_PER_TOT_MVAR_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Reactive Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | C | Numeric | B,DVB
Wind | Other, Percent Of Total MVAR Load | 8/13/2013 changed field type to Conditional and updated validation 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | OTH_PER_TOT_MVAR_LOAD | 1) This field is CONDITIONAL (Not required when Average Amount Of Reactive Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | C | Numeric | B,DVB
Note on I1: This column represents the name of the SQL file/view that uses the field. The name is the same for Delta and Aufit reports unless otherwise noted. The full filename convention is dbo.[RARFAUDIT or DELTA].[Source Report Name].sql

## Sheet9 (hidden)
RARF DATA FIELD | Field Updates | Change Description | RARF Tab | Source Report Name | Label | TABLE | DB Field
Resource Name (Unit Code/Mnemonic) | Do not show Message on Audit or Delta | Added 12/10/13 | Turbine Details |  | all caps | TURBINE | UNIT_NAME
WGR Group | Added 12/10/13 | Added 12/10/13 | Turbine Details |  |  | TURBINE | WGR_GRP
Group Code (Hidden Field on Form) | Added 12/10/13 | Added 12/10/13 | Turbine Details |  |  | TURBINE | GRP_CODE
SITE_GROUP | Added 12/10/13 | Added 12/10/13 | Turbine Details |  |  | TURBINE | SITE_GRP
Type of Turbine (Manufacturer/Model) Turbine Manufacturer/Model | Name change and moved from Unit Info - Turbine | Moved from Unit Info - Turbine and Wind Table | Unit Info -Wind Turbine Turbine Details |  |  | WIND TURBINE | TUR_TYPE TUR_MFG_MOD
MW Rating for this model of Turbine | Moved from Unit Info - Turbine and Wind Table | Moved from Unit Info - Turbine and Wind Table | Unit Info -Wind Turbine Turbine Details |  | MW | WIND TURBINE | TUR_MW_MDL_RTG
Number of this type of Turbine Number of Turbine Manufacturer/Model | Name change and moved from Unit Info - Turbine | Moved from Unit Info - Turbine and Wind Table | Unit Info -Wind Turbine Turbine Details |  | # | WIND TURBINE | TUR_NUM
Turbine Type | Added 12/10/13 | Added 12/10/13 | Turbine Details |  | 1,2,3,4,5 | TURBINE | TUR_TYPE
What is the Mva Base That the Following Data Is Based On? | Moved from Planning - Wind tab | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | MVA | WIND TURBINE | MVABASE
What Is The Kv Base That The Following Data Is Based On? | Moved from Planning - Wind tab | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | KV | WIND TURBINE | KVBASE
Direct Axis Subtransient Reactance, X"di (unsaturated) Subtransient Reactance X'',(Instantaneous Fault Current Period) (unsaturated) | Moved from Planning - Wind tab and name change | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | p.u. | WIND TURBINE | DIRECT_AXIS_SUBSTNT_REACTANCE
Direct Axis Transient Reactance, X'di (unsaturated) Transient Reactance, X' (First 2-3 cycles of the Fault) (unsaturated) | Moved from Planning - Wind tab and name change | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | p.u. | WIND TURBINE | DIRECT_AXIS_TRANSNT_REACTANCE
Positive Sequence Z (unsaturated) Positive Sequence Resistance (unsaturated) | Moved from Planning - Wind tab and name change | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | R in p.u. | WIND TURBINE | POSITIVE_SEQ_Z_R_UNSATURATED_PU
Positive Sequence Z (unsaturated) Synchronous Reactance X (After 4 cycles of the fault) (unsaturated) | Moved from Planning - Wind tab and name change | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | X in p.u. | WIND TURBINE | POSITIVE_SEQ_Z_X_UNSATURATED_PU
Negative Sequence Z (unsaturated) | Moved from Planning - Wind tab | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | R in p.u. | WIND TURBINE | NEGATIVE_SEQ_Z_R_UNSATURATED_PU
Negative Sequence Z (unsaturated) | Moved from Planning - Wind tab | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | X in p.u. | WIND TURBINE | NEGATIVE_SEQ_Z_X-UNSATURATED_PU
Zero Sequence Z (unsaturated) | Moved from Planning - Wind tab | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | R in p.u. | WIND TURBINE | ZERO_SEQ_Z_R_UNSATURATED_PU
Zero Sequence Z (unsaturated) | Moved from Planning - Wind tab | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | X in p.u. | WIND TURBINE | ZERO_SEQ_Z_X_UNSATURATED_PU
Direct Axis Subtransient Reactance, X"dv (saturated) Subtransient Reactance X'',(Instantaneous Fault Current Period) (saturated) | Moved from Planning - Wind tab and name change | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | p.u. | WIND TURBINE | DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED
Direct Axis Transient Reactance, X'dv (saturated) Transient Reactance, X' (First 2-3 cycles of the Fault) (saturated) | Moved from Planning - Wind tab and name change | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | p.u. | WIND TURBINE | DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED
Positive Sequence Z (saturated) Positive Sequence Resistance (saturated) | Moved from Planning - Wind tab and name change | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | R in p.u. | WIND TURBINE | POSITIVE_SEQ_Z_R_PU
Positive Sequence Z (saturated) Synchronous Reactance X (After 4 cycles of the fault) (saturated) | Moved from Planning - Wind tab and name change | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | X in p.u. | WIND TURBINE | POSITIVE_SEQ_Z_X_PU
Negative Sequence Z (saturated) | Moved from Planning - Wind tab | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | R in p.u. | WIND TURBINE | NEGATIVE_SEQ_Z_R_PU
Negative Sequence Z (saturated) | Moved from Planning - Wind tab | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | X in p.u. | WIND TURBINE | NEGATIVE_SEQ_Z_X_PU
Zero Sequence Z (saturated) | Moved from Planning - Wind tab | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | R in p.u. | WIND TURBINE | ZERO_SEQ_Z_R_PU
Zero Sequence Z (saturated) | Moved from Planning - Wind tab | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | X in p.u. | WIND TURBINE | ZERO_SEQ_Z_X_PU
Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) Grounding Resistance For An Impedance Grounded Generator In P.U. (100 Mva Base) | Moved from Planning - Wind tab and name change | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | p.u. | WIND TURBINE | ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU
Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) Grounding Reactance For An Impedance Grounded Generator In P.U. (100 Mva Base) | Moved from Planning - Wind tab and name change | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | p.u. | WIND TURBINE | ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU
Instantaneous Controlled Fault Current Magnitude (% of full load current) for Turbine Types 3 & 4 | Added 12/10/13 | Added 12/10/13 | Turbine Details |  | p.u. | TURBINE | INST_CTRL_FAULT_CUR_MAG
Controlled Fault Current Magnitude At 2 to 3 cycles after fault (% of full load current) for Turbine Types 3 & 4 | Added 12/10/13 | Added 12/10/13 | Turbine Details |  | p.u. | TURBINE | CTRL_FAULT_CUR_MAG_TWO_THREE_CYCLES
Controlled Fault Current Magnitude At 4 plus cycles after fault (% of full load current) for Turbine Types 3 & 4 | Added 12/10/13 | Added 12/10/13 | Turbine Details |  | p.u. | TURBINE | CTRL_CTRL_FAULT_CUR_MAG_FOUR_PLUS_CYCLES
High Side Voltage Level (nominal) | Moved from Planning - Wind tab | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | Kv | WIND TURBINE | HIGH_SIDE_VT_LEVL
Low Side Voltage Level (nominal) | Moved from Planning - Wind tab | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | KV | WIND TURBINE | LOW_SIDE_VT_LEVL
High Side Voltage Connection | Moved from Planning - Wind tab | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | List | WIND TURBINE | HIGH_SIDE_VT_CONNT
Low Side Voltage Connection | Moved from Planning - Wind tab | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | List | WIND TURBINE | LOW_SIDE_VT_CONNT
Impedance Z | Moved from Planning - Wind tab | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | p.u. | WIND TURBINE | IMPEDANCE_Z
X/R Ratio | Moved from Planning - Wind tab | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View |  | WIND TURBINE | X_R_RATIO
Zero Sequence Z | Moved from Planning - Wind tab | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | p.u. | WIND TURBINE | ZERO_SEQ_Z
Zero Sequence X/R Ratio | Moved from Planning - Wind tab | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View |  | WIND TURBINE | ZERO_SEQ_X_R_RATIO
Base Mva For Transformer Data | Moved from Planning - Wind tab | Moved from Planning - Wind tab and Wind Table | Planning - Wind Turbine Details | PLANNING_WIND.View | MVA | WIND TURBINE | BASE_MVA_TRANSFORMER_DATA
Resource Name (Unit Code/Mnemonic) | Do not show Message on Audit or Delta |  | Planning - Wind |  | all caps | WIND | UNIT_NAME
Type of Turbine | Moved to Turbine Details Tab Corrected DB_FIELD 03/01/2012 | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table | Planning - Wind |  | List | WIND | TUR_TYPE
What is the Mva Base That the Following Data Is Based On? | Moved to Turbine Details Tab | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table | Planning - Wind | PLANNING_WIND.View | MVA | WIND | MVABASE
What Is The Kv Base That The Following Data Is Based On? | Moved to Turbine Details Tab | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table | Planning - Wind | PLANNING_WIND.View | KV | WIND | KVBASE
Direct Axis Subtransient Reactance, X"di (unsaturated) | Moved to Turbine Details Tab 05/06/2013 Added Validation #3 11/05/12 Updated Business Rule #2 10/08/2012 updated rules CR 46803 | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | DIRECT_AXIS_SUBSTNT_REACTANCE
Direct Axis Transient Reactance, X'di (unsaturated) | Moved to Turbine Details Tab 05/06/2013 Added Validation #3 11/05/12 Updated Business Rule #2 10/08/2012 updated rules CR 46803 | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | DIRECT_AXIS_TRANSNT_REACTANCE
Positive Sequence Z (unsaturated) | Moved to Turbine Details Tab 11/05/12 Updated Business Rule #2 07/03/2012 Change field name in Data base | 12/10/13 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View | R in p.u. | WIND | POSITIVE_SEQ_Z_R_UNSATURATED_PU
Positive Sequence Z (unsaturated) | Moved to Turbine Details Tab 11/05/12 Updated Business Rule #2 10/08/2012 Updated Business Rule. CR 46804 07/03/2012 Change field name in Data base | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View | X in p.u. | WIND | POSITIVE_SEQ_Z_X_UNSATURATED_PU
Negative Sequence Z (unsaturated) | Moved to Turbine Details Tab 11/05/12 Updated Business Rule #2 07/03/2012 Change field name in Data base | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table | Planning - Wind | PLANNING_WIND.View | R in p.u. | WIND | NEGATIVE_SEQ_Z_R_UNSATURATED_PU
Negative Sequence Z (unsaturated) | Moved to Turbine Details Tab 11/05/12 Updated Business Rule #2 10/08/2012 Updated Business Rule. CR 46804 07/03/2012 Change field name in Data base | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View | X in p.u. | WIND | NEGATIVE_SEQ_Z_X-UNSATURATED_PU
Does Zero Sequence Z exist? | Remove Field 12/10/13 ADDED 06/27/2012 | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View | Y/N | WIND | DOES_ZERO_SEQ_EXIST
Zero Sequence Z (unsaturated) | Moved to Turbine Details Tab 10/08/2012 Updated Business Rule. CR 46804 07/03/2012 Change field name in Data base | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View | R in p.u. | WIND | ZERO_SEQ_Z_R_UNSATURATED_PU
Zero Sequence Z (unsaturated) | Moved to Turbine Details Tab 10/08/2012 Updated Business Rule. CR 46804 06/28/2012 updated | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View | X in p.u. | WIND | ZERO_SEQ_Z_X_UNSATURATED_PU
Direct Axis Subtransient Reactance, X"dv (saturated) | Moved to Turbine Details Tab 11/05/12 Updated Business Rule #2 10/08/2012 updated rules CR 46803 | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | DIRECT_AXIS_SUBSTNT_REACTANCE_SATURATED
Direct Axis Transient Reactance, X'dv (saturated) | 11/05/12 Updated Business Rule #2 10/08/2012 updated rules CR 46803 | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | DIRECT_AXIS_TRANSNT_REACTANCE_SATURATED
Positive Sequence Z (saturated) | Moved to Turbine Details Tab 11/05/12 Updated Business Rule #2 06/28/2012 updated | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table | Planning - Wind | PLANNING_WIND.View | R in p.u. | WIND | POSITIVE_SEQ_Z_R_PU
Positive Sequence Z (saturated) | Moved to Turbine Details Tab 11/05/12 Updated Business Rule #2 10/08/2012 Updated Business Rule. CR 46804 06/28/2012 updated | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table | Planning - Wind | PLANNING_WIND.View | X in p.u. | WIND | POSITIVE_SEQ_Z_X_PU
Negative Sequence Z (saturated) | Moved to Turbine Details Tab 11/05/12 Updated Business Rule #2 06/28/2012 updated | Moved to Turbine Details Tab and remove from Wind table | Planning - Wind | PLANNING_WIND.View | R in p.u. | WIND | NEGATIVE_SEQ_Z_R_PU
Negative Sequence Z (saturated) | Moved to Turbine Details Tab 11/05/12 Updated Business Rule #2 10/08/2012 Updated Business Rule. CR 46804 06/28/2012 updated | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table | Planning - Wind | PLANNING_WIND.View | X in p.u. | WIND | NEGATIVE_SEQ_Z_X_PU
Zero Sequence Z (saturated) | Moved to Turbine Details Tab 10/08/2012 Updated Business Rule. CR 46804 06/28/2012 updated | Moved to Turbine Details Tab and remove from Wind table | Planning - Wind | PLANNING_WIND.View | R in p.u. | WIND | ZERO_SEQ_Z_R_PU
Zero Sequence Z (saturated) | Moved to Turbine Details Tab 10/08/2012 Updated Business Rule. CR 46804 06/28/2012 updated | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table | Planning - Wind | PLANNING_WIND.View | X in p.u. | WIND | ZERO_SEQ_Z_X_PU
Zero Sequence Grounding Resistance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Moved to Turbine Details Tab 10/04/2012 Change rule #2 and remove rule #3 | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | ZERO_SEQ_GRUND_RESISTANCE_IMPED_GRUND_GEN_PU
Zero Sequence Grounding Reactance For An Impedance Grounded Generator In P.u. (100 Mva Base) | Moved to Turbine Details Tab 10/04/2012 Change rule #2 and remove rule #3 | Moved to Turbine Details Tab and remove from Wind table ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | ZERO_SEQ_GRUND_REACTANCE_IMPED_GRUND_GEN_PU
Average Amount Of Auxiliary Real Power | 08/13/2013 ???? 10/08/2012 Updated Validation rule CR46800 | ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View | MW | WIND | AUX_MWTOTAL
Average Amount Of Auxiliary Reactive Power | 10/19/2012 updated #3. 10/08/2012 Updated Validation rule CR46800 | ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View | MWAR | WIND | AUX_MVARTOTAL
Auxiliary Load Power Factor | 10/08/2012 Updated Validation rule CR46800 | ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | AUX_LOAD_PWR_FACT
Large Motor, Percent Of Total Mw Load | 8/13/2013 changed field type to Conditional and updated validation 2 and 3. 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | LRG_MTR_PER_TOT_MW_LOAD
Small Motor, Percent Of Total Mw Load | 8/13/2013 changed field type to Conditional and updated validation 2 and 3. 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | SML_MTR_PER_TOT_MW_LOAD
Resistive (heating) Load, Percent Of Total Mw Load | 8/13/2013 changed field type to Conditional and updated validation 2 and 3. 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | RESISTIVE_LOAD_PER_TOT_MW_LOAD
Discharge Lighting, Percent Of Total Mw Load | 8/13/2013 changed field type to Conditional and updated validation 2 and 3. 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | DISCHARGE LIGHT_PER_TOT_MW_LOAD
Other, Percent Of Total Mw Load | 8/13/2013 changed field type to Conditional and updated validation 2 and 3. 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | OTH_PER_TOT_MW_LOAD
Large Motor, Percent Of Total MVAR Load | 8/13/2013 changed field type to Conditional and updated validation 2 and 3. 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | LRG_MTR_PER_TOT_MVAR_LOAD
Small Motor, Percent Of Total MVAR Load | 8/13/2013 changed field type to Conditional and updated validation 2 and 3. 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | SML_MTR_PER_TOT_MVAR_LOAD
Discharge Lighting, Percent Of Total MVAR Load | 8/13/2013 changed field type to Conditional and updated validation 2 and 3. 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | DISCHARGE LIGHT_PER_TOT_MVAR_LOAD
Other, Percent Of Total MVAR Load | 8/13/2013 changed field type to Conditional and updated validation 2 and 3. 05/03/2012 removed percent from label on form | ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | OTH_PER_TOT_MVAR_LOAD
High Side Voltage Level (nominal) | Moved to Turbine Details Tab Updated 07/10/12 #3 | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table UPDATED 07/10/2012 ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View | Kv | Wind | HIGH_SIDE_VT_LEVL
High Side Voltage Connection | Moved to Turbine Details Tab 05/23/2012 Updated validation #2 | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View | List | Wind | HIGH_SIDE_VT_CONNT
Low Side Voltage Level (nominal) | Moved to Turbine Details Tab | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View | KV | WIND | LOW_SIDE_VT_LEVL
Low Side Voltage Connection | Moved to Turbine Details Tab 05/23/2012 Updated validation #2 | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View | List | WIND | LOW_SIDE_VT_CONNT
Impedance Z | Moved to Turbine Details Tab | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | IMPEDANCE_Z
X/R Ratio | Moved to Turbine Details Tab | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | X_R_RATIO
Zero Sequence Z | Moved to Turbine Details Tab | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View | p.u. | WIND | ZERO_SEQ_Z
Zero Sequence X/R Ratio | Moved to Turbine Details Tab | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table ADDED 06/27/2012 | Planning - Wind | PLANNING_WIND.View |  | WIND | ZERO_SEQ_X_R_RATIO
Base Mva For Transformer Data | Moved to Turbine Details Tab | 12/10/13 Moved Data to Turbine Details Tab and null values on Wind table ADDED 06/27/2012 | Planning - Wind Turbine Details | PLANNING_WIND.View | MVA | WIND | BASE_MVA_TRANSFORMER_DATA
UNIT_CABLE_FROM_TO_CIRCUIT
Note on F1: This column represents the name of the SQL file/view that uses the field. The name is the same for Delta and Aufit reports unless otherwise noted. The full filename convention is dbo.[RARFAUDIT or DELTA].[Source Report Name].sql

## Sheet12 (hidden)
FUTURE CHANGE
Generation | Mw4 | Reactive Capability - GEN | MW | GENERATION | MW4 | 1. MW4 >0 2. MW4<MW5 3. X(n) > = WMX (Unit Max output) where n is the last MW value in the curve. If the curve has 4 points, X(n) is X(4) [ Generate a Warning Only When Business Rule#2 Fails] | R | Numeric | B,DVB | Lin Xu/ WeiHui | N | Y
CC | Mw4 | Reactive Capability - CC | MW | CCUNIT | MW4_GEN | 1. MW4> 0 2.MW4<MW5 3. X(n) > = WMX (Unit Max output) where n is the last MW value in the curve. If the curve has 4 points, X(n) is X(4) [ Generate a Warning Only When Business Rule#2 Fails] | R | Numeric | B,DVB | Lin Xu/WeiHui | N | Y