## Slide 1
Ancillary Service Methodology Preliminary Quantities For 2018
ERCOT Staff
Sep 15, 2017

## Slide 2: Schedule for Stakeholder Discussion
Sep 15, 2017 – QMWG (w Current Methodology)
Oct 2, 2017 – QMWG (w Proposed Changes)
Oct 11, 2017 – PDCWG
Oct 20, 2017 – OWG
Nov 01, 2017 – WMS
Nov 02, 2017 – ROS
Nov 30, 2017 – TAC
Dec 12, 2017 – BOD

## Slide 3: Scope of Discussion
The Ancillary Service (A/S) quantities for 2018 contained in this presentation are based on the same methodology that was approved in December 2016.
  These quantities for 2018 reflect moving forward the historic data on which quantities are based, unless otherwise noted.
  Spreadsheets that contain the associated quantities for January through August of 2018 have been posted on the meeting page for September 15 QMWG meeting.
ERCOT is seeking feedback, based on this analysis, for changes to the 2018 AS Methodology.

## Slide 4
Divider Slide
Divider Slide (optional)
Regulation Service

## Slide 5: Regulation Service Methodology – 2018
The preliminary Regulation quantities for January 2018 thru August 2018 in subsequent slides have been computed using current methodology (2016 and 2017 five-minute net load variability) and updated GE tables.
GE Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed Wind capacity.
  This table has been updated for 2018.

## Slide 6: GE Table - 2018

## Slide 7: Regulation Up Jan-18

## Slide 8: Regulation Up Feb-18
*.

## Slide 9: Regulation Up Mar-18
*.

## Slide 10: Regulation Up Apr-18
*.

## Slide 11: Regulation Up May-18
*.

## Slide 12: Regulation Up Jun-18
*.

## Slide 13: Regulation Up Jul-18

## Slide 14: Regulation Up Aug-18

## Slide 15: Regulation Down Jan-18

## Slide 16: Regulation Down Feb-18
*.

## Slide 17: Regulation Down Mar-18

## Slide 18: Regulation Down Apr-18
*.

## Slide 19: Regulation Down May-18
*.

## Slide 20: Regulation Down Jun-18
*.

## Slide 21: Regulation Down Jul-18

## Slide 22: Regulation Down Aug-18

## Slide 23: Hourly Avg. Regulation Comparison

## Slide 24
Divider Slide
Divider Slide (optional)
Responsive Reserve Service

## Slide 25: Responsive Service Methodology (RRS) - 2018
The preliminary RRS quantities for January 2018 thru August 2018 in subsequent slides have been computed using current methodology (2016 and 2017 system inertia conditions) and updated RRS table.
The RRS table tracks RRS requirements for different inertia conditions.
  This table has been updated to make the increments in inertia levels uniform across all study scenarios.

## Slide 26: RRS Table - 2018
 | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8 | Scenario 9 | Scenario 10 | Scenario 11 | Scenario 12
LR/PFR | 2.25:1 | 2.11:1 | 1.99:1 | 1.87:1 | 1.77:1 | 1.69:1 | 1.61:1 | 1.54:1 | 1.47:1 | 1.41:1 | 1.36:1 | 1.3:1
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240
PFR Req. (no LR) (MW) | 5246 | 4916 | 4620 | 4361 | 4132 | 3927 | 3743 | 3576 | 3424 | 3285 | 3157 | 3040
*RRS (MW) | 3229 | 3162 | 3090 | 3039 | 2984 | 2920 | 2868 | 2815 | 2772 | 2726 | 2676 | 2643
 | Scenario 13 | Scenario 14 | Scenario 15 | Scenario 16 | Scenario 17 | Scenario 18 | Scenario 19 | Scenario 20 | Scenario 21 | Scenario 22 | Scenario 23 | Scenario 24 | Scenario 25
LR/PFR | 1.26:1 | 1.22:1 | 1.17:1 | 1.14:1 | 1.1:1 | 1.07:1 | 1.04:1 | 1.01:1 | 1.00:1 | 1.00:1 | 1.00:1 | 1.00:1 | 1.00:1
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370
PFR Req. (no LR) (MW) | 2932 | 2831 | 2737 | 2650 | 2569 | 2492 | 2421 | 2353 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS (MW) | 2594 | 2550 | 2523 | 2477 | 2446 | 2408 | 2373 | 2342 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS quantity is calculated with limit of 50% limit on LRs.
**Red font in table above identifies study scenario where RRS needed < 2300 MW. 2300 MW floor will be used in RRS requirement determination.
***Generation mix (CCs, Gas, SC, Coal, Steam) providing 1150 MW of PFR has been aligned with actual historic system operations.
Inertia < 250 GW·s: 30% Coal + 70% Rest. Inertia ≥ 250 GW·s: 15% Coal + 85% Rest

## Slide 27: RRS Jan 2018
*2300 MW Floor across all hours.

## Slide 28: RRS Feb 2018
*.

## Slide 29: RRS Mar 2018

## Slide 30: RRS Apr 2018
*.

## Slide 31: RRS May 2018
*.

## Slide 32: RRS Jun 2018
*.

## Slide 33: RRS Jul 2018

## Slide 34: RRS Aug 2018

## Slide 35: Hourly Avg. RRS Comparison

## Slide 36
Divider Slide
Divider Slide (optional)
Non Spinning Reserve

## Slide 37: Non Spinning Reserve Methodology (NSRS) - 2018
ERCOT is contemplating two changes to Non Spin Service Methodology for 2018.
  Include solar generation and solar forecast in the calculations for Net Load and Net Load Forecast i.e. include effects of solar in Net Load Forecast error calculation.

## Slide 38: Wind Installation Capacity
*The projected wind installation capacity (based on IA Signed with Financial Security) is from July 2017 Generator Interconnection Status Report posted here.

## Slide 39: Wind Installation Capacity
*The projected wind installation capacity (based on IA Signed with Financial Security) is from July 2017 Generator Interconnection Status Report posted here.

## Slide 40: Growth in Installed Wind Capacity
Growth in Installed Wind Capacity in Jan 2018 = Projected Wind Capacity in Jan 2018 – Installed Wind Capacity in Jan 2017
*The projected wind installation capacity (based on IA Signed with Financial Security) is from July 2017 Generator Interconnection Status Report posted here.

## Slide 41: 3-HA Wind Over-Forecast Error
Over time an increasing trend is visible in the 3-HA Wind Over-Forecast Error.
2013
2014
2015
2016
2017

## Slide 42: Non Spinning Reserve Methodology (NSRS) - 2018
ERCOT is contemplating two changes to Non Spin Service Methodology for 2018.
  Include solar generation and solar forecast in the calculations for Net Load and Net Load Forecast i.e. include effects of solar in Net Load Forecast error calculation.
  Include an adjustment to account for additional over-forecast uncertainty from projected increase in installed wind capacity in 2018.
The subsequent slides depict a preliminary assessment of Non Spin quantities for January 2018 thru August 2018 using the above changes to the current methodology (2015, 2016 and 2017 Net Load Forecast Error and risk of Net Load Ramp).

## Slide 43: Estimated Increase in Wind Over-Forecast Error - 2018
An increase in wind over forecast error per 1000 MW increase in installed Wind capacity has been estimated using error in forecasting wind forecast in the last five years.
Average hourly increase in Wind Forecast error per 1000 MW increase in installed Wind capacity = 45 MW

## Slide 44: Estimated Increase in Wind Over-Forecast Error based Wind Growth
Using projected installed wind capacity, compute adjustment to Non-Spin requirement.
Average hourly adjustment to Non Spin Requirement = 121 MW

## Slide 45: NSRS Jan 2018
*1375 MW Floor in On-peak hours (HE 7 thru 22)

## Slide 46: NSRS Feb 2018

## Slide 47: NSRS Mar 2018

## Slide 48: NSRS Apr 2018

## Slide 49: NSRS May 2018

## Slide 50: NSRS Jun 2018

## Slide 51: NSRS Jul 2018

## Slide 52: NSRS Aug 2018

## Slide 53: Hourly Avg. NSRS Comparison

## Slide 54
Divider Slide
Divider Slide (optional)
Discussion