## Slide 1
Review of UFLS Draft NOGRR from UFLS Workshops
Matt Mereness
Director of Compliance
Sept 21, 2017

## Slide 2: UFLS Discussion outline
Recap of key issues to date on clarifying ERCOT UFLS Program
Review action items from Aug 17 OWG
  Is there any risk of overarming and overshooting on UFLS?
  Has ERCOT studied the impacts of ERS deployments?
  Can ERCOT provide more ERS data for improved transparency?
Review current draft NOGRR
Appendix
  NERC requirement excerpt
  UFLS examples
  Potential Load Resource data to provide

## Slide 3: Recap- Summary of UFLS workshops
Key discussions to date
  Recognize there are at least two scenarios of UFLS being activated
    Sudden event: normal day but then significant loss of generation (starting point of 60Hz and no LR deployed)
    Slow-burn event: system is in emergency operations (EEA2), LR deployed, and then loss of generation
    Conclusion that in both cases, need for 25% of armed UFLS to arrest frequency
  ERCOT view that as frequency drops from 60 to 59.7 to 59.3, that the measurement of 25% response is tied to what the Load was when crossing 59.3 and initiating UFLS levels.
  Agreement that annual Compliance survey measurement should align as closely as possible with expected Operations compliance (post event reports and analysis).
  ERCOT was requested to create initial NOGRR draft reflecting expectations
  ERCOT was requested to provide inventory of LRs in DSP footprint
    ERCOT noted this is in network model but can also be provided
  ERCOT asked about providing historical trends/deployments
    ERCOT offered to provide annually if market can agree how to summarize (min, max, avg, annual, etc)
  ERCOT asked about providing Load Resource telemetry to TO/DSPs
  Is DSP or TO the appropriate role/definition for compliance in the NOGRR?

## Slide 4: Action Items from Aug 17 OWG
Is there any risk of overarming and overshooting on UFLS?
  ERCOT does perform planning studies that include dynamic simulations using DWG model that includes equipped UFLS circuits and Load Resources.
  The dynamic study is performed on different models, including High Wind, Low-Load and to date ERCOT has not observed any over-shoot issues related to this study.
  Current ERCOT surveys do reflect a certain amount of overshoot at the different levels (2-3%), and with the current proposed changes allowing movement across tiers, the overshoot may be reduced overall.
Has ERCOT studied the impacts of ERS deployments?
  ERCOT has not studied ERS deployments in current dynamic models
    Current ERS procurement is approximately 800MW
    When compared to the current excess 2-3% UFLS capacity at each tier this is not a significant number
      For 30,000MW load, 600-900MW per tier represent the 2-3% at each tier

## Slide 5: Action Items from Aug 17 OWG
Can ERCOT provide more ERS data for improved transparency?
  Current Data Set
  The following information is sent to either the TDSPs or the NOIEs following the procurement of the June-Sept Standard Contract Term only. The sites are those participating in ERS Time Periods 3 & 4 (1 to 6 pm). ERCOT does not provide an estimate of the Demand Response obligation from each site since many ERS Resources consist of aggregations of 2 or more sites.
  To TDSP’s in competitive areas
  • QSE Representing ERS Resource
  • ERS Resource Type
  Load
  Gen
  Weather-Sensitive
  • ESI-IDs
  To NOIEs
  • QSE Representing ERS Resource
  • ERS Resource Type
  Load
  Gen
  Weather-Sensitive
  • Site Name
  • Address (street, City, Zip code)

## Slide 6: Action Items from Aug 17 OWG
Can ERCOT provide more ERS data for improved transparency?
Proposed data set
  To NOIEs
  • Report by each ERS Time Period
  • ERS Resource Type
  Load
  Gen
  • Disaggregate Resource Obligation by zip code (stations not known in NOIE territories)
  For ERS Loads disaggregation will spread obligation equally among all sites in the Resource
  For ERS Gen disaggregation will be based on name plate rating
  Limit report to zipcodes exceeding a preset minimum (tbd with input by TDSP)
  To TDSP’s in competitive areas
  • Report by each ERS Time Period
  • ERS Resource Type
  Load
  Gen
  • Disaggregate Resource Obligation by Substation (or zip code if preferred)
  For ERS Loads disaggregation will spread obligation equally among all sites in the Resource
  For ERS Gen disaggregation will be based on name plate rating
  Limit report to substations exceeding a preset minimum (tbd with input by TDSP)

## Slide 7: Review current NOGRR version
Summary of changes
  Purposeful in separating (1) and (2) between actual event and survey
    In actual event, compliance with system Load measured at 59.3 Hz (2.6.1(1)).
    In annual survey, compliance with system Load at survey time (2.6.1(2)).
  ERCOT agreeable to allowing totals to roll into next tier
    Moved STEC’s language on deployment amounts into survey section (2).
    Inserted ability for ERCOT to request redistribution if any reliability issues identified in survey
  NOGRR adds ERCOT requirement to annually provide registered Load Resources and capacity in TO/DSP footprint
  Question of proper alignment of DSP and TO responsibilities
  Does not currently include 2 concepts discussed in workshops
      Provision of trends of Load Resource status in TO/DSP footprint (eg, min, max, avg responsibility) – could be added with no project impacts to add
      Provision of telemetry of LR status to TO/DSP – project impacts

## Slide 8
APPENDIX:
2016 and 2017 UFLS Survey results
NERC requirement excerpt
Potential Load Resource data to provide

## Slide 9: Appendix- 2016 & 2017 UFLS Survey Results
ERCOT Compliance coordinates and conducts an annual survey with the TSPs and DSPs to ensure that the required automatic under-frequency load shed circuits are configured to provide the appropriate load relief in an under-frequency event as required by table below from Operating Guides 2.6.1(1) Requirements for Under-Frequency Load Shedding:
2016 results were 7.2% / 12.2% / 12.6% for total of 31.9%
2017 results were 7.8% / 13.2% / 13.2% for total of 34.1%

## Slide 10: Appendix- NERC Requirement
NERC standard PRC-006-2 — Automatic Underfrequency Load Shedding:
Requirement 3. Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s).
Requirement 9. Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. [VRF: High][Time Horizon: Long-term Planning]
Measurement 9. Each UFLS Entity shall have dated evidence such as spreadsheets summarizing feeder load armed with UFLS relays, spreadsheets with UFLS relay settings, or other dated documentation that it provided automatic tripping of load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, per Requirement R9.

## Slide 11: Appendix- Potential Load Resource data to be provided
TDSP shown on Registration Form
  TDSP Duns
From the Load Resource Asset Registration Form
  Dispatch Asset Code
  ESIID (Load Resources for NOIEs will have a non-settlement ESIID)
  Station the Load Resource is mapped to in the Network Operations Model
  PTI Number
  Transmission Transformer Load Name
  Maximum Registered Interruptible Load
Historical Data (more analysis needed)
  Average hourly RRS Responsibility for LR during a predefined date range
  Maximum RRS Responsibility during the same time period