ERCOT Nodal Operating Guides

Section 8

Attachment A

Detailed Black Start Information

October 7, 2011

- This attachment and Section 8, Attachment E, Black Start Plan Template, provide the minimum information necessary to be used in conjunction with the ERCOT Black Start Plan.  Each Transmission Operator (TO), Qualified Scheduling Entity (QSE) representing Black Start Resources, and Black Start Generation Resource should use this information for technical reference, development of Black Start plans, and training of personnel.

# CONSIDERATIONS FOR SYSTEM RESTORATION

## Determining System Status

- (1)	If a Generation Resource or Transmission Operator (TO) loses voltage on all busses and incoming transmission lines, then operators should assume there is a Partial Blackout or Blackout.  If possible, the TO shall also immediately notify ERCOT.  Contracted Black Start Resources shall implement Black Start procedures and establish contact with their TOs.  Other Generation Resources shall contact their QSEs and then wait for instructions from the TOs.  If possible, ERCOT will update TOs and QSEs concerning the status of the ERCOT System by use of the ERCOT Hotline or other available backup communications.

(2)	It is expected that if communication with ERCOT is not possible, TOs will evaluate system conditions and proceed independently with their Black Start plans.

(3)	Priority should be given to determining the status of nuclear Generation Resources and switchyards in order to re-establish offsite power supply.

(4)	System status conditions to be surveyed include but are not limited to:

(a)	Areas of the system that are de-energized;

(b)	Areas of the system that are functioning;

(c)	Amount of generating reserve available in functioning areas;

(d)	Generation Resource availability and time required to restart;

(e)	Status of transmission breakers and sectionalizing equipment along Cranking Paths and Synchronization Corridors, and at Generation Resources;

(f)	Status of transmission breakers and sectionalizing equipment at Direct Current Ties (DC Ties);

(g)	Status of fuel supply from external suppliers;

(h)	Under-frequency relay operation; and

(i)	Relay flags associated with circuits tripped by protective relays.

## Verifying Communications

- (1)	Reliable communications will be the key to a safe and timely restoration following a Partial Blackout or Blackout.  As part of the initial assessment after a Partial Blackout or Blackout, communication facilities shall be tested and verified.  It is possible, especially in case of a Blackout, that communications with out-of-state QSEs representing Generation Resources may not be possible.  It is therefore critical that TOs and Generation Resources located within their transmission system be able to communicate directly during these times.

- (a)	The ERCOT System Operators shall:

(i)	Verify or establish communication paths with TOs;

(ii)	Verify or establish communications paths with QSEs representing Generation Resources;

(iii)	Verify integrity of ERCOT Hotline;

(iv)	Periodically disseminate information to TOs and QSEs; and

(v)	Direct implementation of Black Start plan in areas of a Partial Blackout or Blackout.

- (b)	The TO operators shall:

(i)	Contact ERCOT in order to report status;

(ii)	Establish contact with contracted Black Start Resources and their QSE(s);

(iii)	Initiate Black Start plan; and

(iv)	Establish communication paths with other Generation Resources necessary to the restoration of the ERCOT System.

(c)	The QSE representing Generation Resources shall:

- (i)	Contact ERCOT to report status of Generation Resources within the ERCOT Region;

- (ii)	Assist TOs as required; and

- (iii)	Ensure Generation Resources are prepared to receive and follow instructions directly from the TO to which they are connected.

- (d)	The Black Start Resources shall:

- (i)	Isolate their Black Start Resource from the ERCOT Transmission Grid;

- (ii)	Establish communications with their TOs;

- (iii)	If no communications with the TOs are available, establish communications with ERCOT; and

- (iv)	Start Black Start Resource and request load interconnection from TO.  The Black Start Resource shall not connect to the ERCOT Transmission Grid without specific instructions to do so from either ERCOT or the designated TO responsible for the Black Start Resource.

- (2)	Should problems be encountered with any of the primary communication facilities, back-up facilities shall be deployed and appropriate personnel notified.

- (3)	Communications will be vital to an orderly recovery.  To keep communication facilities available, operating personnel shall ensure that three-part communication is used at all times.

## Preparing for System Restoration

(1)	Orderly restoration will usually require sectionalizing the de-energized parts of the ERCOT System into smaller, manageable blocks before they are energized.

(2)	The sectionalizing process should usually address but is not limited to the following objectives:

(a)	Priority shall be given to restoring offsite power to nuclear Generation Resources;

(b)	Ensure that blocks of load to be energized are sized to minimize the problems of cold load pickup; and

(c)	Operators shall verify that their switching orders as well as any standing emergency switching orders have been completed.

## Bringing Up Generation Resources

(1)	First priority shall be given to preventing damage to Generation Resource equipment and to restoring offsite power to nuclear Generation Resources.  Secondly, attention shall be given to preparing generators that can come On-Line most rapidly.  All operators should remember that large steam Generation Resources will need an outlet for the minimum generation requirement soon after coming On-Line.

(2)	A Black Start Resource has procedures to begin the process of bringing its generators back up when the switchyard and all incoming transmission lines are de-energized.  The Generation Resource shall not synchronize or pick up load without communicating with the TO to which it is connected.

(3)	A Generation Resource without Black Start capability shall have a written procedure in place to begin preparing the Generation Resource to be energized from an external line.  When the TO has energized the Generation Resource switchyard it will contact the Generation Resource directly and the QSE as soon as practical.  The TO will coordinate starting of large motors, bringing Generation Resources On-Line, and synchronizing Generation Resources with the rest of the  ERCOT Transmission Grid.

(4)	Generation Resource operators will be controlling system frequency during the recovery period and must keep it between trip points for generators’ under-frequency and over-frequency relays.  It is preferable to use the generators with lowest under-speed trip for initial restoration.

(5)	Automatic Voltage Regulators (AVRs) should be placed in service as soon as practical after bringing Generators On-Line and should remain in-service to improve machine stability.

(6)	As soon as possible, after bringing a Generator On-Line, automatic Governor controls should be placed in the "automatic" position to ensure instantaneous Governor response to changes in frequency.

## Picking Up Lines

(1)	Ties between nearby Generation Resources shall be established as soon as possible.  Priority shall be given to restoring at least one circuit to nuclear Generation Resources to provide offsite power for safe shutdown.

(2)	A line should be energized from the strongest electrical source.  Switching devices on all substation or transmission capacitor banks along the line should be open unless needed for voltage control.

(3)	Energizing transmission auto-transformers (345/138 kV, 138/69 kV) and shunt reactors at Generation Resource will allow plant operators to increase field current on the generator to increase stability.  Also, this reactive current will help keep transmission voltages from becoming excessive.

(4)	Caution should be exercised in the use of 345 kV transmission system.  Because of high values of line charging, energizing one of these circuits with little or no load can produce excessive voltage and can damage substation equipment  (Note: 345kV lines supply approximately 1 MVAr/mile of line charging while 138kV lines supply approximately 0.1 MVAr/mile).

(5)	Operators in TO control rooms should exercise care when energizing transmission lines, so that they do not close a breaker into a fault.  Operators in TO control rooms should be aware of any transmission lines that tripped while the system was going down and have field personnel check the relay flags before energizing the line.

(6)	Ferroresonance may occur while energizing a line or while picking up a transformer from an unloaded line.  Operators in TO control rooms should be on guard for unusually high and sustained voltages during such switching.  345 kV lines may be highly susceptible to this phenomenon and their use should be minimized in the early stages of restoration.

(7)	Impedance relays that do not have out of step blocking may trip lines due to power swings during restoration (a good indication that the line tripped due to excessive power swings rather than a fault is the existence of impedance relay flags and no ground flags).

## Picking Up Load

(1)	In general, 69 kV and 138 kV lines along with radial 345 kV lines to autotransformers may be used to energize load.  When energizing a 345 kV circuit and autotransformer combination, both the line and transformer should be energized at the same time to avoid the problem of excessive voltage.  The more lightly loaded a generator is, the less load increment it can safely pick up.

(2)	Cold load pick up can involve inrush currents of ten or more times than the normal load current depending on the nature of the load being picked up.  This will generally decay to about two times the normal load current in two to four seconds and remain at a level of 150% to 200% of pre-shutdown levels for as long as 30 minutes.

(3)	Priority shall be given to restoring offsite power to nuclear Generation Resources.  As critical and priority loads are restored, consideration should be given to restoration of loads controlled by under-frequency relays.

(4)	When energizing load, the operators in TO control rooms must be in close contact with the Generation Resource in order that excessive load is not picked up on a generator in one operation.  Generally, the operators in TO control rooms should pick up no more than 5% of the total generating capability in an Island in a single step.  If load is picked up in blocks that are too large, then the inrush current may operate over current relays that trip the loads off the ERCOT System again.  There should be sufficient time between switching operations to allow the generator to recover from the sudden increase in load.

(5)	The operators in TO control rooms should exercise caution when loading a single generator to more than 50% of its control range until additional generators have been brought back On-Line in that Island. Generally, no generator should be loaded to more than 80% of its available capability until ERCOT System conditions return to normal.

(6)	Since each Generation Resource may be operating independently, Generation Resource operators will have to monitor and adjust their generators voltage and frequency.  Frequency should be kept above 59.8 Hz and as close as possible to 60 Hz.  Voltage should be kept as close as possible to normal schedules.  As more generators are brought up and more load is added, the voltage and frequency will tend to stabilize.

(7)	Residential and commercial load will most likely be easier to pick up and maintain than industrial loads.  This is due to the large fluctuation possible with industrial loads.

(8)	The operators in TO control rooms should exercise caution when re-energizing capacitor banks after load has been picked up.  The change in system voltage that occurs will be much larger than normal because of the reduced system fault duty.

## Synchronizing Between Islands

(1)	TOs shall have field personnel in area Islands to check breakers at each end of a line being used to synchronize between Islands to ensure they are open regardless of supervisory indication.  The area with the largest amount of generation On-Line shall energize the line first.

(2)	Where available, field personnel shall synchronize and close the tie breakers at the synchronization point.  If there is a sufficient frequency difference that the Islands cannot be synchronized, the Island with the least generation On-Line shall adjust its frequency to achieve synchronization.

(3)	When synchronizing, both the phase angle across the breaker, and the voltage on each side of the breaker shall be measured.  If possible, the phase rotation should be stopped and the phase angle reduced to 10° or less before closing the breakers.

(4)	In general, lines should not be loaded to more than 50% of thermal rating until multiple tie paths have been established.  Additional ties should be closed as soon as possible.

# ERCOT Coordination

(1)	During the initial stages of the restoration ERCOT will coordinate the Black Start restoration effort by monitoring the implementation of each TO’s Black Start plan, providing ERCOT System status information, and facilitating communication between the Market Participants.  ERCOT will also monitor the changes in Resource conditions, restoration of transmission lines, and any load that is re-energized.  The ERCOT Hotline or available backup communications will periodically be used to communicate simultaneously with the Market Participants on a periodic basis assuming communication is possible.

- (2)	System status conditions that should be surveyed include, but are not limited to:

- (a)	Communication facilities;

- (b)	Transmission system;

- (c)	Generating system;

- (d)	Fuel supplies; and

- (e)	Any other significant conditions which might affect restoration.

- (3)	ERCOT System Operators should be sure that each TO is successfully implementing their Black Start plan and each Generation Resource is successfully implementing their written procedures for preparing their Generation Resources to be energized during Black Start restoration.  ERCOT System Operators will direct mutual assistance by utilizing the Black Start map and contacting the Market Participants most able to provide the assistance.

- (4)	Before synchronization of intercompany Islands ERCOT will designate the entity responsible for frequency control in the combined Islands.  Initially this may be a single Generation Resource.  As the restoration effort progresses, ERCOT will work to combine Islands in such a way as to restore frequency control of one of the QSEs representing Generation Resources.  As Inter-company Islands are synchronized ERCOT will approve the addition of generation and load to the ERCOT System.  No additions shall be made without that approval.

# Considerations for Black Start Testing

(1)	ERCOT shall maintain a record of contracted Black Start Resources and update such records on an annual basis.  The record shall include the name, location, MW capability, type of unit, date of test, and starting method of each Black Start Resource per the North American Electric Reliability Corporation (NERC) Reliability Standards.

(2)	The owner or operator of each Black Start Resource shall demonstrate through the testing procedures outlined in Protocol Section 8.1.1.2.1.5, System Black Start Capability Qualification and Testing, that the Black Start Resource can perform its intended functions as required in the ERCOT Black Start Plan.  ERCOT may also order random simulation or testing of Black Start capabilities.  Documentation of the analysis shall be provided to NERC or the Texas Reliability Entity (Texas RE) upon request as required by the NERC Reliability Standards.

# Criteria for ERCOT and Transmission Operator Black Start Plans

(1)	ERCOT will maintain a Black Start Plan that is consistent with this Operating Guide.  The ERCOT Black Start Plan shall be provided to the QSEs representing Black Start Resources and TOs.

(2)	ERCOT System Operators shall review these documents on a regular basis.  It is suggested that all Black Start plans include at a minimum the following elements:

- (a)	Strategies and guidelines for restoration of the ERCOT System;

- (b)	Identification of the relationships and responsibilities of the QSEs representing Black Start Resources and TO personnel necessary for the restoration;

- (c)	Identification of Black Start Resources including:

- (i)	Generation Resources;

- (ii)	Transmission Facilities;

- (iii)	Communication resources; and

- (iv)	Fuel resources.

- (d)	Mutual assistance arrangements;

- (e)	Contingency plans for failed Generation Resources;

- (f)	Identification of critical load requirements;

- (g)	Identification of special equipment requirements;

- (h)	General instructions and guidelines for ERCOT System Operators, Resource Entities, QSEs representing Generation Resources, and TO operators and their respective communications personnel;

- (i)	Procedures for Notification; and

- (j)	Procedures for return to Market Operations.

(3)	TO’s Black Start plans shall include sections on the Black Start Purpose, Scope, Roles and Responsibilities, Strategies, Priorities, Operations, Communication, and Contingency plans and shall follow the format outlined in Appendix 8E.