## Slide 1
WETT Bearkat Area Transmission Improvements project-ERCOT Independent Review Scope
October 19, 2017

## Slide 2: Overview
Wind Energy Transmission Texas (WETT) submitted Bearkat Area Transmission Improvements project for Regional Planning Group review. This is a Tier 1 project that is estimated to cost $ 69.87 million.
  Proposed for 2021
  Address generator interconnection issues in Bearkat Area
  Reliability Issues
    Voltage Instability
    Thermal Overloads
  Provide exit strategy for WETT proposed Remedial Action Scheme (RAS)
  Improve generator get-a-way capacity at Bearkat
  Economic Benefit

## Slide 3: Overview

## Slide 4: BearKat Area Generators
Project Name | Projected COD | Capacity | Signed Interconnect Agreement | Planning Guide Section 6.9
RATTLESNAKE DEN WIND PHASE 1 G1 | In-Service | 104 | Yes | Yes
RATTLESNAKE DEN WIND PHASE 1 G2 | In-Service | 103 | Yes | Yes
NBOHR(BearKat Wind A) | 12/29/2017 | 197 | Yes | Yes
Edmondson Ranch Wind | 05/07/2018 | 293 | No | No
Kontiki Wind | 04/01/2019 | 500 | No | No
BearKat Wind B | 04/15/2019 | 163 | Yes | Yes

## Slide 5: Study Assumptions
Dynamic Study Case
  Constructed from latest DWG 2020 HWLL Flat Start case finalized March 2017
  Study Region will consist of Far-West and West Weather Zones
  Generator additions that meet Planning Guide Section 6.9 criteria in study region at time of study will be added to the case.
  Transmission Projects expected to be in-service within the study region by 2022 at the time of the study will be added to the case
  Criteria: NERC TPL and ERCOT Planning Guides

## Slide 6: Study Assumptions
Production Cost Study Case
  Constructed from 17 RTP 2023 Production Cost Model
  Study Region will consist of Far-West and West Weather Zones
  Generator additions that meet Planning Guide Section 6.9 criteria in study region at time of study will be added to the case.
  Transmission Projects expected to be in-service within the study region by 2022 at the time of the study will be added to the case

## Slide 7: Study Procedure
Scenarios to be evaluated:
  Study Cases
  Sensitivities based on PG Section 3.1.3(4):
    Generator additions with Signed Generation Interconnection Agreements (SGIA) but that DO NOT meet Planning Guide Section 6.9 criteria in study region at time of study will be added to the case
  Economic Assessment of Alternatives

## Slide 8: Deliverables
  Tentative Timeline
    Final EIR update to RPG – December 2017
    EIR recommendation to TAC – January/February 2018
    BOD Endorsement – February 2018

## Slide 9
?
Stakeholder Comments Also Welcomed to Prabhu Gnanam:
ggnanam@ercot.com