## Slide 1
NPRR 776 NDSWG
Stephen Solis
System Operations Improvement Manager
Mark Lucas
IT Project Manager
ERCOT Public
October 17, 2017

## Slide 2: NPRR776 - Voltage Set Points Project Scope
NPRR 776 implements requirements for transparency of both the actual measured value and desired Set Point for the Point of Interconnection (POI) voltage between all affected entities (TO, ERCOT, QSE, and RE).
ERCOT is working to leverage existing telecomm-unications infrastructure (e.g. ICCP) to minimize additional expenses.
Changes include, NMMS schema changes to allow set points to be entered by TSPs, validation logic of the target values, monitoring of targets and actuals in operator displays, automated push to QSEs via ICCP over the WAN.

## Slide 3: NPRR776 - Voltage Set Points Project Update
ERCOT will be implementing Voltage Set Point targets from the TSPs and logic to direct the appropriate targets to its QSE in Release 1 in February of 2018.
  ICCP points will be available to QSEs about 2 to 3 weeks after Release 1.
Development activities are in-progress for NMMS network model database updates, control room operator displays, validation logic, and ICCP communications.
ICCP handbook changes are in review.
Core system modifications are in process of testing.

## Slide 4: Voltage Set Points - Business Requirements
TSPs will be associating the two ICCP points (Set Point and actual) and generator relationships to the POI kV Measurement device (e.g. on busbar, line, transformer).
ERCOT will be using these relationships in its EMS to map and make available the ICCP points to the appropriate QSE.
QSEs are required to send the two ICCP points (Set Point/Target and Actual POI kV) to the appropriate Generation Resource.
Naming convention should remain for kV measurements, set points/targets will change to a _KVT suffix instead of _KV
ERCOT will update the ICCP Handbook to reflect naming convention for defined points for QSE and TSP.

## Slide 5: Discussion / Q&A