| NPRR Number | 835 | NPRR Title | Removing the Capacity Limits from Resources Providing Fast Responding Regulation Service (FRRS) |
| --- | --- | --- | --- |
| Date |  | July 11, 2017 |  |
| Submitter’s Information |  |  |  |
| Name |  | Sandip Sharma |  |
| E-mail Address |  | Sandip.Sharma@ercot.com |  |
| Company |  | ERCOT |  |
| Phone Number |  | 512-248-4298 |  |
| Cell Number |  | 817-371-7773 |  |
| Market Segment |  | Not applicable |  |

Comments

Nodal Protocol Revision Request (NPRR) 835 proposes the removal of the 65 MW limit on Fast Responding Regulation Up Service (FRRS-Up) and 35 MW limit on Fast Responding Regulation Down Service (FRRS-Down) services.  FRRS-Up and FRRS-Down are subsets of Regulation Up Service (Reg-Up) and Regulation Down Service (Reg-Down), respectively.  ERCOT does not support the removal of all MW limits on the quantity of Reg-Up and Reg-Down that can be provided by Resources providing Fast Responding Regulation Service (FRRS).  ERCOT believes the existing limits of 65 MW on FRRS-Up and 35 MW on FRRS-Down are appropriate and necessary at this time, and that limits will also be needed in the future.  The MW limit ensures that not all Regulation Service is be provided by Resources providing FRRS because ERCOT needs a portion of regulation to be provided by generators that are following continuous Automatic Generation Control (AGC) instructions, which are designed to correct ERCOT’s Area Control Error (ACE).  Generators that are following continuous AGC instructions can remain deployed for longer durations, contrary to the Resources providing FRRS, which are following a different type of signal.

However, ERCOT believes the language changes in the NPRR are acceptable due to presence of other existing language in paragraph (2) and (3) of Section 3.16, Standards for Determining Ancillary Service Quantities, which directs ERCOT to determine the maximum amounts of FRRS-Up and FRRS-Down as part of the annual review and stakeholder approval of the Other Binding Document “ERCOT Methodologies for Determining Minimum Ancillary Service Requirements”.  In the event stakeholders approve NPRR835, ERCOT proposes that the 65 MW limit on FRRS-Up and 35 MW limit on FRRS-Down be captured in the “ERCOT Methodologies for Determining Minimum Ancillary Service Requirements”.

Removing the explicit numerical limits from the Protocols allows for the review and approval of FRRS limits during the annual review of the Ancillary Service methodology without also requiring an NPRR to implement any changes.

Revised Cover Page Language

| NPRR Number | 835 | NPRR Title | Removing the Explicit Numerical Capacity Limits from Resources Providing Fast Responding Regulation Service (FRRS) from the Protocols |
| --- | --- | --- | --- |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) removes the explicit numerical MW capacity limits of Resources providing Fast Responding Regulation Service Up (FRRS-Up) and Fast Responding Regulation Service Down (FRRS-Down) from the Protocols. FRRS limits will continue to exist and are determined and specified as part of the annual review and approval of the “ERCOT Methodologies for Determining Minimum Ancillary Service Requirements.” |  |
| Business Case |  | Removing these limits from Protocols will allow ERCOT to evaluate potential changes to the FRRS limits during the annual review and approval of the Ancillary Service methodology without requiring an NPRR. ERCOT still has the discretion to reduce the FRRS limits when it believes that it will have a negative impact on reliability or if the available capacity would require additional Regulation Service to be deployed. |  |

Revised Proposed Protocol Language

None at this time.