## Slide 1
PDCWG Report to ROS
Chair: Percy Galliguez, Brazos Electric Power Cooperative, Inc.
Vice Chair: Lei Ye, Austin Energy
ROS
November 2nd, 2017

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-1 FMEs & IMFR
    3 FMEs in the month of September
    One FME activated hydro generation resource RRS providers.
    IMFR=1022.32MW/0.1Hz(2.683 times the required IMFR, 381MW/0.1Hz)
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 9/13/17
  Southern Cross DC Tie Transmission Project(ERCOT and Pattern Development Presentations)
  AS Methodology for 2018(ERCOT)
  Regulation & Frequency Control Reports
  MOD-026-1 Discussion(Close to submission)
    NOGRR Proposal/Review Status
  BAL-001-TRE-001 Discussion
    Combined Cycle Steam Governor Deadband R6.2
    Power Augmentation for Chillers

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There was 3 FMEs in September
  9/1/2017 16:56:08
    Loss of 456 MW
    Interconnection Frequency Response: 1014 MW/0.1Hz
    8 of 39(2 of 31 RRS Providers) Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    5 of 39(1 of 31 RRS Providers) Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  9/1/2017 21:41:48
    Loss of 1204 MW(Nadir=59.762Hz)
    Interconnection Frequency Response: 1433 MW/0.1Hz
    6 of 45(1 of 21 RRS Providers) Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    4 of 45(0 of 21 RRS Providers) Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Frequency Measurable Events
  9/15/2017 17:50:47
    Loss of 812 MW
    Interconnection Frequency Response: 855 MW/0.1Hz
    8 of 47(0 of 17 RRS Providers) Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    5 of 47(0 of 17 RRS Providers) Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 7: Interconnection Minimum Frequency Response (IMFR) Performance
IMFR Performance currently 1022.32 MW/0.1Hz

## Slide 8: Frequency Control Report
September 2017

## Slide 9: CPS1 Performance

## Slide 10: RMS1 Performance of ERCOT Frequency

## Slide 11: Frequency Profile Analysis

## Slide 12: Time Error Corrections
There were no Time Error Corrections (TEC) in September

## Slide 13: ERCOT Total Energy

## Slide 14: ERCOT Total Energy from Wind Generation

## Slide 15: ERCOT % Energy from Wind Generation

## Slide 16
Questions?