## Slide 1
Unannounced Capacity Testing Summary for Summer ’17
ERCOT
Operations Planning
November Xth, 2017

## Slide 2: Summer ‘17 Unannounced Unit Testing Summary
Unannounced Resource Capacity Testing Summary |  |  |  |  |  |  | 
All Tests from Summer 2017 |  |  |  |  |  |  | 
Resources Tested: | 35 |  |  |  |  |  | 
Distinct Resources Tested: | 28 |  |  |  |  |  | 
Distinct QSE's Tested: | 21 |  |  |  |  |  | 
Capacity of Resources Tested: | 16672 |  |  |  |  |  | 
Resources Passed: |  | 18 | Resources Failed: |  | 17 |  | 
Cap. of Resources Passed: |  | 9344 |  | Cap. Of Resources Failed: | 7328 |  | 
HSL Reached and Sustained: |  | 18 |  |  |  |  | 
HSL Not Reached: |  |  |  |  | 6 |  | 
HSL Not Reached and Not Sustained: |  |  |  |  | 1 |  | 
HSL Reached but Not Sustained: |  |  |  |  | 10 |  | 
Total MW Capacity Excess of Passed Resources: |  |  |  | 60 |  |  | 
Total MW Capacity Shortfall of Failed Resources: |  |  |  | 80 |  |  | 
Total MW Capacity Shortfall of All Resources: |  |  |  | 20 |  |  | 
20 MW NET shortfall of capacity.

## Slide 3: Summer ‘17 Unannounced Unit Testing Summary
Chart: Capacity Testing Results by Ambient Temperature for Summer 2017
| T <= 85 | 85 < T <= 95 | 95 > T
Pass | 0 | 10 | 8
Fail | 0 | 11 | 6
Pass Rate | 0 | 0.47619 | 0.57143
Capacity Shortfall (T > 95) | 
Excess | 28 MW
Shortfall | -31 MW
Net | -3 MW

## Slide 4: Questions?
Thank you!