## Slide 1
Proposed Ancillary Service Methodology And Quantities For 2018
ERCOT Staff

## Slide 2: Schedule for Stakeholder Discussion
Sep 15, 2017 – QMWG (w Current Methodology)
Oct 09, 2017 – QMWG (w Proposed Changes)
Oct 11, 2017 – PDCWG
Oct 20, 2017 – OWG (Meeting Canceled)
Nov 01, 2017 – WMS
Nov 02, 2017 – ROS
Nov 30, 2017 – TAC
Dec 12, 2017 – BOD

## Slide 3: Scope of Discussion
ERCOT is not recommending any changes to the methodology for determining Regulation Service & Responsive Reserve quantities for 2018.
  The quantities for 2018 Regulation Service & Responsive Reserve reflect moving forward the historic data on which quantities are based, unless otherwise noted.
  The current RRS quantities for 2018 do not reflect any potential impact of recent NSOs.
ERCOT is proposing two changes to the methodology for determining Non-Spin Reserve for 2018.
A redline version of the draft methodology and spreadsheets that contain the associated quantities for January through September of 2018 have been posted on the meeting page for November 01 WMS meeting.

## Slide 4
Divider Slide
Divider Slide (optional)
Regulation Service

## Slide 5: Regulation Service Methodology – 2018
The preliminary Regulation quantities for January 2018 thru September 2018 in subsequent slides have been computed using current methodology (2016 and 2017 five-minute net load variability) and Wind Adjustment tables.
The Wind Adjustment tables (previously called “GE Tables”) track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed Wind capacity.
  This table has been updated for 2018.

## Slide 6: Wind Adjustment Table Monthly Average Comparison
Chart: MW
| Jan. | Feb. | Mar. | Apr. | May | Jun. | Jul. | Aug. | Sep. | Oct. | Nov. | Dec.
Reg-Up Adj 2017 | 2.6971 | 2.892 | 4.4337 | 4.0364 | 5.1179 | 3.3525 | 2.5727 | 2.3761 | 2.123 | 2.2174 | 2.8291 | 2.8366
Reg-Up Adj 2018 | 2.6971 | 3.0397 | 4.2005 | 4.204 | 4.9196 | 3.4549 | 2.6092 | 2.4256 | 2.3962 | 2.0908 | 2.4298 | 2.8531
Chart: MW
| Jan. | Feb. | Mar. | Apr. | May | Jun. | Jul. | Aug. | Sep. | Oct. | Nov. | Dec.
Reg-Down Adj 2017 | 1.1933 | 3.8298 | 2.3042 | 3.241 | 3.907 | 2.2785 | 2.059 | 1.625 | 1.5858 | 2.3123 | 2.3941 | 2.9894
Reg-Down Adj 2018 | 1.1933 | 3.3331 | 2.537 | 3.2991 | 3.6411 | 2.376 | 2.022 | 1.8205 | 1.9084 | 1.7585 | 1.5839 | 1.6027

## Slide 7: Hourly Avg. Regulation Comparison
Chart: MW
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep
2018 Reg Up | 299 | 309 | 306 | 316 | 339 | 330 | 333 | 331.0417 | 326.375
2017 Reg Up | 309 | 315 | 302 | 318 | 340 | 332 | 335 | 343.125 | 332.5833
Chart: MW
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep
2018 Reg Down | 283 | 292 | 295 | 296 | 320 | 301 | 304 | 301.7083 | 308.7917
2017 Reg Down | 279 | 291 | 277 | 298 | 322 | 312 | 314 | 312.5 | 308.9583

## Slide 8
Divider Slide
Divider Slide (optional)
Responsive Reserve Service

## Slide 9: Responsive Service Methodology (RRS) - 2018
The preliminary RRS quantities for January 2018 thru September 2018 in subsequent slides have been computed using current methodology (2016 and 2017 system inertia conditions) and updated RRS table.
  The current RRS quantities for 2018 do not reflect any potential impact of recent NSOs.
The RRS table tracks RRS requirements for different inertia conditions.
  This table has been updated to make the increments in inertia levels uniform across all study scenarios.

## Slide 10: RRS Table - 2018
 | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8 | Scenario 9 | Scenario 10 | Scenario 11 | Scenario 12
LR/PFR | 2.25:1 | 2.11:1 | 1.99:1 | 1.87:1 | 1.77:1 | 1.69:1 | 1.61:1 | 1.54:1 | 1.47:1 | 1.41:1 | 1.36:1 | 1.3:1
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240
PFR Req. (no LR) (MW) | 5246 | 4916 | 4620 | 4361 | 4132 | 3927 | 3743 | 3576 | 3424 | 3285 | 3157 | 3040
*RRS (MW) | 3229 | 3162 | 3090 | 3039 | 2984 | 2920 | 2868 | 2815 | 2772 | 2726 | 2676 | 2643
 | Scenario 13 | Scenario 14 | Scenario 15 | Scenario 16 | Scenario 17 | Scenario 18 | Scenario 19 | Scenario 20 | Scenario 21 | Scenario 22 | Scenario 23 | Scenario 24 | Scenario 25
LR/PFR | 1.26:1 | 1.22:1 | 1.17:1 | 1.14:1 | 1.1:1 | 1.07:1 | 1.04:1 | 1.01:1 | 1.00:1 | 1.00:1 | 1.00:1 | 1.00:1 | 1.00:1
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370
PFR Req. (no LR) (MW) | 2932 | 2831 | 2737 | 2650 | 2569 | 2492 | 2421 | 2353 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS (MW) | 2594 | 2550 | 2523 | 2477 | 2446 | 2408 | 2373 | 2342 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS quantity is calculated with limit of 50% limit on LRs.
**Red font in table above identifies study scenario where RRS needed < 2300 MW. 2300 MW floor will be used in RRS requirement determination.
***Generation mix (CCs, Gas, SC, Coal, Steam) providing 1150 MW of PFR has been aligned with actual historic system operations.
Inertia < 250 GW·s: 30% Coal + 70% Rest. Inertia ≥ 250 GW·s: 15% Coal + 85% Rest

## Slide 11: RRS Jan 2018
*2300 MW Floor across all hours.

## Slide 12: RRS Mar 2018

## Slide 13: RRS Aug 2018

## Slide 14: Hourly Avg. RRS Comparison

## Slide 15: Inertia Contribution of Units with NSO
List of Units | 
GIBCRK_GIB_CRG1 | SDSES_UNIT4
MNSES_UNIT1 | SD5SES_UNIT5
MNSES_UNIT2 | BBSES_UNIT1
MNSES_UNIT3 | BBSES_UNIT2

## Slide 16: Impact over Minimum Inertia of Units with NSO
 | System Inertia (MW·s) | Inertia from Units with NSO (MW·s) | Adjusted System Inertia (MW·s)
4/10/16 2:00 | 142869 | 3185 | 139684
11/22/16 1:00 | 148378 | 12571 | 135807 Overall minimum adjusted system inertia
 | System Inertia (MW·s) | Inertia from Units with NSO (MW·s) | Adjusted System Inertia (MW·s)
2/10/17 2:00 | 134209 | 11047 | 123162 Overall minimum adjusted system inertia
2016
2017 (Jan-Sep)

## Slide 17
Divider Slide
Divider Slide (optional)
Non Spinning Reserve

## Slide 18: Non Spinning Reserve Methodology (NSRS) - 2018
ERCOT is proposing two changes to Non Spin Service Methodology for 2018.
  Include solar generation and solar forecast in the calculations for Net Load and Net Load Forecast i.e. include effects of solar in Net Load Forecast error & Net Load up ramp risk calculation.
  Include an adjustment to account for additional over-forecast uncertainty from projected increase in installed wind capacity in 2018.
The subsequent slides depict a preliminary assessment of Non Spin quantities for January 2018 thru September 2018 using the above changes to the current methodology (2015, 2016 and 2017 Net Load Forecast Error and risk of Net Load Ramp).

## Slide 19: Adjustment to Non-Spin based Wind Growth - 2018
Average hourly adjustment to Non Spin Requirement = 121 MW

## Slide 20: NSRS Jan 2018
*1375 MW Floor in On-peak hours (HE 7 thru 22)

## Slide 21: NSRS Mar 2018

## Slide 22: NSRS Aug 2018

## Slide 23: Hourly Avg. NSRS Comparison

## Slide 24
Divider Slide
Divider Slide (optional)
Discussion

## Slide 25
Divider Slide
Divider Slide (optional)
Appendix

## Slide 26: Wind Installation Capacity
*The projected wind installed capacity (based on IA Signed with Financial Security) is from July 2017 Generator Interconnection Status Report posted here.

## Slide 27: Installed Wind Capacity
*The projected wind installed capacity (based on IA Signed with Financial Security) is from July 2017 Generator Interconnection Status Report posted here.

## Slide 28: Growth in Installed Wind Capacity
Growth in Installed Wind Capacity in Jan 2018 = Projected Wind Capacity in Jan 2018 – Installed Wind Capacity in Jan 2017
*The projected wind installed capacity (based on IA Signed with Financial Security) is from July 2017 Generator Interconnection Status Report posted here.

## Slide 29: 3-HA Wind Over-Forecast Error
Chart: Wind intalled capacity (MW)
| 42005 | 42036 | 42064 | 42095 | 42125 | 42156 | 42186 | 42217 | 42248 | 42278 | 42309 | 42339 | 42370 | 42401 | 42430 | 42461 | 42491 | 42522 | 42552 | 42583 | 42614 | 42644 | 42675 | 42705 | 42736 | 42767 | 42795 | 42826 | 42856 | 42887 | 42917 | 42948 | 42979
MAE of 3-hour ahead Wind Forecast Eerror | 574 | 743 | 635 | 862 | 947 | 696 | 561 | 553 | 551 | 668 | 770 | 903 | 702 | 637 | 705 | 669 | 852 | 742 | 758 | 901 | 758 | 801 | 894 | 947 | 1106 | 1078 | 929 | 1150 | 962 | 906 | 964 | 818 | 705
Wind Installed Capacity | 12822.9032 | 13417.6071 | 13867.9355 | 13950 | 14276.6129 | 14841.7667 | 14898 | 14898 | 15264.7667 | 15609.6129 | 16078.3333 | 16170 | 16246 | 16246 | 16547 | 16547 | 16568 | 16568 | 17013 | 17013 | 17013 | 17834 | 18564 | 18571 | 18923 | 19121 | 19284 | 19284 | 19284 | 19687 | 19687 | 20193 | 20193

## Slide 30: 3-HA Wind Over-Forecast Error
Over time an increasing trend is visible in the 3-HA Wind Over-Forecast Error.
2013
2014
2015
2016
2017

## Slide 31: Estimated Increase in Wind Over-Forecast Error - 2018
An increase in wind over forecast MW error per 1000 MW increase in installed Wind capacity has been estimated using error in forecasting wind forecast in the last five years.
Average hourly increase in Wind Forecast error per 1000 MW increase in installed Wind capacity = 45 MW

## Slide 32: Estimated Increase in Wind Over-Forecast Error based Wind Growth
Using projected installed wind capacity, compute adjustment to Non-Spin requirement.
Average hourly adjustment to Non Spin Requirement = 121 MW