## Slide 1
Discussion on July and August Reliability Unit Commitment Activity (Updated)
Wholesale Market Subcommittee
Dan Woodfin and David Maggio
November 6, 2017

## Slide 2: Introduction
This material is being presented in response to requests from WMS members.
Agenda:
  Reliability Unit Commitment (RUC) Overview
  Analysis of conditions at time of RUCs for capacity
  Load/IRR/COP Input Accuracy
  Analysis of RUC for transmission

## Slide 3: RUC Overview

## Slide 4: RUC Process Overview
The vast majority of unit commitments are made by market participants based on their expectations of market conditions
The RUC process is used to ensure that there is sufficient Resource capacity available to resolve any projected transmission overloads and meet forecasted aggregate system Load requirements.
Ancillary Services (AS) are then used to cover variability around the Resource capacity requirements due to:
  Instant to instant variability in Load and Generation;
  Load and Resource ramps;
  Resource trips; and,
  Load and Resource availability forecast errors.

## Slide 5: RUC Process Overview
Inputs for the analysis include:
  Network model information
  Hourly load forecasts
  Current Operating Plans (COPs)
    This includes Resource statuses, limits, and AS responsibilities.
    IRR forecasts are inherent in the COP information
    Additional Resource information
These inputs can all be sources of uncertainty for the studies

## Slide 6: RUC Process Overview
The RUC engine produces recommendations based on those inputs
  These recommendations are reviewed by ERCOT operators
  In cases where conditions and Resource capability allow it, decisions about recommendations from RUC engine are deferred.
Operating Condition Notices (OCNs) announcing the projected reserve capacity shortage are typically issued when projected shortages are identified in advance, to give the market an opportunity to self-commit additional Resources to meet the identified need rather than ERCOT issuing RUC instructions.

## Slide 7: Reliability Conditions and Concerns as Seen by RUC

## Slide 8: Summary of RUC Instructions
RUC Reason | RUC Bought Back | July | August
System Capacity | N | 3 | 42
 | Y | 0 | 0
Congestion | N | 37 | 4
 | Y | 28 | 23
Storm Related | N | 0 | 35
 | Y | 0 | 0
Count of RUC-Instructed Resource-Hours
  Resources are not necessarily available for dispatch in real-time for the entirety of the hour.

## Slide 9: RUC for Capacity on July 17th (Updated)
ERCOT was projecting a reserve capacity shortage and issued an OCN at 6:08 AM.
771 MW short for hour ending 15
  392 MW committed
Load was slightly under-forecasted but observed 1,000+ MW of additional Resource capacity beyond the 10 AM projection.
  Difference does not appear driven by IRR forecasts
1461 MW of Resources with start-up times < 1 hour were showed at OFF for hour ending 15
  Excludes Combined-Cycle Resources
Chart: Forecasted Load vs. Projected Online Capacity during July 17, 2017 Hourly RUC at 10 AM
HASL-Load | 1453.7 | 1134.4 | 26.1 | -770.6 | -598.8 | -150 | 636 | -288.6 | 1502.6 | 2148.9 | 2415.8
HSL | 60396.3 | 62617.1 | 63577.1 | 64132.1 | 64612.3 | 65179.8 | 65353.1 | 63382.7 | 63258.7 | 62071.1 | 60931.4
HASL | 57737.3 | 60076 | 61035.9 | 61634.7 | 62158.6 | 62692.4 | 62868.2 | 60880.8 | 60875.6 | 59681.1 | 58600.4
Load | 56283.6 | 58941.6 | 61009.8 | 62405.3 | 62757.4 | 62842.4 | 62232.2 | 61169.4 | 59373 | 57532.2 | 56184.6

## Slide 10: RUC for Capacity on August 4th (Updated)
ERCOT was projecting a reserve capacity shortage and issued an OCN at 8:41 AM.
704 MW short for hour ending 16
  435 MW committed
Some additional Resource capacity was observed, however load was also over-forecasted by between ~1,500 and 2,000 MW for the RUC-committed hours.
1537 MW of Resources with start-up times < 1 hour were showed at OFF for hour ending 15
  Excludes Combined-Cycle Resources
Chart: Forecasted Load vs. Projected Online Capacity during August 4, 2017 HRUC at 12 PM
HASL-Load | 105.6 | -459.5 | -704.2 | -113.6 | 378.7 | -67.2
HSL | 64868 | 66149.2 | 66667.4 | 67140.7 | 66871.5 | 64936.9
HASL | 62267.5 | 63695.9 | 64245.1 | 64725.4 | 64415.4 | 62461.9
Load | 62161.9 | 64155.4 | 64949.3 | 64839 | 64036.7 | 62529.1

## Slide 11: RUC for Capacity on August 5th (Updated)
ERCOT was projecting a reserve capacity shortage and issued an OCN at 8:24 AM.
1,906 MW short for hour ending 16
  1,248 MW committed for that same hour (less for other hours)
Additional Resource capacity and an over-forecasting of load was observed.
  Difference in additional Resource capacity partially driven by under-forecasting of IRR capability
1592 MW of Resources with start-up times < 1 hour were showed at OFF for hour ending 15
  Excludes Combined-Cycle Resources
Chart: Forecasted Load vs. Projected Online Capacity during August 5, 2017 HRUC at 10 AM
HASL-Load | 3436.7 | 1666.7 | 729.9 | -648.1 | -1905.9 | -1874.9 | -952.1 | -202.6 | 2837.7 | 3451.4 | 3600.2
HSL | 61366.6 | 62912.5 | 64569.2 | 64946.5 | 65109.7 | 65549.3 | 65950.2 | 64863.9 | 64899.8 | 64114.9 | 61895.7
HASL | 58717.6 | 60299 | 61990.3 | 62515.5 | 62704.7 | 63166.2 | 63539.9 | 62429.4 | 62526.5 | 61808.9 | 59527.9
Load | 55280.9 | 58632.3 | 61260.4 | 63163.6 | 64610.6 | 65041.1 | 64492 | 62632 | 59688.8 | 58357.5 | 55927.7

## Slide 12: RUC for Capacity on August 6th (Updated)
ERCOT was projecting a reserve capacity shortage and issued an OCN at 3:19 AM.
1,830 MW short for hour ending 19 (as much as 2,669 MW short during the 6 AM HRUC)
  1349 MW committed between the 2 HRUCs
Additional Resource capacity and an over-forecasting of load was observed.
  Difference in additional Resource capacity partially driven by under-forecasting of IRR capability
1626 MW of Resources with start-up times < 1 hour were showed at OFF for hour ending 15
  Excludes Combined-Cycle Resources
Chart: Forecasted Load vs. Projected Online Capacity during August 6, 2017 HRUC at 7 AM
HASL-Load | 1973.4 | 2500.2 | 868 | -699.6 | -1418.9 | -1813.3 | -1829.7 | -1849.1 | -785.3 | 555.2 | 632.1 | 1634.6
HSL | 59418.7 | 62198.7 | 63398.2 | 64084.7 | 64328.5 | 64542.3 | 64531.9 | 63131.3 | 62101.3 | 61898.5 | 60510.1 | 58422.1
HASL | 56770.6 | 59631.7 | 60801.2 | 61668.7 | 61936.8 | 62149.5 | 62113.8 | 60706.3 | 59730.8 | 59586.7 | 58137 | 56039.2
Load | 54797.2 | 57131.5 | 59933.2 | 62368.3 | 63355.7 | 63962.8 | 63943.5 | 62555.4 | 60516.1 | 59031.5 | 57504.9 | 54404.6

## Slide 13: RUC Input Accuracy

## Slide 14: Wind Forecasting Error
Wind Forecasting Error (MAPE) | July 2017 | Aug. 2017
1-hour ahead | 3.7% | 3.2%
3-hour ahead | 4.0% | 3.5%

## Slide 15: Wind Forecasting Error (Added)
Wind Forecasting Error (MAE) | July 2017 | Aug. 2017
1-hour ahead (MW) | 720 | 640
3-hour ahead (MW) | 791 | 708

## Slide 16: Load Forecasting Error
Load Forecasting Error (MAPE) | July 2017 | Aug. 2017
1-hour ahead | 0.8% | 0.98%
3-hour ahead | 1.2% | 1.6%

## Slide 17: Load Forecasting Error (Added)
Load Forecasting Error (MAE) | July 2017 | Aug. 2017
1-hour ahead (MW) | 410 | 474
3-hour ahead (MW) | 622 | 780

## Slide 18: COP HSL “Forecasts” excluding IRRs
COP HSL Error ex. IRRs (MAPE) | July 2017 | Aug. 2017
1-hour ahead (Latest COP) | 0.90% | 0.88%
3-hour ahead | 1.08% | 1.09%
Chart: 1-Hour Ahead COP HSL Error (July)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
8/1/2017 0:00 | 0.031064 | 0.025853 | 0.0076955 | -0.0045713 | -0.0062027 | 0.00059054 | 0.0047635 | -0.0073776 | -0.0041829 | 0.0011342 | -0.0088645 | 0.0056227 | 0.01162 | 0.0011918 | 0.0020548 | -0.001182 | -0.0014865 | 0.00087773 | 0.0021806 | 0.003993 | 0.001517 | 0.0093795 | 0.012508 | -0.0037173
8/2/2017 0:00 | -0.0017759 | -0.01335 | 0.0010874 | -0.0012007 | -0.0020257 | 0.0025721 | 0.00094443 | -0.021283 | 3.5988e-05 | 0.0113 | -0.00091931 | -0.017774 | -0.021669 | -0.006092 | -0.0067442 | 1.8947e-05 | 0.0019085 | 0.0031222 | -0.0038165 | -0.0032113 | -0.0059267 | 0.011605 | 0.0080521 | 0.008404
8/3/2017 0:00 | -0.0053391 | -0.012493 | -5.2186e-16 | -0.0010579 | -3.576e-05 | 0.014047 | 0.0083316 | -0.010947 | -0.0013184 | 0.0030983 | -4.2774e-05 | -0.013703 | -0.013479 | -0.005623 | -0.010211 | -0.0092795 | -0.0092851 | -0.0050508 | -0.0077481 | -0.0066432 | -0.011381 | -0.012766 | -0.01182 | 8.3581e-05
8/4/2017 0:00 | 0.0091008 | 0.00038944 | 0.0017325 | 0.0011308 | -0.00042398 | 0.002789 | 0.0059626 | -0.0069019 | 0.0066524 | -0.0068993 | -0.016016 | -0.0089855 | -0.018356 | -0.01105 | -0.020467 | -0.0016855 | -0.0018501 | -0.0063391 | -0.0074481 | 0.00934 | 0.0020772 | 0.012116 | -0.0019668 | 0.010062
8/5/2017 0:00 | -0.0026888 | -0.0028888 | -0.0023575 | -0.0024 | -0.0024941 | -0.0012565 | 0.0015554 | -0.01372 | -0.0278 | -0.023544 | -0.0066495 | -0.0088486 | -0.0073079 | 0.0026274 | -0.0048634 | 0.0083253 | 0.010509 | 0.0090041 | 0.01665 | 0.0044825 | 0.013705 | 0.020628 | 0.024999 | 0.014461
8/6/2017 0:00 | 0.012618 | 0.00041905 | 0.0016836 | 0.0013406 | 0.0012069 | 0.0031733 | -0.0016427 | -0.011269 | -0.0014885 | 0.00066006 | 0.0074583 | 0.0043629 | 0.0042022 | 0.016204 | 0.009575 | 0.020588 | 0.024599 | 0.012385 | 0.018651 | 0.018628 | 0.020944 | 0.014346 | 0.010264 | 0.016391
8/7/2017 0:00 | 0.001744 | -0.0076423 | 4.7183e-05 | 0.0022306 | 0.002604 | -0.0084407 | -0.0066466 | -0.0085099 | 0.0020123 | 0.0010985 | -0.0025736 | -0.0054661 | 0.017238 | 0.020332 | 0.00055224 | 0.011276 | 0.0097999 | 0.0056403 | 0.0068399 | 0.0061687 | 0.0091026 | 0.012143 | 0.022864 | 0.0091843
8/8/2017 0:00 | 0.011322 | -0.0072769 | -0.012276 | -0.012753 | -0.028173 | -0.015344 | -0.0040097 | -0.0075474 | -0.0058021 | -0.0012687 | -0.0027779 | 0.0012243 | 0.010134 | 0.013738 | 0.018626 | 0.021467 | 0.026771 | 0.022596 | 0.021335 | 0.014062 | 0.012175 | 0.018718 | 0.008495 | 0.0017989
8/9/2017 0:00 | 0.00778 | -0.00086577 | 4.7276e-05 | -7.9443e-05 | -0.00015845 | -0.0015976 | -0.00042083 | -0.0011114 | 0.0081445 | 0.0017508 | -0.0001103 | 0.0015438 | -0.0070056 | -0.0063681 | -0.003937 | -0.0021665 | -0.003622 | -0.0062867 | 0.0037804 | -0.013748 | -0.012994 | -0.026737 | -0.021691 | -0.01567
8/10/2017 0:00 | -0.0097287 | -0.016469 | -0.019154 | -0.016696 | -0.015855 | -0.034401 | -0.015861 | -0.017343 | 0.0026458 | 0.0047355 | -0.011869 | -0.022694 | -0.015292 | -0.0023928 | -0.010329 | -0.0059124 | -0.0057676 | -0.0066174 | -0.0058451 | -0.0051256 | -0.012709 | 0.0054059 | -0.012338 | -0.012529
8/11/2017 0:00 | 0.025047 | -0.0045688 | -0.0038887 | -0.0043785 | -0.0054307 | -0.0026113 | -0.028449 | -0.03456 | -0.01166 | 0.01278 | 0.0050153 | 0.0070594 | 0.0017731 | -0.0049302 | 0.0020772 | -0.001588 | -0.00019495 | 0.0086922 | 0.016 | 0.0067022 | 0.0081525 | 0.0017482 | 0.0006172 | -0.023902
8/12/2017 0:00 | 0.036244 | 0.043167 | 0.039036 | 0.039509 | 0.039132 | 0.026952 | 0.014106 | 0.0025846 | -0.0084244 | 0.0089905 | 0.00082031 | -0.014671 | -0.0023934 | -0.012515 | -0.0093091 | -0.015992 | -0.012367 | -0.01022 | 0.0012106 | 0.0025129 | -0.0088188 | 0.004782 | 0.011507 | -0.0013047
Chart: 3-Hour Ahead COP HSL Error (July)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
8/1/2017 0:00 | 0.037126 | 0.02775 | 0.023188 | 0.016121 | -0.0028008 | -0.0045244 | 0.00030681 | -0.0041899 | -0.0092229 | 0.0029707 | -0.015665 | -0.0088451 | -0.0097261 | -0.010933 | -0.00076552 | -0.010704 | -0.014348 | -0.0052069 | -0.0023297 | 0.0042897 | 0.00094124 | 0.0025743 | 0.011715 | -0.0096985
8/2/2017 0:00 | -0.01798 | -0.01421 | -0.015249 | -0.016554 | -0.0019519 | 0.0025721 | 0.0011324 | -0.021446 | -9.4469e-05 | 0.0062789 | -0.0064473 | -0.022362 | -0.023793 | -0.0125 | -0.012622 | -0.0093063 | -0.0067415 | -0.0012619 | -0.0031655 | -0.0050385 | -0.010987 | -0.0055727 | -0.0014439 | 0.0038942
8/3/2017 0:00 | 0.011467 | 0.016344 | 0.0029885 | 0.00054208 | 0.0018714 | 0.014186 | 0.010306 | -0.0094166 | -0.00063214 | 0.0033224 | -0.005545 | -0.020256 | -0.022422 | -0.010202 | -0.014962 | -0.018079 | -0.018742 | -0.01019 | -0.0062175 | -0.020647 | -0.046666 | -0.018637 | -0.012326 | -0.00066651
8/4/2017 0:00 | -0.00019402 | -0.0093123 | 0.0013914 | 0.0024932 | 0.00092915 | 0.002789 | 0.0062504 | -0.0045787 | 0.0067369 | -0.011528 | -0.020669 | -0.01278 | -0.031399 | -0.023193 | -0.031361 | -0.01519 | -0.0073073 | -0.0054402 | -0.0025788 | -0.0074783 | -0.017231 | 0.010704 | -0.0020683 | 0.0099547
8/5/2017 0:00 | -0.0028638 | -0.0028888 | -0.011674 | -0.011711 | -0.0021665 | -0.0014964 | 0.0010014 | -0.014535 | -0.03665 | -0.023844 | -0.0053333 | -0.010961 | -0.0049955 | 0.0099415 | 0.0008716 | 0.005514 | 0.011087 | 0.0093924 | 0.0226 | 0.0037502 | 0.0043945 | 0.0141 | 0.024269 | 0.013872
8/6/2017 0:00 | -0.0029831 | -0.0079824 | 0.0085001 | 0.00090946 | 0.0012069 | 0.0031733 | -0.0018219 | -0.011347 | -0.0064247 | 0.010186 | 0.0070315 | 0.0052227 | 0.0013823 | 0.013075 | 0.0015302 | 0.018421 | 0.024432 | 0.017172 | 0.017238 | 0.015601 | 0.018314 | 0.0133 | 0.0068899 | 0.0088477
8/7/2017 0:00 | -0.0099715 | -0.010802 | -0.016672 | -0.01662 | 0.00041696 | -0.0081955 | -0.0064092 | -0.0085783 | 0.00055282 | -0.0013193 | 0.0033148 | 0.00028594 | 0.017381 | 0.023018 | 0.026283 | 0.025631 | -0.0020861 | -0.0051934 | 0.0047276 | -0.0003474 | 0.0086701 | 0.011458 | 0.022584 | 0.00085948
8/8/2017 0:00 | 0.0084093 | -0.0098072 | -0.012533 | -0.014071 | -0.029236 | -0.023579 | -0.023751 | -0.036998 | -0.0074251 | -0.0017245 | -0.0032521 | -0.0040177 | 0.011589 | 0.0050413 | 0.029926 | 0.027698 | 0.025441 | 0.022993 | 0.025508 | 0.0072019 | 0.011725 | 0.018934 | 0.0046449 | -0.0023387
8/9/2017 0:00 | 0.0076005 | -0.0079015 | -0.0087417 | -0.0019947 | -0.00045821 | -0.0018946 | -0.00042083 | -0.01147 | 0.0064014 | 0.008248 | 0.0064343 | -0.0033859 | -0.016644 | -0.01151 | -0.0068137 | -0.0078204 | -0.0093743 | -0.011702 | -0.0018145 | -0.014096 | -0.017736 | -0.034539 | -0.028339 | -0.021652
8/10/2017 0:00 | -0.031821 | -0.040655 | -0.01883 | -0.019005 | -0.018112 | -0.035106 | -0.016678 | -0.017502 | 0.0025677 | -0.013672 | -0.02709 | -0.029577 | -0.031735 | -0.025865 | -0.029149 | -0.013537 | -0.011834 | -0.010497 | -0.0028819 | -0.0021583 | -0.012438 | -0.013888 | -0.012261 | 0.0044898
8/11/2017 0:00 | -0.0061874 | -0.03028 | -0.0039689 | -0.0041402 | -0.0051624 | -0.002657 | -0.029398 | -0.035133 | -0.014982 | 0.0071185 | -0.0024358 | 0.002608 | -0.0047545 | -0.0091285 | -0.00037249 | 0.006035 | 0.0063865 | 0.0057137 | 0.015157 | 0.00012281 | -0.0051808 | 0.0018044 | 0.00067693 | -0.023902
8/12/2017 0:00 | 0.046116 | 0.0061405 | 0.012282 | 0.045474 | 0.045159 | 0.040352 | 0.020832 | -0.0037702 | -0.0084466 | 0.0049087 | -0.005489 | -0.019405 | -0.0068137 | -0.011712 | -0.019249 | -0.018889 | -0.019765 | -0.020263 | -0.0053584 | 0.0052467 | -0.0083927 | -0.0038309 | 0.011303 | -0.0015172
Chart: 1-Hour Ahead COP HSL Error (August)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
8/1/2017 0:00 | 0.0036018 | -0.00024637 | -0.0011566 | -9.8472e-05 | 0.00012094 | 5.9421e-05 | 0.002953 | 0.0010617 | 0.0081736 | 0.0079984 | 0.025425 | 0.029146 | 0.026534 | 0.006697 | 0.00021629 | 0.0045291 | -0.0024973 | -0.0038526 | 0.007644 | 0.0040822 | 0.0093208 | 0.031419 | 0.033367 | 0.034637
8/2/2017 0:00 | -0.0084454 | -0.011817 | 0.00203 | 0.001211 | -0.0025396 | 0.0013451 | 0.0067338 | -0.0020443 | 0.00069093 | -0.0042309 | -0.0063988 | 0.0007757 | -0.012867 | -0.016025 | -0.010195 | -0.0048227 | -0.01048 | -0.01243 | -0.015734 | -0.017924 | -0.0089009 | -0.013423 | -0.008143 | -0.0058774
8/3/2017 0:00 | -0.0016599 | -4.8364e-05 | 0.011844 | 0.016577 | 0.0077716 | 0.018926 | -0.0004089 | -0.011873 | -0.0089925 | -0.017798 | 0.003004 | -0.0017354 | 0.0033162 | 0.0017107 | -0.0010251 | 0.013345 | 0.010705 | 0.0033508 | 0.016188 | 0.014577 | 0.021021 | 0.020722 | 0.015568 | 0.0034064
8/4/2017 0:00 | -0.0027543 | -0.0044807 | -0.0026308 | -0.0036614 | 0.0026452 | 0.0029553 | 0.0017254 | 0.001599 | 0.0068636 | -0.0086132 | 0.0090123 | 0.0048789 | 0.016359 | 0.011162 | -0.0068342 | -0.0040185 | -0.0034846 | 0.002247 | 0.013392 | 0.013485 | 0.030469 | 0.031967 | -0.0080816 | -0.010265
8/5/2017 0:00 | 0.031999 | 0.0042598 | 0.012689 | 0.013072 | 0.0067968 | 0.0056891 | 0.00028012 | 0.011098 | 0.024111 | -0.00032319 | -0.014706 | -0.0019834 | -0.00055667 | -0.0097382 | -0.0084648 | -0.014257 | -0.01391 | -0.00021304 | 0.023021 | 0.0084963 | -0.0099667 | 0.018732 | 0.0039068 | 0.032279
8/6/2017 0:00 | 0.026404 | 0.011102 | 0.0030295 | 0.0021918 | 0.00093594 | 0.0037937 | 0.0048545 | 0.02282 | 0.025473 | -0.0041664 | -0.011088 | 0.0063262 | 0.0045169 | -0.0020704 | -0.0014808 | 0.0040441 | 0.0013598 | -0.00052905 | -0.003233 | 0.0098352 | 0.016936 | 0.023166 | 0.0053975 | 0.0050775
8/7/2017 0:00 | 0.011037 | 0.00070843 | 0.0037266 | 0.0047698 | 0.00089004 | 0.0063842 | -0.014524 | -0.020654 | 0.0055404 | -0.0012249 | -0.0047232 | -0.003731 | -0.0084266 | -0.015645 | -0.010428 | -0.01414 | -0.015419 | 0.001511 | -0.001901 | 0.0036019 | -0.0051329 | 0.0014489 | -0.0047338 | 0.014562
8/8/2017 0:00 | -0.0032189 | -0.0038271 | -0.0035474 | -0.0038057 | -0.0034512 | -0.0015531 | 0.0066096 | 0.00036538 | 0.0046371 | 0.004966 | -0.0051169 | 0.0030677 | -0.0038716 | -0.0055959 | -0.0017382 | 0.0028114 | 0.022959 | 0.02166 | 0.024795 | 0.014838 | 0.0020628 | 0.021123 | -0.0073398 | -0.01267
8/9/2017 0:00 | -0.0042695 | -0.0059176 | -0.01328 | -0.012128 | -0.0028666 | -0.0036496 | 0.0030838 | -0.0062505 | -0.0023682 | -0.0032428 | 0.00037016 | 0.0027691 | 0.00020615 | -0.0041731 | 0.03108 | 0.031101 | 0.037622 | 0.024888 | 0.036764 | 0.019995 | 0.013525 | 0.031968 | 0.00094597 | -0.0066167
8/10/2017 0:00 | 0.00080574 | -0.00072287 | -0.00053003 | -0.0041093 | -0.0024619 | -0.0012405 | 0.015463 | 0.016619 | 0.025942 | 0.0059258 | 0.026457 | 0.020938 | 0.024335 | 0.00013353 | 0.00058967 | 0.011452 | 0.0098584 | 0.012101 | 0.029195 | 0.020116 | 0.030568 | 0.022599 | 0.0042482 | -0.0035149
8/11/2017 0:00 | 0.0012772 | -0.0012807 | -0.00089771 | 0.0027992 | 0.0071033 | 0.0077718 | 0.010507 | 0.012748 | 0.0097251 | -0.0022322 | -0.00034174 | -0.0030767 | -0.010303 | 0.0025068 | 0.00052337 | 0.0031573 | 0.0023759 | 0.0046434 | 0.0099612 | 0.0083794 | 0.014697 | 0.01962 | 0.0085998 | -0.0125
8/12/2017 0:00 | 0.0078393 | -0.00058316 | -0.0026122 | 0.0012803 | 0.005495 | 0.0047121 | 0.00050184 | -5.8121e-05 | 0.0050478 | 0.003815 | -0.0043651 | 0.0039235 | 0.0019793 | 0.0076061 | 0.0089737 | 0.01029 | 0.0087826 | -0.0013024 | 0.0081146 | 0.00024674 | -0.016104 | 0.013359 | 0.0050105 | 0.0080931
Chart: 3-Hour Ahead COP HSL Error (August)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
8/1/2017 0:00 | 0.0019637 | 0.0034902 | -0.0011463 | -8.8214e-05 | 0.00012094 | -0.00011474 | 0.0029224 | 0.0012027 | 0.0081136 | 0.0029992 | 0.019809 | 0.039693 | 0.051039 | 0.016679 | 0.0029491 | 0.0045684 | -0.0024029 | -0.0052675 | 0.0044385 | 0.00067786 | 0.0046784 | 0.032382 | 0.035377 | 0.036202
8/2/2017 0:00 | -0.0013107 | -0.0047238 | -0.010261 | -0.010808 | -0.002379 | 0.0012859 | 0.0067338 | -0.0012449 | 0.00085945 | -0.0059893 | -0.026706 | -0.021369 | -0.030724 | -0.022074 | -0.012292 | -0.0030359 | -0.0085166 | -0.012145 | -0.018275 | -0.020012 | -0.022693 | -0.029563 | -0.013485 | -0.011372
8/3/2017 0:00 | -0.011012 | -0.00036071 | 0.0018328 | -0.003073 | -0.0025314 | 0.018886 | 0.0068648 | -0.0060785 | -0.017971 | -0.027335 | -0.01083 | -0.017358 | -0.0087349 | -0.019277 | -0.0051789 | 0.0012661 | 0.010991 | 0.019036 | 0.019902 | 0.013035 | 0.027186 | 0.020775 | 0.015398 | 0.0033867
8/4/2017 0:00 | -0.0031323 | -0.004981 | -0.0029115 | -0.003972 | 0.0025855 | 0.0029156 | 0.0017451 | 0.0010699 | 0.0065938 | -0.0083878 | 0.0071068 | 0.012504 | 0.021653 | 0.011771 | 0.0033321 | -0.001047 | -0.0087695 | -0.00066794 | 0.0066269 | 0.0085243 | 0.030944 | 0.03224 | -0.0077457 | -0.010223
8/5/2017 0:00 | 0.022071 | -0.0061294 | 0.012758 | 0.014223 | 0.015712 | 0.0146 | 0.0014281 | 0.011098 | 0.017021 | 0.0068509 | -0.015779 | -0.0070371 | -0.0052172 | 0.002675 | -0.0038232 | -0.02617 | -0.02023 | -0.0067562 | 0.018997 | 0.0089586 | -0.0087347 | 0.0070578 | -0.0072585 | 0.032496
8/6/2017 0:00 | 0.026771 | 0.010912 | -5.812e-05 | -0.00031485 | 0.00093594 | 0.0065842 | 0.0036289 | 0.022785 | 0.02544 | -0.004355 | -0.012564 | 0.0041519 | -0.0063418 | -0.016611 | 0.0021154 | 0.0011146 | -9.2904e-05 | -0.0095898 | 0.0010342 | 0.0072418 | 0.012421 | 0.028947 | 0.011324 | 0.0045791
8/7/2017 0:00 | 0.011037 | 9.809e-05 | 0.0025954 | 0.0042485 | 0.0047107 | 0.010181 | -0.014524 | -0.020899 | 0.0053044 | -0.0021468 | -0.0092492 | -0.0079981 | -0.026857 | -0.028513 | -0.022189 | -0.02055 | -0.017902 | -0.015893 | -0.015385 | 0.0025306 | -0.0058819 | 0.0011637 | -0.0043421 | 0.015352
8/8/2017 0:00 | -0.0029518 | -0.0029237 | -0.00365 | -0.0038057 | -0.0034512 | -0.0015531 | 0.0066096 | 0.00094757 | 0.0052101 | 0.0011174 | -0.0039192 | 0.0038533 | -0.010938 | -0.01559 | -0.0081914 | -0.0025514 | 0.017454 | 0.025878 | 0.030442 | 0.01529 | -0.0039777 | 0.014984 | -0.0082377 | -0.013602
8/9/2017 0:00 | -0.012609 | -0.012895 | -0.012181 | -0.0087005 | 0.00066819 | 0.0024589 | 0.0096591 | -0.019786 | -0.011977 | -0.011982 | -0.020985 | -0.015825 | -0.0064809 | -0.0035105 | 0.033244 | 0.041988 | 0.037227 | 0.044536 | 0.05084 | 0.026068 | 0.022897 | 0.032147 | 0.00075213 | -0.0065154
8/10/2017 0:00 | -0.0071415 | -0.0087091 | -0.00053003 | -0.0042115 | -0.0027684 | -0.0014029 | 0.015503 | 0.014318 | 0.023709 | 0.014258 | 0.029915 | 0.023339 | 0.025183 | 0.0010698 | 0.0017475 | 0.01217 | 0.0086713 | 0.01491 | 0.032009 | 0.018904 | 0.016359 | 0.0088352 | 0.0039714 | -0.003324
8/11/2017 0:00 | 0.0013366 | -0.0010226 | 0.0026615 | 0.0041182 | 0.0070049 | 0.0077718 | 0.01634 | 0.011437 | 0.0052086 | -0.0020907 | 0.00058874 | -0.0014864 | -0.0084636 | 0.009219 | 0.0024075 | -0.0014319 | 0.0037463 | 0.0016701 | 0.0010984 | 0.0084423 | 0.010574 | 0.015079 | 0.0055762 | -0.011166
8/12/2017 0:00 | 0.0049173 | -0.00034018 | 0.00022495 | 0.00033118 | 0.0032696 | 0.0033149 | 0.00057811 | 0.0021064 | 0.0034556 | 0.0011296 | -0.0049962 | 0.0050408 | 0.011328 | 0.0093917 | 0.013105 | 0.02464 | 0.01703 | 0.00021946 | 0.0077156 | -0.00026375 | -0.0073545 | -0.00045913 | -0.012632 | 0.0085309

## Slide 19: COP HSL “Forecasts” excluding IRRs (Added)
COP HSL Error ex. IRRs (MAE) | July 2017 | Aug. 2017
1-hour ahead (Latest COP) | 500 MW | 466 MW
3-hour ahead | 596 MW | 572 MW
Chart: 1-Hour Ahead COP HSL Error (August)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
8/1/2017 0:00 | 175.9 | -12 | -56.3 | -4.8 | 5.9 | 2.9 | 144.7 | 52.7 | 408.9 | 426.7 | 1426.5 | 1736.5 | 1652.8 | 422.8 | 13.7 | 288 | -158.8 | -240.7 | 468.1 | 243.3 | 542.3 | 1795 | 1809.6 | 1799.2
8/2/2017 0:00 | -421.4 | -588.1 | 101.1 | 60.3 | -126.5 | 68.2 | 349 | -107.4 | 36.9 | -230.5 | -356.6 | 44.2 | -730.3 | -916.7 | -588.3 | -280.7 | -606.7 | -718.4 | -894.3 | -1011.4 | -495 | -726 | -417.7 | -293.1
8/3/2017 0:00 | -82.2 | -2.4 | 592.6 | 830.2 | 389.6 | 962.9 | -20.8 | -598.3 | -456.7 | -931.3 | 164.7 | -97.8 | 192.9 | 100.9 | -61.2 | 809.5 | 650.4 | 203.7 | 982.8 | 864.1 | 1219 | 1174 | 825.4 | 173.2
8/4/2017 0:00 | -137.7 | -223.9 | -131.2 | -182.7 | 133 | 149.1 | 87.5 | 81.6 | 356.2 | -458.5 | 510.8 | 291.5 | 1020 | 713.7 | -438.3 | -258.3 | -222.2 | 142.3 | 821.1 | 805.7 | 1732.8 | 1756.9 | -409 | -491.6
8/5/2017 0:00 | 1450.3 | 184.1 | 550.4 | 567.7 | 295.8 | 249 | 12.2 | 489.5 | 1088.3 | -15.7 | -753.9 | -104 | -30.1 | -546.8 | -477.8 | -810.2 | -793.2 | -12.1 | 1292.9 | 463.2 | -522.6 | 951.5 | 186.5 | 1484.6
8/6/2017 0:00 | 1151.4 | 465.4 | 125.1 | 90.5 | 38.7 | 157.7 | 202 | 966.8 | 1139.5 | -198.9 | -555.8 | 334.6 | 250 | -117.9 | -86.8 | 240.2 | 80.5 | -30.9 | -186 | 553.7 | 941.6 | 1254.3 | 279.6 | 244.5
8/7/2017 0:00 | 511.6 | 32.5 | 171.3 | 219.6 | 41 | 295.9 | -699.7 | -1008.7 | 281.7 | -65.1 | -258.8 | -206.7 | -467.9 | -865.6 | -575.4 | -781 | -850.8 | 83 | -103.9 | 195 | -274.1 | 76.2 | -241.7 | 718.7
8/8/2017 0:00 | -156.7 | -186.4 | -172.8 | -185.4 | -168.3 | -76.2 | 327.9 | 18.2 | 234.7 | 260.3 | -277.7 | 171.8 | -220.8 | -321.4 | -100.2 | 163.3 | 1353.3 | 1278.6 | 1448.9 | 852.8 | 114.4 | 1142.4 | -376 | -625.1
8/9/2017 0:00 | -205.3 | -284.7 | -639.1 | -586.7 | -139 | -178.7 | 153.6 | -313.1 | -120.4 | -168.9 | 20 | 154.6 | 11.9 | -247.5 | 1921.2 | 1950.3 | 2385.6 | 1579.6 | 2274.8 | 1198.6 | 787.9 | 1786.4 | 48.8 | -326.6
8/10/2017 0:00 | 39.5 | -35.4 | -26 | -200.9 | -120.5 | -61.1 | 776.4 | 863.1 | 1362.5 | 322.3 | 1510 | 1264.1 | 1527.1 | 8.6 | 38.4 | 754.4 | 648.6 | 788.4 | 1862.5 | 1257.1 | 1847.9 | 1300.4 | 230.2 | -184.1
8/11/2017 0:00 | 64.5 | -64.5 | -45.4 | 142.2 | 361.2 | 397.3 | 542.3 | 680.5 | 529.7 | -126.2 | -20.2 | -189.6 | -655.3 | 164.7 | 35 | 211.9 | 159.5 | 307.5 | 648.4 | 533.2 | 898.3 | 1149.2 | 469.3 | -646.5
8/12/2017 0:00 | 391.7 | -28.8 | -128.9 | 63.4 | 273.1 | 235.4 | 25 | -2.9 | 258.7 | 202.3 | -242.1 | 227.4 | 119.4 | 472.4 | 570.4 | 659.7 | 563.3 | -81.9 | 500.3 | 14.5 | -911.1 | 733.2 | 262.7 | 406.6
Chart: 3-Hour Ahead COP HSL Error (August)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
8/1/2017 0:00 | 95.9 | 170 | -55.8 | -4.3 | 5.9 | -5.6 | 143.2 | 59.7 | 405.9 | 160 | 1111.4 | 2364.9 | 3179.2 | 1053 | 186.8 | 290.5 | -152.8 | -329.1 | 271.8 | 40.4 | 272.2 | 1850 | 1918.6 | 1880.5
8/2/2017 0:00 | -65.4 | -235.1 | -511 | -538.2 | -118.5 | 65.2 | 349 | -65.4 | 45.9 | -326.3 | -1488.3 | -1217.6 | -1743.8 | -1262.7 | -709.3 | -176.7 | -493 | -701.9 | -1038.7 | -1129.2 | -1262 | -1599 | -691.7 | -567.1
8/3/2017 0:00 | -545.3 | -17.9 | 91.7 | -153.9 | -126.9 | 960.9 | 349.2 | -306.3 | -912.7 | -1430.3 | -593.8 | -978.2 | -508.1 | -1137 | -309.2 | 76.8 | 667.8 | 1157.2 | 1208.3 | 772.7 | 1576.5 | 1177 | 816.4 | 172.2
8/4/2017 0:00 | -156.6 | -248.9 | -145.2 | -198.2 | 130 | 147.1 | 88.5 | 54.6 | 342.2 | -446.5 | 402.8 | 747.1 | 1350.1 | 752.6 | 213.7 | -67.3 | -559.2 | -42.3 | 406.3 | 509.3 | 1759.8 | 1771.9 | -392 | -489.6
8/5/2017 0:00 | 1000.3 | -264.9 | 553.4 | 617.7 | 683.8 | 639 | 62.2 | 489.5 | 768.3 | 332.8 | -808.9 | -369 | -282.1 | 150.2 | -215.8 | -1487.2 | -1152.1 | -383.2 | 1066.9 | 488.4 | -458 | 358.5 | -346.5 | 1494.6
8/6/2017 0:00 | 1167.4 | 457.4 | -2.4 | -13 | 38.7 | 273.7 | 151 | 965.3 | 1138 | -207.9 | -629.8 | 219.6 | -351 | -945.9 | 124 | 66.2 | -5.5 | -560.1 | 59.5 | 407.7 | 690.6 | 1567.3 | 586.6 | 220.5
8/7/2017 0:00 | 511.6 | 4.5 | 119.3 | 195.6 | 217 | 471.9 | -699.7 | -1020.7 | 269.7 | -114.1 | -506.8 | -443.1 | -1491.3 | -1577.6 | -1224.4 | -1135 | -987.8 | -873 | -840.9 | 137 | -314.1 | 61.2 | -221.7 | 757.7
8/8/2017 0:00 | -143.7 | -142.4 | -177.8 | -185.4 | -168.3 | -76.2 | 327.9 | 47.2 | 263.7 | 58.5 | -212.7 | 215.8 | -623.8 | -895.4 | -472.2 | -148.2 | 1028.8 | 1527.6 | 1778.9 | 878.8 | -220.6 | 810.4 | -422 | -671.1
8/9/2017 0:00 | -606.3 | -620.4 | -586.2 | -420.9 | 32.4 | 120.4 | 481.1 | -991.1 | -608.9 | -623.8 | -1133 | -883.5 | -374.1 | -208.2 | 2055 | 2633 | 2360.6 | 2826.6 | 3145.8 | 1562.6 | 1333.9 | 1796.4 | 38.8 | -321.6
8/10/2017 0:00 | -350.1 | -426.5 | -26 | -205.9 | -135.5 | -69.1 | 778.4 | 743.6 | 1245.2 | 775 | 1706.1 | 1409.1 | 1580.3 | 68.9 | 113.8 | 801.7 | 570.5 | 971.4 | 2042 | 1181.4 | 988.9 | 508.4 | 215.2 | -174.1
8/11/2017 0:00 | 67.5 | -51.5 | 134.6 | 209.2 | 356.2 | 397.3 | 843.3 | 610.5 | 283.7 | -118.2 | 34.8 | -91.6 | -538.3 | 605.7 | 161 | -96.1 | 251.5 | 110.6 | 71.5 | 537.2 | 646.3 | 883.2 | 304.3 | -577.5
8/12/2017 0:00 | 245.7 | -16.8 | 11.1 | 16.4 | 162.5 | 165.6 | 28.8 | 105.1 | 177.1 | 59.9 | -277.1 | 292 | 682.9 | 583.3 | 833 | 1579.7 | 1092.3 | 13.8 | 475.7 | -15.5 | -416.1 | -25.2 | -662.3 | 428.6
Chart: 1-Hour Ahead COP HSL Error (July)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
8/1/2017 0:00 | 1409.1 | 1131.4 | 332.8 | -196.4 | -266.2 | 25.4 | 212.7 | -337.9 | -196.7 | 56.2 | -454.9 | 304.3 | 650.4 | 67.9 | 117.3 | -67.9 | -85.3 | 50.2 | 122.8 | 222.1 | 83 | 494.8 | 631.3 | -173.4
8/2/2017 0:00 | -75.4 | -543 | 44.2 | -48.8 | -82.3 | 105 | 40.2 | -915.8 | 1.6 | 519.4 | -45.4 | -927.8 | -1188.8 | -343.2 | -387.6 | 1.1 | 111.2 | 181.6 | -216.9 | -177.5 | -318.6 | 600.6 | 392.6 | 372.7
8/3/2017 0:00 | -231.6 | -529.4 | -2.1828e-11 | -44.3 | -1.5 | 605.4 | 375.5 | -507.8 | -63.4 | 152.1 | -2.2 | -746.6 | -773.2 | -332.8 | -614.6 | -561 | -561 | -306.6 | -462.7 | -378 | -619.9 | -674.2 | -584.5 | 3.9
8/4/2017 0:00 | 403.4 | 17.1 | 76.2 | 49.8 | -18.8 | 124.1 | 269.3 | -317 | 315 | -335.4 | -815.8 | -492.5 | -1054.1 | -649.7 | -1208.1 | -101.1 | -111.2 | -380.8 | -439 | 534.8 | 116.4 | 643.7 | -96.9 | 467.8
8/5/2017 0:00 | -122.9 | -132.1 | -107.8 | -109.8 | -114.2 | -57.6 | 73 | -656.6 | -1382.1 | -1255.8 | -368.8 | -519.5 | -445.6 | 165.6 | -310.8 | 536.3 | 678.5 | 579.7 | 1064.8 | 278.5 | 824.3 | 1207.1 | 1368.9 | 737.4
8/6/2017 0:00 | 616.7 | 20.4 | 82 | 65.3 | 58.8 | 154.9 | -82.5 | -575.9 | -77.5 | 36.1 | 419.4 | 258.8 | 257.8 | 1036.2 | 620.1 | 1348.9 | 1616.2 | 811.9 | 1190.4 | 1150.9 | 1250.5 | 823.4 | 562.8 | 858.3
8/7/2017 0:00 | 87.8 | -374.9 | 2.3 | 109.1 | 127.4 | -413.1 | -336 | -435.7 | 105.2 | 59.7 | -148.6 | -328.8 | 1084.9 | 1320.2 | 36.4 | 750.1 | 646.4 | 366 | 431 | 380 | 543 | 691.8 | 1226.5 | 462.7
8/8/2017 0:00 | 532.1 | -336.2 | -573.2 | -599.7 | -1325.6 | -727.4 | -191 | -361.7 | -286 | -66.8 | -152.3 | 70.3 | 609.4 | 848.3 | 1173.7 | 1361 | 1705.5 | 1420.8 | 1303.5 | 834.3 | 702.7 | 1040.9 | 447.9 | 91.3
8/9/2017 0:00 | 368.3 | -40.3 | 2.2 | -3.7 | -7.4 | -75.3 | -19.9 | -53 | 406.5 | 90 | -6 | 88 | -408.5 | -376.5 | -235.4 | -129.9 | -216.6 | -371.5 | 222.3 | -805.6 | -748.4 | -1456.7 | -1119.1 | -766.4
8/10/2017 0:00 | -454.6 | -763.2 | -886.9 | -773.7 | -737.7 | -1608.9 | -776.9 | -869.1 | 135.5 | 251.6 | -658.1 | -1318.7 | -904.9 | -141.7 | -612.5 | -351.3 | -343.2 | -390.6 | -345.2 | -299.7 | -726.7 | 299.8 | -637.4 | -618.4
8/11/2017 0:00 | 1137.1 | -199.2 | -169.7 | -191.1 | -236.9 | -114.3 | -1259.3 | -1562.3 | -547.6 | 629.8 | 265.2 | 393.3 | 102 | -288.3 | 123.8 | -95.2 | -11.7 | 518 | 939.7 | 382 | 454.3 | 93.3 | 31 | -1095.4
8/12/2017 0:00 | 1558.4 | 1764.5 | 1565.6 | 1586.2 | 1571.3 | 1084.1 | 572.5 | 109 | -378.4 | 429.5 | 41.8 | -788.6 | -133.2 | -716.5 | -538.5 | -930.6 | -719.1 | -594.8 | 69.2 | 138.8 | -476 | 250.4 | 564.1 | -61.4
Chart: 3-Hour Ahead COP HSL Error (July)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
8/1/2017 0:00 | 1684.1 | 1214.4 | 1002.8 | 692.6 | -120.2 | -194.6 | 13.7 | -191.9 | -433.7 | 147.2 | -803.9 | -478.7 | -544.4 | -622.9 | -43.7 | -614.9 | -823.3 | -297.8 | -131.2 | 238.6 | 51.5 | 135.8 | 591.3 | -452.4
8/2/2017 0:00 | -763.4 | -578 | -619.8 | -672.8 | -79.3 | 105 | 48.2 | -922.8 | -4.2 | 288.6 | -318.4 | -1167.3 | -1305.3 | -704.2 | -725.4 | -540.3 | -392.8 | -73.4 | -179.9 | -278.5 | -590.6 | -288.4 | -70.4 | 172.7
8/3/2017 0:00 | 497.4 | 692.6 | 125 | 22.7 | 78.5 | 611.4 | 464.5 | -436.8 | -30.4 | 163.1 | -285.2 | -1103.6 | -1286.2 | -603.8 | -900.6 | -1093 | -1132.4 | -618.6 | -371.3 | -1174.8 | -2541.9 | -984.2 | -609.5 | -31.1
8/4/2017 0:00 | -8.6 | -408.9 | 61.2 | 109.8 | 41.2 | 124.1 | 282.3 | -210.3 | 319 | -560.4 | -1052.8 | -700.5 | -1803.1 | -1363.7 | -1851.1 | -911.1 | -439.2 | -326.8 | -152 | -428.2 | -965.6 | 568.7 | -101.9 | 462.8
8/5/2017 0:00 | -130.9 | -132.1 | -533.8 | -535.8 | -99.2 | -68.6 | 47 | -695.6 | -1822.1 | -1271.8 | -295.8 | -643.5 | -304.6 | 626.6 | 55.7 | 355.2 | 715.8 | 604.7 | 1445.3 | 233 | 264.3 | 825.1 | 1328.9 | 707.4
8/6/2017 0:00 | -145.8 | -388.6 | 414 | 44.3 | 58.8 | 154.9 | -91.5 | -579.9 | -334.5 | 557.1 | 395.4 | 309.8 | 84.8 | 836.1 | 99.1 | 1206.9 | 1605.2 | 1125.7 | 1100.2 | 963.9 | 1093.5 | 763.4 | 377.8 | 463.3
8/7/2017 0:00 | -502 | -529.9 | -812.7 | -812.9 | 20.4 | -401.1 | -324 | -439.2 | 28.9 | -71.7 | 191.4 | 17.2 | 1093.9 | 1494.6 | 1732.4 | 1705.1 | -137.6 | -337 | 297.9 | -21.4 | 517.2 | 652.8 | 1211.5 | 43.3
8/8/2017 0:00 | 395.2 | -453.1 | -585.2 | -661.7 | -1375.6 | -1117.8 | -1131.4 | -1773.1 | -366 | -90.8 | -178.3 | -230.7 | 696.9 | 311.3 | 1885.7 | 1756 | 1620.8 | 1445.8 | 1558.5 | 427.3 | 676.7 | 1052.9 | 244.9 | -118.7
8/9/2017 0:00 | 359.8 | -367.8 | -406.8 | -92.9 | -21.4 | -89.3 | -19.9 | -547 | 319.5 | 424 | 350 | -193 | -970.5 | -680.5 | -407.4 | -468.9 | -560.6 | -691.5 | -106.7 | -826 | -1021.5 | -1881.8 | -1462.1 | -1059
8/10/2017 0:00 | -1486.9 | -1884 | -871.9 | -880.7 | -842.7 | -1641.9 | -816.9 | -877.1 | 131.5 | -726.4 | -1502.1 | -1718.7 | -1877.9 | -1531.7 | -1728.5 | -804.3 | -704.2 | -619.6 | -170.2 | -126.2 | -711.2 | -770.2 | -633.4 | 221.6
8/11/2017 0:00 | -280.9 | -1320.2 | -173.2 | -180.7 | -225.2 | -116.3 | -1301.3 | -1588.2 | -703.6 | 350.8 | -128.8 | 145.3 | -273.5 | -533.8 | -22.2 | 361.8 | 383.3 | 340.5 | 890.2 | 7 | -288.7 | 96.3 | 34 | -1095.4
8/12/2017 0:00 | 1982.9 | 251 | 492.6 | 1825.7 | 1813.3 | 1623.1 | 845.5 | -159 | -379.4 | 234.5 | -279.7 | -1043.1 | -379.2 | -670.5 | -1113.5 | -1099.2 | -1149.3 | -1179.3 | -306.3 | 289.8 | -453 | -200.6 | 554.1 | -71.4
Notes: Error = SCED HSL – COP HSL

## Slide 20: Histogram of Wind Forecasting Errors (Added)
6 hour ahead large wind under-forecast error (>3000 MW) occurred on 7/9/2017, 7/30/2017, 8/6/2017

## Slide 21: Histogram of Load Forecasting Errors (Added)
6 hour ahead large load over-forecast error (<-4000 MW) occurred on 7/1/2017, 7/7/2017, 7/15/2017, 8/7/2017, 8/17/2017, 8/21/2017, 8/26/2017

## Slide 22: Histogram of COP HSL “Forecasts” excluding IRRs (Added)
6 hour ahead large COP HSL under-forecast error (>3000 MW) occurred on 7/14/2017, 7/16/2017, 8/1/2017, 8/9/2017, and 8/24/2017

## Slide 23: Transmission Reliability Conditions and Concerns as Seen by RUC

## Slide 24: Examples of Congestion Issues Seen by RUC
This is less straight-forward to evaluate
  Cannot solely look at the COP and forecast information being used by the RUC engine
  Constraint information stored in the systems and presented to operators and market participants represent the outputs from the final iteration

## Slide 25: Examples of Congestion Issues Seen by RUC
Instead, executed specific RUC cases where all COP Resource statuses that were originally “OFF” were changed to “OUT”
  This makes those Resources unavailable for commitment by the RUC engine
  Provides an indication of what RUC would have been unable to solve without the ability to commit additional Resources
  Results may still not always be intuitive for linking RUC instructions to specific constraints.
    E.g., if the commitment of a Resource to solve one constraint drives other congestion within later iterations of the RUC optimization
    Additionally, a large number of RUC engine recommendations are not selected.

## Slide 26: RUC for Congestion on July 20th
For the RUC instruction on July 20th, the commitment was noted as being for congestion, specifically for contingency DRNS_TB5.
Evaluating the RUC study case from 7 AM that day, there was one primary constraint that was violated without the ability to commit Resources
  That congestion was on the line between Basf to Hofman (with contingency DVELCAM8) with violations as high as 16 MW
  There were minor violations on the lines between Singleton to Zenith

## Slide 27: RUC for Congestion on July 29th
For the RUC instruction on July 29th, the commitment was noted as being for congestion, specifically for contingency SHIWCIT8.
Evaluating the RUC study case from 7 AM that day, there were a few constraints that were violated without the ability to commit Resources
  Most notable was congestion on the lines between Singleton to Zenith (with contingency DRNS_TB5) with violations as high as 183 MW
  Constraints on the lines between Morris Street and Nueces Bay (with contingency SHIWCIT8) and between Twin Oak Switch and Jack Creek were also violated, but to a lesser degree

## Slide 28: RUC for Congestion on August 5th
For the RUC instructions on August 5th, one of the commitments was noted as being for congestion, specifically for contingency DWAP_BI5.
Evaluating the RUC study case from 10 AM that day, there were a few constraints that were violated without the ability to commit Resources
  Most notable was congestion on the lines between Singleton to Zenith (with contingency DRNS_TB5) which were violated for all four RUC-instructed hours with violations as high as 80 MW
  A constraint on the line between WA Parish and Jeanetta (with contingency DWAP_BI5) was also violated, but to a lesser degree

## Slide 29: RUC for Congestion on August 15th
For the RUC instructions on August 15th, the commitment was noted as being for congestion, specifically for contingencies SPHRCTR5 and SMDOPHR5.
Evaluating the RUC study case from 8 AM that day, there were a few constraints that were violated without the ability to commit Resources
  Most notable was congestion on the line between Seminole and Friendswood TNP (with contingency SMDOPHR5) with violations for several hours with values as high as 86 MW.

## Slide 30
Questions?