## Slide 1
Challenges building resources near series capacitors
Jonathan Rose
ERCOT Planning Engineer
RPG, 11/14/2017

## Slide 2: Purpose of Presentation
Recently, Renewable Resources are connecting closer to series capacitors, even tapping series-compensated lines themselves
  Causing complex engineering challenges
  May require extra time and extra capital to resolve

## Slide 3: Tapping a Series Compensated Line
Compensation level seen by IRR can be >100%
Potential Challenges:
  More SSR risk
  VRT / tripping issues
  “Energy accumulation”
  Voltage Profile
  Voltage Control

## Slide 4: SSR Risk
Higher percent compensation seen by generator:
  Appears more difficult for renewable manufacturers to damp SSR
  SSR studies take longer

## Slide 5: “Energy Accumulation” and VRT Tripping Issues
Energy accumulates in capacitor during fault
Fault clears, and energy discharges into IRR
May reverse power flow leading to generator tripping
ERCOT expects generators to ride through (LVRT)
May require hardware changes to fix
  Custom engineering. No “off-the-shelf” fix.
Bypassing? The CREZ series capacitors may not automatically bypass depending on fault conditions. Thus energy accumulation is a real possibility.

## Slide 6: Voltage Profile on Series-Compensated Line
(Sample, for illustration)
Voltage varies widely with flow
Most CREZ lines are insulated for normal operation up to 110% voltage
Possible to have voltages >105% during contingency and heavy flows
Voltage control more challenging (effective impedance varies)

## Slide 7: Summary
Unique challenges locating close to series capacitors, especially tapping a series-compensated line
May complicate studies
May require custom engineering solutions
Takeaway:
  GINR-FIS process may need more scrutiny
  Highly recommended perform SSR study well in advance (e.g. 1 year)
  Expect challenges / difficulties
  Temporary taps create extra layer of complexity