NMMS:

ERCOT Modeling Guidelines

Version 1.11

| Document Revisions |
| --- |
| Date | Version | Description | Author(s) |
| 1/13/09 | 0.01 | Initial draft | Terry Nielsen |
| 1/29/09 | 0.02 | Updated rules, edited to support for draft release to NDWSG. | Terry Nielsen |
| 2/17/09 | 0.03 | Updated with section changes based upon NDSWG input and NMMS team input. Also updated to add draft completed section for switch. | Terry Nielsen, Keith Smith |
| 4/9/09 | 0.04 | Updated with sections for: SVC Substations Breakers Disconnectors Shunt Compensators Series Compensators Lines and ACLinesgements SCADA and ICCP data Transformers Modeling Objects | Terry Nielsen Including sections from ERCOT NMMS Team |
| 4/16/09 | 0.05 | Incorporate comments from internal review by MMS and EMS team. | Terry Nielsen Including updates from ERCOT NMMS Team |
| 5/6/2009 | 0.06 | Updates to loads, substations section. Incorporating comments from Market participants. | Kalidindi Raju Joel Koepke Nitika Mago Mario De La Garza Kimberly Boatright Kashia Thuerwaechter Neelima Bezwada Vamsi Madam Keith Smith Rochie Guiyab Sujatha Kotamarty John Moseley |
| 6/3/2009 | 0.07 | Incorporating comments from Austin Energy, Center Point Energy and Oncor | Kalidindi Raju Joel Koepke Nitika Mago Mario De La Garza Kimberly Boatright Kashia Thuerwaechter Neelima Bezwada Vamsi Madam Keith Smith Rochie Guiyab Sujatha Kotamarty John Moseley |
| 6/25/2009 | 0.08 | Incorporating comments from Austin Energy, Center Point Energy and Oncor | Kalidindi Raju Joel Koepke Nitika Mago Mario De La Garza Kimberly Boatright Kashia Thuerwaechter Neelima Bezwada Vamsi Madam Keith Smith Rochie Guiyab Sujatha Kotamarty John Moseley |
| 7/02/2009 | 0.081 | Incorporating comments from Austin Energy | Kalidindi Raju Joel Koepke Nitika Mago Mario De La Garza Kimberly Boatright Kashia Thuerwaechter Neelima Bezwada Vamsi Madam Keith Smith Rochie Guiyab Sujatha Kotamarty John Moseley |
| 8/10/2009 | 1.0 | Black lining the document | Kalidindi Raju |
| 4/22/2010 | 1.1 | Update Validation rules | Neelima Bezwada |
| 1/26/11 | 1.3 | Update with MGRRS | Trisha Miller |
|  | 1.4 |  |  |
| 7/6/2012 | 1.5 | New validation rules in MGRR_0016 | Trisha Miller |
| 2/26/2013 | 1.6 | New walidation rules in MGRR_0017 | Trisha Miller |
| 8/12/2013 | 1.7 | New Validation rules in MGRR_0018 | Trisha Miller |
| 12/5/2014 | 1.8 | New Validation rule in MGRR_0019 | Trisha Miller |
| 5/12/2015 | 1.9 | Updates to appendix A-validation rules-required fields, MGRR_0020 | Trisha Miller |
| 4/23/2016 | 1.10 | Update to validation rule-MGRR_0022 | Trisha Miller |
| 7/6/2016 | 1.10_1 | MGRR__0021SVC Modeling | Trisha Miller |
| 11/2/2016 | 1.11 | MGRR_0023 solar unit val rules | Trisha Miller |
| 11/2/2016 | 1.11 | MGRR_0024 removing necessity to model MVA ratings on transformer winding | Trisha Miller |
| 11/2/2016 | 1.11 | MGRR_0026 shunt compensator required links update | Trisha Miller |
| 4/17/2017 | 1.11 | MGRR_0027 add line length requirement to AC Line Segment | Trisha Miller |
| 4/17/2017 | 1.11 | MGRR_0028 Clarification of required conductor rating | Trisha Miller |
| 4/17/2017 | 1.11 | MGRR_0029 Shunt Compensator update (Dominant Capbank) | Trisha Miller |
| 8/10/2017 | 1.11 | MGRR_0030 Phase Angle | Trisha Miller |
| 8/10/2017 | 1.11 | MGRR_0031 Add County requirement link to Substation | Trisha Miller |
| 9/18/2017 | 1.11 | NMMS Upgrade updates | Trisha Miller |

Table of Contents

1	OVERVIEW	24

1.1	Document Organization	24

1.1.1	Major Sections	24

1.1.2	Modeling Approach Subsection	24

1.1.3	Attribute	24

1.1.4	Linkage	24

1.1.5	Appendix A - Validation Rules for Required Fields	24

1.1.6	Appendix B - Validation Rules for Required Associations	25

1.1.7	Appendix C – Complex Validation Rules	25

1.1.8	Appendix D - Classes Not Allowed Subsection	25

1.1.9	Appendix E – Enumeration Type Values	25

1.1.10	Validations	25

1.1.11	Automatic Validation Performed by NMMS Based Upon Data Dictionary	25

1.1.12	Further Clarification on Interpreting Data Dictionary and How Data is used in NMMS Information Model Manager	26

1.1.13	Relevant reference documents:	27

2	PROJECT TRACKER AND COORDINATOR	28

2.1	SGEM PROJECT	28

2.2	Network Operations model change Request	30

2.3	COLLABORATIVE Action model Request	31

3	Information Model Manager	33

3.1	Create New Instance	34

3.2	Add Attributes	38

3.3	Add Links	39

3.4	Rename Instance	41

3.5	Delete Instance	42

4	Information Model Manager Tools	43

4.1	Templates	43

4.2	Auto Layout	43

5	Modeling Breakers	44

5.1	Modeling Approach	44

5.2	Attributes	45

5.3	Linkage	48

6	Modeling Disconnectors	49

6.1	Modeling Approach	49

6.2	Attributes	50

6.3	Linkage	53

7	Modeling Shunt Compensators	54

7.1	Modeling Approach	54

7.2	Attributes	54

7.3	Linkage	57

8	Modeling Series Compensators	58

8.1	Modeling Approach	58

8.2	Attributes	58

8.3	Linkage	60

9	Modeling Lines	61

9.1	Modeling Approach	61

9.3 Linkage	63

10	Modeling ACLineSegment	64

10.1	Modeling Approach	64

10.2	Attributes	64

10.3	Linkage	66

11	Modeling Substation	68

11.1	Modeling Approach	68

11.2	Attributes	68

11.3	Linkage	72

12	Modeling Bay	74

12.1	Modeling Approach	74

12.2	Attributes	74

12.3	Linkage	75

13	Modeling SCADA	77

13.1	Modeling Approach for SCADA	77

13.1.1	Modeling Approach for MeasurementLocation	78

13.1.1.1	Linkage	78

13.1.2	Modeling Approach for a MeasurementGroup	79

13.1.2.1	Attributes	79

13.1.3	Modeling Approach for a Calculation	80

13.1.3.1	Attributes	81

13.1.3.2	Linkage	82

13.1.4	Modeling Approach for MeasurementArgument	82

13.1.4.1	Attributes	82

13.1.4.2	Linkage	83

13.1.5	Modeling Approach for ConstantArgument	83

13.1.5.1	Attributes	84

13.1.5.2	Linkage	84

13.1.6	Modeling Function and FunctionArguments	85

13.1.7	Modeling Approach for Analog and Discrete Measurement	86

13.1.7.1	Attributes	86

13.1.7.2	Linkage	88

13.1.8	Modeling Approach for SCADA AnalogValue and DiscreteValue	89

13.1.8.1	Attributes	89

13.1.8.2	Linkage	98

13.1.9	Modeling Approach for Auxiliary SCADA Lists	99

14	Modeling ICCP	100

14.1  Modeling Approach for ICCP	100

14.2	Modeling Approach for ICCP AnalogValue and DiscreteValue	101

14.2.1	Attributes	101

14.2.2	Linkage	107

14.3	Modeling Approach for MeasurementValueQuality	108

14.3.1	Attributes	108

14.3.2	Linkage	111

15	Modeling Ratings	112

15.1.1	Modeling Approach for Ratings	112

15.1.1.1	Attributes	113

15.1.1.2	Linkage	114

15.1.2	Modeling Approach for SCADA AnalogLimit	114

15.1.2.1	Attributes	114

15.1.2.2	Linkage	115

15.1.3	Modeling Approach for Ratings AnalogLimit	117

15.1.3.1	Linkage	119

16	Modeling Transformers	120

16.1	Modeling Approach	120

16.2	Modeling Approach for Powertransformer	120

16.2.1	Attributes	121

16.2.2	Linkage	124

16.3	Modeling Approach for POWERTRANSFORMEREND	125

16.3.1	Attributes	125

16.3.2	Linkage	130

16.4	Modeling Approach for TapChanger	131

16.4.1	Attributes	131

16.4.2	Linkage	135

16.5	Modeling Approach for Transformerkluge	136

16.5.1	Attributes	137

16.5.2	Linkage	138

17	Modeling Load	139

17.1	Modeling Approach	139

17.2	Modeling Approach for CustomerLoad	139

17.2.1	Attributes	140

17.2.2	Linkage	143

17.3	Modeling Approach for StationSupply	144

17.3.1	Attributes	145

17.3.2	Linkage	147

17.4	Modeling Approach for ConformLoadGroup	148

17.4.1	Attributes	149

17.4.2	Linkage	150

17.5	Modeling Approach for ConformLoadSchedule	150

17.5.1	Attributes	150

17.5.2	Linkage	150

17.6	Modeling Approach for NONConformLoadGroup	151

17.6.1	Attributes	151

17.6.2	Linkage	152

17.7	Modeling Approach for NONConformLoadSchedule	152

17.7.1	Attributes	152

17.7.2	Linkage	152

18	Modeling Curves	154

18.1	Modeling Approach	154

18.2	Attributes	154

18.3	Linkage	156

19	Modeling CurveData	158

19.1	Modeling Approach	158

19.2	Attributes	158

19.3	Linkage	159

20	Modeling RegularTimePoint	160

20.1	Modeling Approach	160

20.2	Attributes	160

20.3	Linkage	160

21	Modeling Terminal	161

21.1	Modeling Approach	161

21.2	Attributes	161

21.3	Linkage	163

22	Modeling ConnectivityNode	164

22.1	Modeling Approach	164

22.2	Attributes	164

22.3	Linkage	165

23	Modeling ElectricalBus	168

23.1	Modeling Approach	168

23.2	Attributes	169

23.3	Linkage	170

24	Modeling ConnectivityNodeGroup	171

24.1	Modeling Approach	171

24.2	Attributes	171

24.3	Linkage	172

25	Modeling OwnershareRating	174

25.1	Modeling Approach	174

25.2	Attributes	174

25.3	Linkage	175

26	Modeling BusbarSection	176

26.1	Modeling Approach	176

26.2	Attributes	176

26.3	Linkage	180

27	Modeling DynamicElement	181

27.1	Modeling Approach	181

27.2	Attributes	181

27.3	Linkage	182

Classes Only Modeled By ERCOT	183

28	Modeling BaseVoltage	184

28.1	Modeling Approach	184

28.2	Attributes	184

28.3	Linkage	185

29	Modeling Company	186

29.1	Modeling Approach	186

29.2	Attributes	186

29.3	Linkage	188

30	Modeling SubgeographicalRegion	189

30.1	Modeling Approach	189

30.2	Attributes	189

30.3	Linkage	190

31	Modeling Geographical Region	191

31.1	Modeling Approach	191

31.2	Attributes	191

31.3	Linkage	192

32	Modeling Market Objects	193

32.1	Modeling Approach for SettlementHUB	193

32.1.1	Attributes	193

32.1.2	Linkage	194

32.2	Modeling Approach for AggregateHUB	194

32.2.1	HB_HUBAVG	194

32.2.1.1	Attributes	194

32.2.1.2	Linkage	194

32.2.2	HB_BUSAVG	194

32.2.2.1	Attributes	194

32.2.2.2	Linkage	195

32.3	Modeling Approach for HUBBus	195

32.3.1.1	Attributes	195

32.3.1.2	Linkage	195

32.4	Modeling Approach for PricingVector	196

32.4.1	Attributes	196

32.4.2	Linkages	197

32.5	Modeling Approach for EPSMeter	197

32.5.1	Attributes	197

32.5.2	Linkage	197

32.6	Modeling Approach for ResourceNode	197

32.6.1	Attributes	198

32.6.2	Linkage	198

32.7	Modeling Approach for SettlementLoadZone	199

32.7.1	Attributes	199

32.7.2	Linkage	200

32.8	Modeling Approach for SettlementNOIELoadZone	200

32.8.1	Attributes	201

32.8.2	Linkage	202

33	Modeling Generation	203

33.1	Modeling Generating Unit	203

33.1.1	Modeling Approach for Resource Controller	203

33.1.1.1	Attributes	203

33.1.1.2	Linkage	204

33.1.2	Modeling Approach for Generating Unit	205

33.1.2.1	Attributes	205

33.1.2.2	Linkage	215

33.1.3	Modeling Approach for Synchronous Machine	216

33.1.3.1	Attributes	217

33.1.3.2	Linkage	221

33.2	Modeling Combined Cycle PLant	221

33.2.1	Modeling Approach for Combined Cycle Plant	222

33.2.1.1	Attributes	223

33.2.1.2	Linkage	224

33.2.2	Modeling Approach for Logical Configuration	225

33.2.2.1	Attributes	225

33.2.2.2	Linkage	226

33.2.3	Modeling Approach for Configuration	226

33.2.3.1	Attributes	227

33.2.3.2	Linkage	228

33.2.4	Modeling Approach for TransState	229

33.2.4.1	Attributes	229

33.2.4.2	Linkage	230

33.2.5	Modeling Approach for Configuration Member	230

33.2.5.1	Attributes	231

33.2.5.2	Linkage	232

34	Modeling Controllable Load Resources and Load resources	233

34.1	Modeling Approach	233

34.2	Attributes	234

34.3	Linkage	237

35	Modeling Owner Share Limits	238

35.1.1	Modeling Approach	238

35.1.2	Attributes	238

35.1.3	Linkage	239

36	Modeling Ownership	241

36.1	Modeling Approach	241

36.2	Attributes	241

36.3	Linkage	242

37	Modeling Operatorship	243

37.1	Modeling Approach	243

37.2	Attributes	243

37.3	Linkage	244

38	Modeling DC Ties	245

38.1	Modeling Approach	245

38.2	Attributes	245

38.3	Linkage	246

39	Modeling Contingencies	247

39.1	Modeling Approach for contingency	247

39.1.1	Attributes	247

39.1.2	Linkage	250

39.2	Modeling Approach for Contingency Element	250

39.2.1	Attributes	250

39.2.2	Linkage	251

39.3	Modeling approach for Contingency Groups	251

39.3.1	Attributes	252

39.3.2	Linkage	253

39.4	Modeling approach for Contingency Group Members	253

39.4.1	Attributes	253

39.4.2	Linkage	254

40	Modeling Remedial Action Schemes (RAS)	255

40.1	Modeling Approach	255

40.2	Modeling Approach RAS	255

40.2.1	Attributes	256

40.2.2	Linkage	257

40.3	Modeling Approach for RAS-Stage, Stage Trigger, Private Protective Actions	257

40.3.1	Attributes	257

40.3.2	Linkage for RAS-Stage	258

40.3.3	Linkage for RAS-Stage Trigger	258

40.3.4	Linkage for RAS- Private Protective Actions	258

40.4	Modeling Approach for RAS-Protective Action ACLine Segment, Series   Compensator, Switch, and Transformer Winding	258

40.4.1	Attributes	258

40.4.2	Linkage	259

40.5	Modeling Approach for RAS-Protective Action Analog, Energy Consumer, Station Reduction, and Synchronous Machine	259

40.5.1	Attributes	259

40.5.2	Linkage	260

40.6	Modeling Approach for RAS-Protective Action and Protective Action Shared	261

40.6.1	Attributes	261

40.6.2	Linkage for RAS- Protective Action	261

40.6.3	Linkage for RAS- Protective Action Shared	261

40.7	Modeling Approach for RAS- Trigger Condition	262

40.7.1	Attributes	262

40.7.2	Linkage	262

40.8	Modeling Approach for RAS- Gate	263

40.8.1	Attributes	263

40.8.2	Linkage	264

40.9	Modeling Approach for RAS- Gate Input Pin, Pin Branch Group, Pin Branch Group, Pin Gate, Pin Switch, Pin Trigger Condition, and Pin Voltage	264

40.9.1	Attributes	264

40.9.2	Linkage for RAS- Gate Input Pin	265

40.9.3	Linkage for RAS- Pin Branch Group	265

40.9.4	Linkage for RAS- Pin Gate	265

40.9.5	Linkage for RAS- Pin Switch	265

40.9.6	Linkage for RAS- Pin Trigger Condition	266

40.9.7	Linkage for RAS- Pin Voltage	266

40.10	Modeling Approach for RAS-Pin Flow	266

40.10.1	Attributes	266

40.10.2	Linkage	267

41	Modeling PrivateAreaNetworks	268

41.1	Modeling Approach	268

41.2	Attributes	268

41.3	Linkage	269

42	Modeling Branch Group	270

42.1	Modeling Approach	270

42.2	Attributes	270

42.3	Linkage	271

43	Modeling Branch Group Terminal	272

43.1	Modeling Approach	272

43.2	Attributes	272

43.3	Linkage	273

44	Modeling Endcap	274

44.1	Modeling Approach	274

44.2	Attributes	274

44.3	Linkage	275

45	Modeling Tiecorridor	277

45.1	Modeling Approach	277

45.2	Attributes	277

45.3	Linkage	278

46	Modeling PermissionArea	279

46.1	Modeling Approach	279

46.2	Attributes	279

46.3	Linkage	280

47	Modeling Approach for DayType	281

47.1	Modeling Approach	281

47.2	Attributes	281

47.3	Linkage	282

48	Modeling Approach for LoadType	283

48.1	Modeling Approach	283

48.2	Attributes	283

48.3	Linkage	284

49	Modeling Approach for SubLoadArea	285

49.1	Attributes	285

49.2	Linkage	285

50	Modeling Approach for Season	286

50.1	Modeling Approach	286

50.2	Attributes	286

50.3	Linkage	287

51	Modeling PseudoTerminal	288

51.1	Modeling Approach	288

51.2	Attributes	288

51.3	Linkage	289

52	Modeling Planning Objects	290

52.1	Modeling Approach for Planning Area	290

52.1.1	Attributes	290

52.1.2	Linkage	291

52.2	Modeling Approach for Planning Zones	291

52.2.1	Attributes	292

52.2.2	Linkage	293

52.3	Modeling Approach for SubcontrolArea	293

52.3.1	Attributes	293

52.3.2	Linkage	294

53	Modeling VoltageMonitored	295

53.1	Modeling Approach	295

53.2	Attributes	295

53.3	Linkage	296

54	Modeling VoltageLimitset	297

54.1	Modeling Approach	297

54.2	Attributes	297

54.3	Linkage	298

55	Modeling VoltageLimit	299

55.1	Modeling Approach	299

55.2	Attributes	299

55.3	Linkage	300

56	MODELING STATIC VAR COMPENSATOR (SVC)	301

56.1	Modeling Approach for static var compensator (svc)	301

56.2 Attributes	303

56.3 Linkage	305

Appendix A - Validation Rules – Required Fields	306

Appendix B - Validation Rules – Required associations	316

Appendix C - Validation Rules – COMPLEX rules	319

Appendix D – Classes Not Allowed	343

Appendix E – Data Types Values	345

FIGURES

Figure 1 – Change Request Summary Screen

Figure 2 - Create New Project Display

Figure 3 - Edit Project Display

Figure 4 - Edit NOMCR Display

Figure 5 – CAMR Display and Categories

Figure 6 – MAGE Main Screen

Figure 7 – ERCOT Texas Network

Figure 8 - Create New Instance

Figure 9 – Create New Substation

Figure 10 –General Edit Instance Screen

Figure 11 – AA1 in Model Hierarchy

Figure 12 - Substation Attributes

Figure 13 - Substation Links

Figure 14 – AA1 Links Populated

Figure 15 - Rename Substation

Figure 16 – Delete Substation

Figure 17 - Breaker

Figure 18 – Breaker with Parent/Child Association

Figure 19 - Disconnector

Figure 20 - Disconnector with Parent/Child Association

Figure 21 –Shunt Compensator

Figure 22 – Series Compensator

Figure 23 - Location of Lines containing AC Line Segments

Figure 24 - Location of Lines containing Series Compensators

Figure 25 – AC Line Segment

Figure 26 - Substation

Figure 27 - Bay

Figure 28 - Information Model Manager Hierarchical View for SCADA Measurement

Figure 29 - Information Model Manager Hierarchical View of a Load with Multiple SCADA Measurements

Figure 30 - Information Model Manager Hierarchical View of a Calculation Definition

Figure 31 - Information Model Manager Hierarchical View of a Function Definition in the ERCOT Model

Figure 32 - Information Model Manager Hierarchical View of ICCP-Sourced Measurements in the ERCOT Model

Figure 33 - Information Model Manager Hierarchical View of SCADA Limits in the ERCOT Model

Figure 34 - Hierarchy for PowerTransformer

Figure 35 - Hierarchy for TransformerKluge

Figure 36 – Customer Load

Figure 37 – NonConform Load

Figure 38 – Conform Load Group

Figure 39 – NonConform Load Group

Figure 40 - Modeled RampRateCurves with Parent/Child Associations

Figure 41 – Curve Data

Figure 42 – Regular Time Point

Figure 43 - Terminal

Figure 44 – Connectivity Node

Figure 45 - Electrical Bus

Figure 46 – Connectivity Node Group

Figure 47 - Hierarchy for OwnerShareRating

Figure 48 - Hierarchy for BusBar Section

Figure 49 - Hierarchy for Dynamic Element

Figure 50 – Base Voltage

Figure 51 - Company

Figure 52 – SubGeographical Region

Figure 53 - Geographical Region

Figure 54 – Settlement Hub

Figure 55 – HubBus

Figure 56 – Pricing Vector

Figure 57 – Resource Node

Figure 58 – Settlement Load Zone

Figure 59 – Settlement NOI Load Zone

Figure 60 – Modeled Generating Unit with Parent/Child Association

Figure 61 – Modeled Generating Unit with Parent/Child Association

Figure 62 - Synchronous Machine

Figure 63 - Combined Cycle with Parent/Child Association

Figure 64 - Modeled Combined Cycle Plant with Parent/Child Association

Figure 65 – Modeled Logical Configuration with Parent/Child Association

Figure 66 – Configuration

Figure 67 - TransState

Figure 68 - Configuration Member

Figure 69 - ControllableLoadResource

Figure 70 - LoadResource

Figure 71 - OwnerShareLimits

Figure 72 - Ownership

Figure 73 - Operatorship

Figure 74 - DcTie

Figure 75 - Hierarchy of Contingencies

Figure 76 - Hierarchy for Contingency Elements

Figure 77 - Hierarchy for Contingency Groups

Figure 78 - Hierarchy for Contingency Group Member

Figure 79 - RAS

Figure 80 - Information Model Manager hierarchical view of a PrivateAreaNetwork as modeled in the ERCOT model

Figure 81 – Branch Group

Figure 82 – Branch Group Terminal

Figure 83 - EndCap

Figure 84 – Tie Corridor

Figure 85 – Hierarchy for Permission Area

Figure 86 - DayType

Figure 87 - LoadType

Figure 88 – SubLoad Area

Figure 89 - Season

Figure 90 – Pseudo Terminal

Figure 91 – Planning Area

Figure 92 – Planning Zone

Figure 93 – Subcontrol Area

Figure 94 - Hierarchy for VoltageMonitored

Figure 95 - Hierarchy for VoltageLimitset

Figure 96 - Hierarchy for VoltageLimit

Figure 97 - Static Var Compensator

# OVERVIEW

This document provides guidelines for the creation of Network Model changes that are to be submitted to ERCOT. The Network Model changes may be either created using the Information Model Management (Information Model Manager) editor component of the Network Model Management System (NMMS) or by submitting a file that is in Common Information Model (CIM) XML format.

DOCUMENT CHANGE CONTROL

This document serves as an interface design document for ERCOT and TSP network modeling systems.  For this reason, the document will be controlled in a manner that allows full transparency and vetting of proposed changes by ERCOT and TSPs.  Any proposed changes to the modeling guidelines will be posted as redlines to the current version of the document and discussed at the Network Data Support Working Group.   For sections related to Planning model changes, the SSWG will be asked to contribute in vetting of those proposed changes.  The current version of the Modeling Guideline will be kept on the NDWSG homepage.

## Document Organization

The document explains how to use the attributes, associations and classes defined in the ERCOT data dictionary. The classes are organized into two sections. Classes that can be modified by TSP’s and ERCOT and classes that can be modeled by ERCOT only. Also there are appendices showing the validation rules and the list of classes that are not allowed.

### Major Sections

The document is broken down into major sections that map to a single CIM package or a subsection of a package. This breaks down the document into logical subsections that cover areas such as generation, loads, etc.

The major sections are divided into two groups, those that are anticipated to be submitted by TSPs and ERCOT and those that are maintained by ERCOT only, but would appear in any ERCOT model files.

Introductory sections describing how to perform general modeling tasks are covered first before the detailed modeling approach subsections.

### Modeling Approach Subsection

These are documented, either class by class or as logical group in subsections titled “Modeling approach for <X>”. The modeling approach section will describe the approach a user should take for modeling this object type. It covers what associations and attributes are needed and how they should be defined. For more complex modeling concepts, it may include flowcharts or other diagrams necessary to explain the modeling approach.

### Attribute

All the attributes for each of the classes are listed in the Attributes subsection with the required attributes in Bold. QSE supplied classes and attributes are entered into NMMS through NOMCR’s created by ERCOT. Any classes supplied by QSE’s are documented under ERCOT.

### Linkage

Linkage subsection lists only the required links from the class that is being described, to other classes. Other associations are not shown in this document.

### Appendix A - Validation Rules for Required Fields

Appendix A lists all of the validation rules for attributes that must be defined for a specific class. It also lists any validation for attributes that must be within a specific value range.

### Appendix B - Validation Rules for Required Associations

Appendix B lists all of the validation rules for associations (links) that must be defined for a specific class.

### Appendix C – Complex Validation Rules

Appendix C lists all the validation rules that beyond the required attributes and links and could apply to more than one class at a time.  It also list all the validation rules that are more complex than required fields and range checks. These include validation rules that are conditional based upon certain conditions, involve associations with other attributes, and those that describe specific data relationships. The validation rule is explained descriptively and not in a formal language.

### Appendix D - Classes Not Allowed Subsection

If a particular CIM class is not used in the ERCOT systems and would potentially break the ERCOT model, the class will be listed in the subsection titled “Classes Not Allowed”. The complete lists of classes that are not used are listed in Appendix D.

### Appendix E – Enumeration Type Values

This section lists the definitions for each of the enumeration types used in the ERCOT model. For ex: the AnalogLimitNames used in the model include 15MIN, NRML, EMGY etc, the definitions for these are included in Appendix E.

### Validations

The appendices at the end of this document contain the complete listing of validation rules that run against each NMMS NOMCR submission. If any of these rules do not pass, the NOMCR will not be allowed to be submitted and the user must make the necessary corrections. These rules document any minimally required attributes, valid data ranges. The validation also ensures that the submission meets the cardinality defined in the latest ERCOT data dictionary.

If the imported CIM file fails validation due to not allowed classes the submitor can delete the invalid class using the ERCOT editor and have the NOMCR pass validation.

### Automatic Validation Performed by NMMS Based Upon Data Dictionary

The list of validation rules does not include the validation that is automatically performed by NMMS for links between objects. These links are validated based upon the data dictionary definition of the cardinality between the associated objects. There are two cardinality definitions that are validated; the first is the CardinalityRoleA and the second CardinalityRoleB. CardinalityRoleA defines the number of objects of the first Class that may exist related to the second Class.

For instance, in the data dictionary, the link between ThermalGeneratingUnit to CombinedCyclePlant CardinalityRoleA has a value of “0..n”. This means that there may be anything between 0 and n ThermalGeneratingUnits associated with a CombinedCyclePlant. The same association has a CardinalityRoleB of “0...1” which means that there may be between 0 and 1 CombinedCyclePlants associated with a ThermalGeneratingUnit.

This validation performed by NMMS follows the inheritance tree and the same validation is done for all objects that inherit from the object which has the cardinality definition.

For instance, in the data dictionary, a GeneratingUnit has a link to a ResourceNode that has a CardinalityRoleA defined as 1..n. This means that validation would be performed checking that there are one or more GeneratingUnits associated with a ResourceNode. It also means that validation would be performed for HydroGeneratingUnit, ThermalGeneratingUnit, WindGeneratingUnit and NuclearGeneratingUnit because these classes inherit from GeneratingUnit. Note that the cardinality is not defined explicitly for each inherited class.

### Further Clarification on Interpreting Data Dictionary and How Data is used in NMMS Information Model Manager

The rules used when dealing with associations/links may help with understanding these relationships. In general, the direction is defined in the data dictionary by the A and B (e.g. Class A and Class B, A --> B). The key, however, is that while the Information Model Manager UI uses the direction of the link to determine which side to display the links, the CIM/RDF export standard uses the cardinality to determine which side to export links.

Sample association definition:

| Class A | Cardinality A | Class B | Cardinality B | NMMS Label |
| --- | --- | --- | --- | --- |
| GeneratingUnit | 0..1 | DCTie | 1..1 | PartOfDCTie |

The NMMS Information Model Manager UI displays links in the direction A --> B.

By default the Information Model Manager UI instance editor will show links to instances of Class B on the Class A side. This means you will see links in the direction of A --> B. In the definition above, the Information Model Manager UI will show the link to DCTie on the "link tab" of the GeneratingUnit. If the user wishes to see the links in the opposite direction, they can do so by pressing the [Options] button and choosing the appropriate setting.

The NMMS RDF Export lists the links to the Class having lower cardinality under the Class having higher cardinality.

The CIM/RDF standard recommends that the side with the lower cardinality be exported under the side having higher cardinality. In case the cardinalities are equal, NMMS is implemented so that it export the links to Class B under the Class A instance.

This explains why the user sees an inconsistency between Information Model Manager UI and RDF export with the GeneratingUnit to DCTie relationship. Information Model Manager UI shows the links to DCTie (Class B) under the GeneratingUnit (Class A). However, RDF Export lists the links pointing to GeneratingUnit (cardinality 0-1) under the DCTie (cardinality 1-1).

The cardinality order is shown in the following table:

Cardinality Order (Least to Greatest)

0..1

1..1

0..n

1..n

Below is another example:

| Class A | Cardinality A | Class B | Cardinality B | NMMS Label |
| --- | --- | --- | --- | --- |
| ConductingEquipment | 0..n | BaseVoltage | 0..1 | BaseVoltage |
| SynchronousMachine | 0..1 | GeneratingUnit | 0..1 | GeneratingUnit |
| Reservoir | 0..1 | HydroPowerPlant | 0..n | Provides Water To(HydroPowerPlants) |

The links to BaseVoltage (lower cardinality) will be exported under ConductingEquipment (higher cardinality). Likewise, Information Model Manager UI will list the links to BaseVoltage (Class B) under the ConductingEquipment (Class A).

The links to GeneratingUnit (cardinality 0..1) will be exported under the SynchronousMachine (cardinality 0..1). Likewise, Information Model Manager UI will list the links to GeneratingUnit (Class B) under the SynchronousMachine (Class A). The links to Reservoir (lower cardinality) will be exported under HydroPowerPlant (higher cardinality). However, Information Model Manager UI will list the links to HydroPowerPlant (Class B) under the Reservoir (Class A).

### Relevant reference documents:

References will be added once they are available.

- ERCOT Data Dictionary.

- ERCOT Processes and Procedures.

- ERCOT Training documents.

# PROJECT TRACKER AND COORDINATOR

The Smart Grid Engineering Manager (SGEM) is the single entry point for Operations Model changes.  Modeling data and change requests are initially received in the SGEM, where each submission is tracked through any corrections, resubmission, validation, testing and review.

Upon login to the SGEM, the user will see the Change Request Summary screen shown below in Figure 1.  This screen is the base display for the SGEM and provides the user the ability to view, edit, and create both change requests and projects.

Figure 1 – Change Request Summary Screen

## SGEM PROJECT

An SGEM project is a container that is used to group similar change requests.  It is a requirement that every change request belong to a project, even if it is the only change request in the project.  To create a new project the user will click the “New Project and Model Change Request” button on the “Change Request Summary” screen.  The Create New Model Request screen will open in a new tab and is shown below in Figure 2. The user must designate the project as a NOMCR (Network Operations Model Change Request) project, a CAMR (Collaborate Action Model Request) project, or an ICR (Information Change Request) project.  Required fields are marked with “(required)” in gray.   For modeling purposes, we will only cover a NOMCR project.   After the required fields have been filled, the user can save the project.

Figure 2 - Create New Project Display

Once a change request is created and saved, the Edit Model Request screen can be opened by clicking on the Project ID on the Change Request Summary Screen.  The Edit Model Request screen is shown below in Figure 3.  Here the user can make changes to the change request, attach non-CIM files, view submission history, see action plans and request history and messages, or edit the existing change request.

Figure 3 - Edit Project Display

## Network Operations model change Request

Transmission Service Providers (TSPs) will submit all types of modeling changes using a Network Operations Model Change Request (NOMCR).  These changes include topological changes, limit/rating changes, telemetry mapping, and telemetry definitions.  The NOMCR process is defined in the Nodal Protocols and outlines submission deadlines, formats, and procedures.

A new NOMCR can be created from the Change Request Summary Screen.   Once a NOMCR is created, the Edit NOMCR screen shown in Figure 4 will appear.  All NOMCR information can be added/edited from this screen.

Figure 4 - Edit NOMCR Display

Once data is entered in required fields in the screen shown in Figure 2, the user can make changes to the model.  The most common method for making changes to the model is by clicking the Edit in Model Editor button on the screen, which will open the Information Model Manager.  Once model changes have been made in the Model And Graphics Editor, the NOMCR must be validated and submitted for the model changes to be applied to the Network Operations Model.  Validation is performed by clicking the Validate Model Change Request button if changes were made in the graphical editor, or the Import and Validate CIM File button if a CIM file was imported.  If the model changes pass validation, the NOMCR can be submitted by clicking the Submit button. If the model changes fail validation, an error message will appear under the Model Validation Results.  The validation errors can be viewed by clicking on the Validation Log button.  These errors must be corrected before the NOMCR can be submitted. If the submitted data does not pass the validation rules shown in Appendices, then the user is shown an error message on the screen. The user can then correct the error through the Information Model Manager screen and revalidate the data.

Another option for making changes to the model is importing a CIM XML file.   This can be done by clicking the Choose File button under the Import or Create and Validate Model Change section of the Edit Model Request Screen.  Once a CIM XML file is selected, the file is imported by clicking the Import and Validate CIM File button.  After the file is imported and validated successfully, the NOMCR can be submitted.

## COLLABORATIVE Action model Request

Collaborative Action Model Requests (CAMRs) are used for the Network Modeling group to assist with a modeling change.  Examples of these scenarios are contingencies, ownership, operatorship, etc.    A majority of CAMR requests will be proposed internally by ERCOT for generation, load resources, ICCP, etc.

CAMR information is entered into the SGEM through the Create a New Model Change Request display shown in the below figure.  The request will include information detailing a proposed change to the model.  If the proposal is acceptable, the Network Modelers will create the change in IMM and notify the requester it is available for review.  The submitter can view the changes in IMM but cannot alter them.  If the submitter finds the IMM changes acceptable the requester may submit the change as a change request.  This change request will be processed similar to a NOMCR would with the exception that any further changes to the model will require assistance from the ERCOT Network Modelers   Data for the CAMR is submitted to the SGEM by uploading a file with the necessary data for the model request through the Create a New Model Change Request  screen.  ERCOT will accept all file types and formats for upload.

Figure 5: CAMR Display and Categories

# Information Model Manager

Modeling and Graphic Editor (MAGE) is the user interface used to add and modify data in the Network Operations Model database.  MAGE can be accessed by clicking the “Launch Model Editor” button on the Edit NOMCR screen which opens up to the model information, as shown below in Figure 6.

Figure 6 - MAGE Main Screen

Market Participants will be responsible for maintaining only a small number of the instances that are seen in MAGE.  Majority of these instances will be under the path Network/Ercot Texas Network.  Figure 6 shows the full ERCOT Texas Network.  The ERCOT Texas Network includes substations, AC lines, and series compensators, all of which will be modeled by the Market Participants.

Figure 7 - ERCOT Texas Network

In order to find where in the model hierarchy a device is modeled it is best to look at the section on Substations.  Here we see that a Substation is modeled under a WeatherZone.  To create a new substation right-click on weather zone and select Add, as seen below in Figure 8.

## Create New Instance

In order to find where in the model hierarchy a device is modeled it is best to look at the section on Substations.  Here we see that a Substation is modeled under a WeatherZone.  To create a new substation right-click on weather zone and select New, as seen below in Figure 8.

The screen seen in Figure 9 will appear prompting the user to select an instance type.  Select substation and click the Create Instance button.

Figure 8 - Create New Instance

Figure 9 - Create New Substation

Once the substation is created the General Edit Instance screen shown below in Figure 10 will appear.  A name must be entered for the instance before the instance can be saved in the model.  Upon saving the new instance, the substation will appear in the model hierarchy.

Figure 10 - General Edit Instance Screen

The updated model hierarchy with new substation AA1 is shown below in Figure 11.

Figure 11 -  AA1 in Model Hierarchy

## Add Attributes

Once the substation has been created and saved, attributes for the substation must be entered into the required attribute fields.  Required attributes for each device can be found in a table in the device section.  Looking at the section on Substations, it is found that the required attributes for a substation are forNetwork and forScada.  These fields must be populated for the model changes to pass MAGE validation.  For some of the required attributes defaults are defined in the MAGE. If a default value is defined then the user need not submit any value for that attribute but it is important to verify ( if possible and known ) that the defaults are accurate and if they are not, then it should changed to the correct value. All the attributes that are of type “Boolean” have a default value defined in the system.

Many of the attribute fields are auto-populated by the MAGE.  Figure 12 shows the attributes screen for a newly created substation.  The auto-populated fields are populated in this figure. The MAGE will prevent data that is not of the correct data type or size from being saved in the model.

Figure 12 - Substation Attributes

## Add Links

As with attributes, for every device there are required link fields that must be populated for the model changes to pass the MAGE validation.  The required links for a Substation can be found in the table named required links in the Substation section of this document.  Looking at this table, it is found that the required links for a Substation are Ownership, Operatorship, and PermissionArea.  Figure 13 shows the links screen for a newly created Substation.

Figure 13 - Substation Links

Links cannot be manually entered into the value column.  All of the links must be added using the drag and drop method or the copy/paste method.  The path for all of the required links can be found in the Required Links table.  Using the links screen shown in Figure 13 above, navigate to the desired link in MAGE and left-click on the link holding down the mouse button.  Drag the selected link into the desired field and release the mouse button.  The value field will be populated with the link.  Save the change and move forward populating all of the required links in a similar manner.  The screen shot in Figure 14 shows the ERCOT_Operator and ERCOT_Owner links in the AA1 Operatorship and Ownership fields.  Links can also be copied and pasted by clicking the Right mouse button.

Figure 14 - AA1 Links Populated

## Rename Instance

To rename an instance right-click simply type the new name in the Name field of the instance and press Enter. The instance name will be updated immediately in the model hierarchy.

Figure 15 - Rename Substation

## Delete Instance

To delete an instance right-click on the instance and select Delete.  The warning message shown in Figure 16 will appear.  If the instance or children of the instance are modified in a later job, the user will not be able to delete the instance.

Figure 16 - Delete Substation

# Information Model Manager Tools

## Templates

## Auto Layout

# Modeling Breakers

## Modeling Approach

The ERCOT CIM model defines a Breaker as a mechanical switching device capable of making, carrying, and breaking currents under normal circuit conditions and also making, carrying for a specified time, and breaking currents under specified abnormal circuit conditions e.g. those of short circuit.  ERCOT shall develop the naming convention with the assistance of the TSP and the approval of TAC.

A Breaker is modeled under a VoltageLevel or a Bay in a Substation.  Two Terminals are modeled under the Breaker as connection points to the circuit.  Each terminal has a link to a connectivity node.    Naming requirements for this connectivity node are, the name length of the connectivity node should not exceed 4 characters and the name has to be unique within a substation.

Figure 17 - Breaker

SCADA values modeled under a Terminal provide the Open/Close status of the Breakers to the model.  Figure below shows a Breaker modeled in the Information Model Manager model hierarchy with parent/child associations labeled.    For more information on modeling SCADA values, refer to the section on ‘Modeling SCADA’.

Figure 18 – Breaker with Parent/Child Associations

## Attributes

The attributes for a Breaker are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Name | Name of the instance of this class | String |  | G010 |
| Teid | Transmission Element ID | Integer | Auto-populated |  |
| normalOpen | The attribute is used in cases when no Measurement for the status value is present. | Boolean | False |  |
| initiallyOpen | T = The initial breaker state for the online switching device model is open. | Boolean | False |  |
| inTransitTime | The transition time from open to close, in seconds. | Float | 0 |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Current Flow | Fault interrupting rating in amperes. | Float | None |  |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Enable Manual Switching | T = Enables manual switching capability for the device. | Boolean | True |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Description | Description of the object or instance. |  |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | None |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | PhaseCode | None |  |
| PSS/E ID | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String | None |  |
| recloseMaxAngle | Max Phase Angle for reclosing. 0 to 90 is allowed | Integer | -90 |  |
| Remove | The equipment is removed from the network. | Boolean | False |  |
| Remove Enable | The equipment can be removed from the network. | Boolean | False |  |
| RUC Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Switch On Count | The switch on count since the switch was last reset or initialized. | Integer | None |  |
| Switch On Date | The date and time when the switch was last switched on. | Date/Time | None |  |
| Switch Operation Over | Over Limit Violation Switch Operation (Open/Close). | Boolean | None |  |
| Switch Operation Under | Under Limit Violation Switch Operation (Open/Close). | Boolean | None |  |
| Switched By Schedule | T = The switch will follow a switching schedule to change state in the network applications. | Boolean | False |  |
| Trigger Network Sequence | T = The switch will trigger the realtime network application sequence when the switch changes state in SCADA. | Boolean | False |  |
| Trip Lockout | Lockout after trip. | Boolean | None |  |
| Zero Impedance Branch | Mark Switching devices that should be converted to Zero Impedance Branches in Connectivity Node to Bus Processing. | Boolean | False |  |
| Protect Under Action | Protect Under Action |  |  |  |
| contingencyComponent |  |  |  |  |
| futureTransition | T = Enable creation of alternate contingency defition that would capture a normalState transition on this switch. |  |  |  |
| protectLockoutAfterAction | Protect lockout after action. |  |  |  |
| protectOverAction | Protect over action. |  |  |  |

## Linkage

The required links for a Breaker are defined below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

# Modeling Disconnectors

## Modeling Approach

The ERCOT CIM model defines a Disconnector as manually operated or motor operated mechanical switching device used for changing the connections in a circuit, or for isolating a circuit or equipment from a source of power. It is required to open or close circuits when negligible current is broken or made.  ERCOT shall develop the naming convention with the assistance of the TSP and the approval of TAC.

A Disconnector is modeled under a VoltageLevel or a Bay in a Substation.  Two Terminals are modeled under the Disconnector as connection points to the circuit.  Each terminal has a link to a connectivity node.    Naming requirements for this connectivity node are, the name length of the connectivity node should not exceed 4 characters and the name has to be unique within a substation.

Figure 19 - Disconnector

SCADA values modeled under the Terminals provide the Open/Close status of the Disconnectors to the model.  Figure below shows a Disconnector modeled in the Information Model Manager model hierarchy with parent/child associations labeled.    For more information on modeling SCADA values, refer to the section on SCADA.

Figure 20 – Disconnector with Parent/Child Associations

## Attributes

The attributes for a Disconnector are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 |
| normalOpen | The attribute is used in cases when no Measurement for the status value is present. | Boolean | False |  |
| initiallyOpen | T = The initial breaker state for the online switching device model is open. | Boolean | False |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Enable Manual Switching | T = Enables manual switching capability for the device. | Boolean | True |  |
| Description | Description of the object or instance. |  |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Protect Under Action | Protect under action |  |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | PhaseCode | None |  |
| PSS/E ID | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String | None |  |
| recloseMaxAngle | Max Phase Angle for reclosing. 0 to 90 is allowed | Integer | -90 |  |
| Remove | The equipment is removed from the network. | Boolean | False |  |
| Remove Enable | The equipment can be removed from the network. | Boolean | False |  |
| RUC Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Switch On Count | The switch on count since the switch was last reset or initialized. | Integer | None |  |
| Switch On Date | The date and time when the switch was last switched on. | Date/Time | None |  |
| Switched By Schedule | T = The switch will follow a switching schedule to change state in the network applications. | Boolean | False |  |
| Trigger Network Sequence | T = The switch will trigger the realtime network application sequence when the switch changes state in SCADA. | Boolean | False |  |
| Zero Impedance Branch | Mark Switching devices that should be converted to Zero Impedance Branches in Connectivity Node to Bus Processing. | Boolean | False |  |
| Switch Operation Over | Over Limit Violation Switch Operation (Open/Close). |  |  |  |
| Switch Operation Under | Under Limit Violation Switch Operation (Open/Close). |  |  |  |
| Transmission Element ID | Transmission Element ID. |  |  |  |
| Trip Lockout | Lockout after trip. |  |  |  |
| contingencyComponent |  |  |  |  |
| futureTransition | T = Enable creation of alternate contingency defition that would capture a normalState transition on this switch. |  |  |  |
| protectLockoutAfterAction | Protect lockout after action. |  |  |  |
| protectOverAction | Protect over action. |  |  |  |

## Linkage

The required links for a Disconnector are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

# Modeling Shunt Compensators

## Modeling Approach

In the ERCOT CIM model, a ShuntCompensator is defined as a shunt capacitor or reactor or switchable bank of shunt capacitors or reactors. A section of a Shunt Compensator is an individual capacitor or reactor. Negative values for attributes mVArPerSection and nominalMVAr indicate that the Compensator is a Reactor. Postive values for attributes mVArPerSection and nominalMVAr indicate that the compensator is a Capacitor.  ERCOT shall develop the naming convention with the assistance of the TSP and the approval of TAC.
A Shunt Compensator is modeled under a VoltageLevel in a Substation.  One Terminal is modeled under the Shunt Compensator as a connection point to the circuit.  Figure below shows a Shunt Compensator modeled in the Information Model Manager model hierarchy with parent/child associations labeled.    For more information on modeling SCADA values, refer to the SCADA section of this document.

Figure 21 - Shunt Compensator

## Attributes

The attributes for a Shunt Compensator are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Name | Name of the instance of this class | String |  | CB_1 |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Automatic Voltage Regulation Delay | Time delay in seconds required for the device to be connected or disconnected by automatic voltage regulation (AVR). | Seconds | None |  |
| Automatic Voltage Regulation Enabled | T = Automatic voltage regulation enabled. | Boolean |  |  |
| Contingency_Element |  | Boolean |  |  |
| Control Mode | Shunt compensator control mode. | EnumShuntControlMode | None |  |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Description | Description of the object or instance. | String |  |  |
| Impedance - ShuntCompensator | The positive sequence impedance of the capacitor. | Impedance |  |  |
| Load Based Regulation Enabled | T = Load based voltage regulation enabled. | Boolean |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Maximum Sections - ShuntCompensator | For a capacitor bank, the maximum number of sections that may be switched in. | Counter | None |  |
| Maximum kV - ShuntCompensator | The maximum voltage at which the capacitor bank should operate. | Voltage | None |  |
| Minimum kV - ShuntCompensator | The minimum voltage at which the capacitor bank should operate. | Voltage | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| Nominal MVAr - ShuntCompensator | Nominal MVAr output of the capacitor bank at the nominal kV. This number should be positive. | Reactive Power | None |  |
| Nominal kV - ShuntCompensator | The nominal voltage at which the nominal MVAr was measured. This should normally be within 10% of the voltage at which the capacitor is connected to the network. | Voltage | None |  |
| Normal Sections - ShuntCompensator | For a capacitor bank, the normal number of sections switched in. This number should correspond to the Nominal MVAr. | Counter | None |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer | None |  |
| Optimized Step Switching | A boolean flag to designate a ShuntCompensator's block stepping capabilities. False = steps and blocks are switched on in input order, and off in reverse input order. True = steps and blocks are switched on and off such that the next highest (or lowest, as appropriate) total admittance is achieved. | Integer | None |  |
| PSS/E ID | Attribute will give IMM modelers control over the PSS/E ID that the Topology Processor uses to properly name units, loads, branches, and transformers. | String | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Percent Reactive Power Transfer | Percent reactive power transfer. | Reactive Power | None |  |
| Phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | PhaseCode | None |  |
| RUC Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Remove | The equipment is removed from the network. | Boolean | False |  |
| Remove Enable | The equipment can be removed from the network. | Boolean | False |  |
| Switch On Count - ShuntCompensator | The switch on count since the capacitor count was last reset or initialized. | Counter | None |  |
| Switch On Date - ShuntCompensator | The date and time when the capacitor bank was last switched on. | Absolute Date/Time | None |  |
| Switching Priority - ShuntCompensator | Switching priority number. | Integer | 1 | 12345 |
| Transmission Element ID | Transmission Element ID. | Integer |  |  |
| Voltage Sensitivity - ShuntCompensator | Voltage sensitivity required for the device to regulate the bus voltage, in per unit voltage/MVAr. | PU kV per MVAr |  |  |
| Y Per Section | For a capacitor bank, the admittance of each switchable section. Calculated using the MVAr per section and corrected for network voltage. | Admittance | None |  |
| contingencyComponent |  | Reactive Power | None |  |
| height | height |  |  |  |
| label height | label height |  |  |  |
| label width | label width |  |  |  |
| label x co-ordinate | label x co-ordinate |  |  |  |
| label y co-ordinate | label y co-ordinate |  |  |  |
| mVAr Per Section - ShuntCompensator | For a capacitor bank, the size in MVAr of each switchable section at the Nominal kV. |  |  |  |
| width | width |  |  |  |
| x co-ordinate | x co-ordinate |  |  |  |

## Linkage

The required links for a Shunt Compensator are defined in Table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

# Modeling Series Compensators

## Modeling Approach

In the ERCOT CIM model a SeriesCompensator is defined as a series capacitor, reactor, or AC transmission line without charging susceptance.  ERCOT shall develop the naming convention with the assistance of the TSP and the approval of TAC.

Although SeriesCompensators are contained within a Substation in the ERCOT model, they are not modeled under a Substation in the ERCOT model.  SeriesCompensators are modeled in the container named ERCOT-SeriesCompensator under ERCOT Texas Network, where they are grouped by voltage level.

Figure below shows a SeriesCompensator in the Information Model Manager model hierarchy.  SeriesCompensators must be modeled under a line and have two Terminals that serve as connection points to the circuit.  Analog SCADA values that provide limits and ratings for the SeriesCompensator are modeled under the Terminals.  These SCADA values can be modeled using multiple configurations.  More information on modeling SCADA values can be found in the SCADA section of this document.

SeriesCompensator cannot go between different voltage levels and should be contained within one Substation.

Figure 22 – Series Compensator

## Attributes

The attributes for a SeriesCompensator are shown in the table below

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 |
| 15 minute rating Max Shadow Price | States the 15 minute Max Shadow price for a SeriesCompensator. | DoubleFloat | 99999 |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Emergency Max Shadow Price | States the Emergency Max Shadow price for a SeriesCompensator. | DoubleFloat | 99999 |  |
| Latitude | Latitude coordinates. | Float | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | Float | None |  |
| Max Shadow Price | States the Max Shadow price | DoubleFloat | 99999 |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | PhaseCode | None |  |
| PSS/E ID | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String | None |  |
| Reactance | Positive sequence reactance | Float | None |  |
| Remove | The equipment is removed from the network. | Boolean | False |  |
| Remove Enable | The equipment can be removed from the network. | Boolean | False |  |
| Resistance | Positive sequence resistance | Float | None |  |
| RUC Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| height | height |  |  |  |
| label height | label height |  |  |  |
| label width | label width |  |  |  |
| label x co-ordinate | label x co-ordinate |  |  |  |
| label y co-ordinate | label y co-ordinate |  |  |  |
| width | width |  |  |  |
| x co-ordinate | x co-ordinate |  |  |  |
| y co-ordinate | y co-ordinate |  |  |  |

## Linkage

The required links for a SeriesCompensator are defined in Table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| BaseVoltage | BaseVoltage to which the SeriesCompensator belongs to. | Network/Base Voltage |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

# Modeling Lines

## Modeling Approach

This section describes the modeling of the Line container class as well as the ACLineSegment (transmission lines that connect two Substations) and SeriesCompensators (transmission lines that are fully contained within a substation) classes.  ERCOT shall develop the naming convention with the assistance of the TSP and the approval of TAC.  Each transmission line that operates in excess of 60 kV shall be modeled.

The Line class is modeled underneath a Geographical and Sub Geographical Region.  GeographicalRegions are used for convenient grouping of Texas Network.The Geographical Region in which the line will be created differs depending on what type of sub-classes the line will contain.  If the line is to contain an ACLineSegment, then the line must be in a Sub Geographical Region (named after the base voltage of the line) which is underneath the “ERCOT – AC Lines”.  Likewise, if the line will contain a SeriesCompensator, it must be created underneath both the “ERCOT – Series Compensators” geographical region and the sub geographical region corresponding to the line’s base voltage

Figure 23 – Location of Lines containing ACLineSegments

Figure 24 – Location of Lines containing SeriesCompensators

9.2 Attributes

Attributes for a Line are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 |
| teid | Transmission Element ID | Integer | Auto-populated |  |
| 15 minute rating Max Shadow Price | 15 minute rating Max Shadow price | DoubleFloat |  |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Emergency Max Shadow Price | Emergency Max Shadow price | DoubleFloat |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Max Shadow Price | Max shadow price | DoubleFloat |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |

## 9.3 Linkage

There are required links.

# Modeling ACLineSegment

## Modeling Approach

The ACLineSegment class represents an AC transmission line that connects two different Substations.  An ACLineSegment cannot be contained within a single Substation.  Additionally, an ACLineSegment must be underneath a Line instance and must have two Terminals.  ERCOT shall develop the naming convention with the assistance of the TSP and the approval of TAC.

ACLinesegment cannot go between different voltage levels.

Figure 25 - ACLineSegment

## Attributes

Attributes for an ACLineSegment are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 |
| 15 minute rating Max Shadow Price | 15 minute rating Max Shadow price | Double Float |  |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| b0ch | Zero sequence shunt (charging) susceptance, uniformly distributed, of the entire line section. | Double Float |  |  |
| bch | Positive sequence shunt (charging) susceptance, uniformly distributed, of the entire line section. | Double Float |  |  |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Bool |  |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Bool |  |  |
| Emergency Max Shadow Price | Emergency Max Shadow price | Double Float |  |  |
| g0ch | Zero sequence shunt (charging) conductance, uniformly distributed, of the entire line section. | Double Float |  |  |
| gch | Positive sequence shunt (charging) conductance, uniformly distributed, of the entire line section. | Double Float |  |  |
| Latitude | Latitude coordinates. | Float | None |  |
| length | Segment length for calculating line section capabilities (long length units). | Float |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | Float | None |  |
| Max Shadow Price | Max shadow price | Double Float |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Long Int | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | String |  |  |
| PSS/E | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly name units, loads, branches, and transformers. | String |  |  |
| r | Positive sequence series resistance of the entire line section. | Double Float |  |  |
| R0 | Zero sequence series resistance of the entire line section. | Double Float |  |  |
| Remove | The equipment is removed from the network. | Bool |  |  |
| Remove Enable | The equipment can be removed from the network in the EMS. | Bool |  |  |
| RUC Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Bool |  |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Bool |  |  |
| teid | Transmission Element ID | Integer | Auto-populated |  |
| x | Positive sequence series reactance of the entire line section. | Double Float |  |  |
| X0 | Zero sequence series reactance of the entire line section. | Double Float |  |  |
| height | height |  |  |  |
| label height | label height |  |  |  |
| label width | label width |  |  |  |
| label x co-ordinate | label x co-ordinate |  |  |  |
| label y co-ordinate | label y co-ordinate |  |  |  |
| width | width |  |  |  |
| x co-ordinate | x co-ordinate |  |  |  |
| y co-ordinate | y co-ordinate |  |  |  |

## Linkage

The required links for ACLineSegment are defined in Table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| BaseVoltage | BaseVoltage to which this ACLineSegment belongs | Network/Base Voltage |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

# Modeling Substation

## Modeling Approach

The ERCOT CIM model defines a Substation as collection of equipment for purposes other than generation or utilization, through which electric energy in bulk is passed for the purposes of switching or modifying its characteristics.  ERCOT shall develop the naming convention with the assistance of the TSP and the approval of TAC.

A Substation is modeled under a SubGeographicalRegion.  VoltageLevels, Transformers and Device types are modeled under the Substation along with generic equipment.  The Substation serves as a container for these instances.  Figure below shows a Substation modeled in the Information Model Manager model hierarchy with parent/child associations labeled.    For more information on modeling VoltageLevels, Device Types, and PowerTransformers please see relevant sections.

Figure 26 – Substation

## Attributes

The attributes for a Substation are shown in the table below.

| Attribute | Description | Data Type | Default value | Sample data |
| --- | --- | --- | --- | --- |
| Name | Name of the instance of this class | String |  | CB_1 |
| Abnormal For Alarm | This flag is used to cause alarm messages for abnormals to have their date/time displayed in black in the Alarm displays instead of red (assuming the HABITAT FG element set). | Boolean | False |  |
| bnormal For SCADA | Setting this flag to true does not affect Alarm displays, but forces the record to appear Normal on SCADA displays. | Boolean | False |  |
| Alarm Location | Alarm location, must match LOC.ID_LOC in the Alarm database. | String |  |  |
| Alias Name | Free text name of the object or instance. | String |  |  |
| Audible Tone | A flag indicating that notifications of alarm conditions via audible tones and horns will be suppressed. | Boolean | False |  |
| County | County | String |  |  |
| Description | Description of the object or instance. | String |  | Salty Creek Plant |
| Inhibit Abnormal For Alarm | Permanently Inhibit the flag of abnormalForAlarm . | Boolean | False |  |
| Inhibit Abnormal For SCADA | Permanently Inhibit the flag of abnormalForSCADA. | Boolean | False |  |
| Inhibit Audible Tone | Permanently Inhibit the flag of audibleTone. | Boolean | False |  |
| Inhibit Logging and Alarm List | Permanently Inhibit the flag of loggingAndAlarmList. | Boolean | False |  |
| Inhibit Unacknowledged Alarm List | Permanently Inhibit the flag of unacknowledgedAlarmList. | Boolean | False |  |
| Initially Inhibit | A flag indicating that when the system first comes online, alarm indications for this SCADA entiry will initially be inhibited. | Boolean | False |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Logging and Alarm List | A flag indicating that SCADA will issue neither an alarm nor an event. Therefore, entries will appear in the neither the alarm list nor the event logs. | Boolean | False |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |  |
| Override Default Inhibit Definition | A flag indicating that that the Operator Inhibit Definition overrides the Global Default Inhibit. | Boolean | False |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Transmission Element ID | Transmission Element ID. | Integer |  |  |
| Unacknowledged Alarm List | A flag ndicating that SCADA will issue an event to the event log, but will not issue unacknowledged alarm indications to the alarm list. | Boolean | False |  |
| contingencyComponent |  | Boolean |  |  |
| for Network | This flag is used to indicate this substation is used by Network application. | Boolean | True |  |
| for Scada | This flag is used to indicate this substation is used by SCADA application. | Boolean | True |  |

## Linkage

Below are the required links for a Substation.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

Note:  Even though an entity might own the substation at 100 percent there might be equipment located in the station that the entity might not own, such as a switch.

# Modeling Bay

## Modeling Approach

The ERCOT CIM model defines a Bay as a collection of Breakers and Disconnectors within a given VoltageLevel.  A Bay is modeled under a VoltageLevel. Only Breakers and Disconnectors can be modeled under a Bay.   ERCOT shall develop the naming convention with the assistance of the TSP and the approval of TAC.

Figure 27 - Bay

## Attributes

The attributes for a Bay are shown in the table below.

| Attribute | Description | Data Type | Default value | Sample data |
| --- | --- | --- | --- | --- |
| Name | Name of the instance of this class | String |  | CB_1 |
| Alias Name | Free text name of the object or instance. | String |  |  |
| Breaker Configuration | Breaker configuration. | Breakerconfiguration |  |  |
| Busbar Configuration | Busbar configuration. | BusbarConfiguration |  |  |
| Description | Description of the object or instance. | String |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Transmission Element ID | Transmission Element ID. | Integer |  |  |
| bay Energy Measurement Flag | Indicates the presence/absence of kWh/kvarh measurements. | Boolean | False |  |
| bay Power Measurement Flag | Indicates the presence/absence of MW/MVAr measurements. | Boolean | False |  |
| contingencyComponent |  | Boolean |  |  |

## Linkage

The required links for a Bay are defined below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

# Modeling SCADA

## Modeling Approach for SCADA

This section describes the approach for modeling SCADA in the ERCOT CIM model. SCADA stands for Supervisory Control and Data Acquisition. It refers to the centralized systems which monitor and control entire sites, or complexes of systems spread over large areas. The control actions are performed automatically by the remote terminal units or by programming logic controllers.

In the ERCOT CIM model Analog and Discrete measurements are created under equipment’s Terminal. A Terminal association ascertains the ConnectivityNode in the network model that closely represents location of the physical measuring device in the field. In addition to ConnectivityNode, it is useful to know equipment in the network model, this measurement data is being supplied for. In case of most measurements this equipment is usually the parent of identified terminal.

Knowledge of the medium being utilized to transfer the measured data to ERCOT is equally essential. Most of the measurements in the CIM model use ICCP, SCADA RTUs or Calculation as the media for data transfer. The CIM model identifies the transfer medium for a measurement as its MeasurementValueSource. The subtle differences in modeling Analog and Discrete measurements from each of these MeasurementValueSources are outlined in this section.

The CIM classes, MeasurementLocation, MeasurementGroup, Analog, Discrete, AnalogValue and DiscreteValue are mainly utilized for defining the SCADA measurement components in the network model. Figure below shows the modeling of MVAR telemetry for a load as modeled in the Information Model Manager hierarchy. As can be seen in figure, an Analog named MVAR is modeled under the Load’s Terminal.   An AnalogValue MVAR is modeled under the MVAR Analog. Both the Analog and AnalogValue instances are together used to define various SCADA specific features of the MVAR measurement. A MeasurementLocation is visible be modeled under the load, indicating the presence of measurements at the load. A MeasurementGroup is modeled under the MeasurementLocation. The following sections describe the modeling of each of these classes in detail.

Figure 28 - Information Model Manager Hierarchical View for SCADA Measurement

### Modeling Approach for MeasurementLocation

A MeasurementLocation is used to identify equipment in the network model which is being monitored using Analog and Discrete measurements. This monitored equipment can be of type Breaker, Busbarsection, Synchronousmachine, Transfomerwinding etc.

In the figure above a MeasurementLocation is created under the load at which the MVAR flow measurements are being monitored. A MeasurementLocation must have the exact same name as that of its parent device. In the ERCOT CIM model, a MeasurementLocation also holds the SCADA device-type for its parent device, but for ACLineSegments and SeriesCompensators the grandparent of device name should be used. With the exception of Lines and PowerTransformers, any equipment in the ERCOT network model must have only one child MeasurementLocation of a specific device-type. In case of Lines/PowerTransformers a maximum of two MeasurementLocation children may be present, one each of each end/winding of the Line/Transformer.

#### Linkage

The required links for a MeasurementLocation are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| MeasurementLocationHasTypeof(DeviceTypeName) | Identifies the device type at which the measurement is being defined | Other Orphans/DeviceTypeName |
| MeasurementLocationHas(PermissionArea) | Identifies the permission area | List_Information/Permission Areas/ERCOT |

### Modeling Approach for a MeasurementGroup

The ERCOT data dictionary defines a MeasurementGroup as a group of related Analog or Discrete measurements. In the ERCOT CIM model, MeasurementGroups are created under MeasurementLocations. Analog and Discrete measurements that are sourced from SCADA RTU’s and/or ICCP are collected together by associations to MeasurementGroup. MeasurementGroups that are under the same parent MeasurementLocation must have unique names, no longer than 4 characters. An example of a MeasurementGroup ANLG as visible in the Information Model Manager Hierarchy view is shown in the below figure. Also the AnalogValues that are sourced from ICCP, both reference ANLG.

Figure 29 - Information Model Manager Hierarchical View of a Load with Multiple SCADA Measurements

#### Attributes

The attributes for a MeasurementGroup are shown in the table below.

| Attribute | Description | Data Type | DefaultValue | Sample Data |
| --- | --- | --- | --- | --- |
| Name | Name of the instance of this class | String |  | CB_1 |
| Alias Name | Free text name of the object or instance. | String | None | XYZ |
| Description | Description of the object or instance. | String | None | XYZ |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | 323 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ |
| Zonal Attribute | Temp Attribute to support dual SCADA feeds. | Boolean | False | False |
| buffer Period | Number of seconds to wait for a cluster of exceptions to be reported. | Short Integer | None | 3 |
| grace Period | Number of seconds to wait before declaring an expected scan "late". | Short Integer | None | 5 |
| integrity Period | Number of seconds between integrity scans. | Short Integer | None | 3 |
| scan Period | Number of seconds between scans. | Short Integer | None | 4 |

### Modeling Approach for a Calculation

A Calculation is a type of MeasurementValueSource for Analog and Discrete measurements in the network model. Calculations are usually defined when a physical quantity desired to be monitored at a particular equipment isn’t directly measured but can be computed using one or more direct/derived measurements. Calculations may be modeled both by TSPs and ERCOT in the network model.

For MVA calculations, ERCOT has supplied a template for TSPs to model MVA calculations as required when MW and MVAr telemetry is provided.  In cases where MW and MVAr telemetry is not available, TSPs will need to model a MVA measurement with Ratings, but no site linkage. While model ownership of the MVA calculations will be reflected as being with the TSPs, ERCOT takes full responsibility for their content, application, and use.

In the ERCOT CIM model, a Calculation is modeled under a MeasurementLocation using one or many MeasurementArguments and/or ConstantArguments.  An example of a Calculation CALC is visible in the hierarchy view in the figure. Note that, all Calculations under the same parent MeasurementLocation should have unique names, no longer than 4 characters as well.

Figure 30 - Information Model Manager Hierarchical View of a Calculation Definition

#### Attributes

The attributes for a Calculation are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| Name | Name of the instance of this class | String |  | CB_1 |
| Alias Name | Free text name of the object or instance. | String | None | XYZ |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | 232 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ |
| Type | Type | String | None | XYZ |
| Zonal Attribute | Temp Attribute to support dual SCADA feeds. | Boolean | False | False |

#### Linkage

The required links for a Calculation are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| CalculationUsesFunction | Identifies the function used to do the Calculation | List_Information/Functions |

### Modeling Approach for MeasurementArgument

When creating Calculations in the ERCOT CIM model, input/output parameters that involve Analog and Discrete measurements are defined using instances of type MeasurementArgument. Each MeasurementArgument must be associated to a single SCADA AnalogValue and/or SCADA DiscreteValue in the model. Note that the output parameter of a Calculation should always be MeasurementArgument whereas not all input parameters of a Calculation need be of type MeasurementArgument.

As mentioned in earlier sections, MeasurementArguments are created under a Calculation. The Calculation CALC shown in the hierarchical view in figure has two MeasurementArguments, namely CBMW and LDMW as its input/output parameters.

#### Attributes

The attributes for a MeasurementArgument are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| Name | Name of the instance of this class | String |  | CB_1 |
| Alias Name | Free text name of the object or instance. | String | None | XYZ |
| Description | Description of the object or instance. | String | None | XYZ |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | Boolean | False | False |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | 343 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ |
| Reference Flag | The Boolean flag to indicate this arguement is a reference. | Boolean | False | False |
| Reference Name | If this is a Reference, name for the reference. | String | None | XYZ |
| Zonal Attribute | Temporary attribute to support dual SCADA feeds. | Boolean | False | False |
| Trigger Flag | This reference record is an input to a calculation and triggers that calculation when referenced Measurement record changes. | Boolean | False | False |

#### Linkage

The required links for a MeasurementArgument are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| CalculationArgumentAssignedToFunctionArgument | Identifies to which function argument of the function it belongs to. | List_Information/Functions/ |
| MeasurementArgumentMappedToMeasurementValue | Identifies a MeasurementValue that is acting as an input/output feed to/for this MeasurementArgument. |  |

### Modeling Approach for ConstantArgument

In addition to MeasurementArguments, the ERCOT data dictionary allows scalar inputs parameters to be defined for a Calculation using instances of type ConstantArguments. Similar to MeasurementArgument modeling, ConstantArguments are modeled under a Calculation as well. ConstantArguments can only serve as input parameters of a Calculation. The Information Model Manager hierarchical view for the Calculation CALC in figure shows one such CalculationArgument, namely 1NEG as its input.

ERCOT recognizes that the TSP modeled calculations may not need ConstantArguments but from the point of completeness, modeling of ConstantArguments is being described here.

#### Attributes

The attributes for a ConstantArgument are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| Name | Name of the instance of this class | String |  | CB_1 |
| Alias Name | Free text name of the object or instance. | String | None | XYZ |
| Description | Description of the object or instance | String | None | XYZ |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | 232 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ |
| Reference Flag | The Boolean flag to indicate this arguement is a reference. | Boolean | False | False |
| Reference Name | If this is a Reference, name for the reference. | String | None | XYZ |
| Scalar Value | The scalar constant I/O parameter for a SCADA calculation. | Float | None | 123 |
| Zonal Attribute | Temporary attribute to support dual SCADA feeds. | Boolean | False | False |

#### Linkage

The required links for a ConstantArgument are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| CalculationArgumentAssignedTo(FunctionArgument) | Identifies to which function argument of the function it belongs to. | List_Information/Function/ FuctionArgument |
| ConstantArgumentMappedToConstantValue | Identifies a ConstantValue that is acting as an input/output feed to/for this ConstantArgument. |  |

### Modeling Function and FunctionArguments

In the ERCOT CIM model Functions are utilized to define commonly use mathematical computations pertaining to SCADA measurements. Functions get referenced when defining Calculations in the model. Some of the function definitions available for re-use in the ERCOT CIM model include absolute value (ABS), addition (ADD3), average (AVG1), bestOf (BEST), division (DIV), multiplication (MULT) and MVA-computation (MVA1). A list of all available Functions in the model can be viewed in the Information Model Manager hierarchy at the path List_Information/Functions.

ERCOT will maintain (add/modify/delete) Functions and FunctionArguments in the network model.

The CIM model uses FunctionArguments to define the characteristic features of the input and output parameters of a function.  The attributes ReadFlag and WriteFlag for a FunctionArgument are of special importance. As the names suggests ReadFlag and WriteFlag help define the I/O nature of the parameter, i.e. the parameter will be considered as an input to the function when it’s ReadFlag = True and WriteFlag = False. Similarly the variant will be considered as an output to the Function when it’s ReadFlag = True and WriteFlag = False. In the CIM model FunctionArguments get referenced when defining MeasurementArguments and/or ConstantArguments for a Calculation.

Figure 31 - Information Model Manager Hierarchical View of a Function Definition in the ERCOT Model

An example of the function ADD is visible in the figure. This function has three FunctionArguments under it namely, ARG1, ARG2 and ARG3. When defining Calculations in the model the total number of input/output parameters (MeasurementArguments and/or ConstantArguments) is limited by the total number of FunctionArguments defined in the referenced Function. Thus if a Calculation is to be modeled by referencing the Function ADD, it must have 3 input/output parameters (MeasurementArguments and/or ConstantArguments) modeled as its children.

### Modeling Approach for Analog and Discrete Measurement

The ERCOT data dictionary defines Analog and/or Discrete measurement as any measured, calculated or non-measured quantity. Any piece of equipment in the model can have measurements, e.g. a Substation may have temperature measurements and door open indications, a Transformer may have oil temperature and tank pressure measurements, a bay may contain a number of power flow measurements and a breaker may contain a switch status measurement.

As mentioned earlier, in the ERCOT model Analog and Discrete measurements are created under a terminal. The choice of a measurement is dependent on the nature of the physical quantity being measured. For example, MW/MVAR/MVA measurements will be identified as Analog measurement in the ERCOT model, whereas Status-like binary-logic based measurements will be classified as Discrete measurements in the ERCOT model.

#### Attributes

The attributes for Analog and Discrete measurements are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data | Analog | Discrete |
| --- | --- | --- | --- | --- | --- | --- |
| Name | Name of the instance of this class | String |  | CB_1 | X | X |
| Alias Name | Free text name of the object or instance. | String | None | XYZ | X | X |
| Description | Description of the object or instance. | String | None | XYZ | X | X |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ | X | X |
| Maximum Value | Normal value range maximum for any of the MeasurementValue.values. Used for scaling, e.g. in bar graphs or of telemetered raw values. | Float | None | 23 | X | X |
| Minimum Value | Normal value range minimum for any of the MeasurementValue.values. Used for scaling, e.g. in bar graphs or of telemetered raw values. | Float | None | 34 | X | X |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | String | 234 | X | X |
| Normal Value | Normal measurement value, e.g., used for percentage calculations. | Float | None | 34 | X | X |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ | X | X |
| Positive Flow In | If true then this measurement is a MW, MVAR or AMPS with the convention that a positive value measured at the Terminal means power is flowing into the related PowerSystemResource. | Boolean | False | False | X |  |
| Scan Rate | ICCP scan rate used for the measurement. | Float | False | 343 | X | X |
| Transmission Element ID | Transmission Element ID. | Long Integer | Auto Populated | 343 | X | X |
| Zonal Attribute | Temp Attribute to support dual SCADA feeds. | Boolean | False | False | X | X |
| for Network | If true then this measurement is only for network monitoring. | Boolean | False | False | X |  |

#### Linkage

The required links for Analog and Discrete measurements are defined in the table below

| Link Name | Description | Path Name | Analog | Discrete |
| --- | --- | --- | --- | --- |
| Measurements MeasurementType | Specify the type of measurement ex. threephasepower, threephasereactivepower, threephaseactivepower, linecurrent, etc. | List_Information/MeasurementType | X | X |
| Measurements Unit | Dimension of the telemetered value. Ex. MVA, MW, MVAr, A, etc. | List_Information/Units | X | X |
| Contains_sMeasurements PowerSystemResource | The device identified in this association is exactly same as the parent device of the associated terminal. | Network/ERCOTTexasNetwork/ERCOTSubstations/WeatherZone/Substation/VoltageLevel/Device | X | X |
| Measurementy Ownership | The operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. | Network/Companies | X | X |
| Measurement Operatorship | The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies | X | X |

### Modeling Approach for SCADA AnalogValue and DiscreteValue

The ERCOT data dictionary utilizes AnalogValues and/or DiscreteValues to define current state for the Analog and/or Discrete measurement. A state value is an instance of a measurement from a specific source. Analog and/or Discrete measurements can be associated with many state values, each representing a different source for the measurement.

In the ERCOT CIM model AnalogValues and/or DiscreteValues are used to define inputs for the EMS SCADA database or the ICCP database by variations in the linkages of AnalogValue and/or DiscreteValue. For simplicity the prior type of AnalogValue and/or DiscreteValue is referred as SCADA MeasurementValue and the later is referred as ICCP MeasurementValue this section onwards. The current section will describe the modeling subtleties of SCADA measurementvalues whereas the ICCP measurementvalues will be covered in the following sections.

All TSP entered measurements will be ICCP sourced. ERCOT Is requesting TSPs to model SCADA maps along with ICCP till an automatic process is defined to add the SCADA counterparts.

All Analog and/or Discrete measurements irrespective of their MeasurementValueSource should have a SCADA MeasurementValue of appropriate type created under it. The hierarchical view in the figure shows the AnalogValue MVAR_SValue created under the Analog MVAR.

#### Attributes

The attributes for a SCADA AnalogValues and DiscreteValues are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data | Analog | Discrete |
| --- | --- | --- | --- | --- | --- | --- |
| Name | Name of the instance of this class | String |  | CB_1 |  |  |
| Abnormal Alarm Delay Time | The number of seconds for the alarm to remain on the persistance alarm list before toning/alarming because it remained in the violated state. | Long Integer | None | 23 | X | X |
| Abnormal For Alarm | This flag is used to cause alarm messages for abnormals to have their date/time displayed in black in the Alarm displays instead of red (assuming the HABITAT FG element set). | Boolean | False | False | X | X |
| Abnormal For SCADA | Setting this flag to true does not affect Alarm displays, but forces the record to appear Normal on SCADA displays. | Boolean | False | False | X | X |
| Alias Name | Free text name of the object or instance. | String | None | XYZ | X | X |
| Allow Control from Foreign Sites | True = Another site may issue a control on this point. |  | False | False |  | X |
| Allow Multiple Raise or Lower | True = Multiple Tap Raise and Lower commands may be issued consecutively without re-selecting the... |  | False | False |  | X |
| Allow SELECT Step | True = a separate SELECT action is allowed (but not required) prior to the supervisory control action. | Boolean | False | False | X | X |
| Audible Tone | A flag indicating that notifications of alarm conditions via audible tones and horns will be suppressed. | Boolean | False | False | X | X |
| Auto Ack and Delete Alarms | Automatically acknowledge and delete alarms if the Analog is manually entered or successfully controlled by the operator to a normal state. | Boolean | False | False | X | X |
| Auto Acknowledge | When set to true, this flag specifies that alarms will be automatically acknowledged on return to normal. This will only occur if the Alarm Return to Violations flag is not set on the Limit Names table. | Boolean | False | False | X | X |
| Block via Primary Site | Block Value and Quality update via Primary Site: Do not allow update from the primary site. | Boolean | False | False | X | X |
| Block via Secondary Site | Block Value and Quality update via Secondary Site: Do not allow update from the secondary site. | Boolean | False | False | X | X |
| byPass | When set to true, this flag specifies allowing bypass entry of Suspect values if telemetered from a remote site or SCADA Front End. | Boolean | False | False | X | X |
| Component Status | True when value represents status of communication path component. | Boolean | False | False | X | X |
| Control Demand Scan | True = Issues a demand scan request to the RTU at a configurable number of seconds after any successful control requests are issued. This feature is primarily used by measurements with a slow scan rate to provide more timely feedback on the success or failure of the control operation. | Boolean | False | False | X | X |
| Control MMI Sequence | true = override any default settings. | Boolean | False | False | X |  |
| Description | Description of the object or instance. | String | None | XYZ | X | X |
| Enable Auto SE Replacement | True = Allow automatic State Estimator replacement. Automatically substitute the display value with a good quality state estimated value if the quality of the telemetered analog becomes SUSPECT. | Boolean | False | False | X |  |
| Feedback Analog | True = The Analog Name which is configured to provide feedback of the associated analog value for control completion checks of Raise/Lower supervisory controls. The chosen Analog must be modeled under the same Device as the controlling Point record. This field is optional. |  | None | XYZ |  | X |
| from Calculation | Value is from calculation. | Boolean | False | False | X | X |
| From External Program | When set to true, this flag specifies the source of the data is an external program. | Boolean | False | False | X | X |
| from Manual Entry | Value is from manual entry. | Boolean | False | False | X | X |
| from Remote | Value is from remote. | Boolean | False | False | X | X |
| From State Estimator | When set to true, this flag specifies the source of the data is state estimator. | Boolean | False | False | X |  |
| General Read Access | This flag is used in conjuction with MeasurementValue_ReadBy association to identify read privileges on a MeasurementValue. When MeasurementValue_ReadBy is non-null the value of this boolean will not matter, i.e. only the MeasurementValueSource identified by the association will have read permissions on the model. When MeasurementValue_ReadBy is null, a true value on this boolean will be interpreted as read privileges being available to all MeasurementValueSource, and a false value on this boolean will be interpreted as read privileges being not available to any MeasurementValueSource. | Boolean |  |  | X | X |
| HABC Name | Connection ID of value using HABConnect. | String | None | False | X | X |
| Historical Recording Deadband | Threshold (percentage currently recorded analog data) above which additional data points should not retained. | Double Float | 0 | 45.6 | X |  |
| ICCP Data Set Period | ICCP data set period used for the measurement. | Double Float | 0 | 45.6 |  | X |
| Inhibit Abnormal For Alarm | Permanently Inhibit the flag of abnormalForAlarm. | Boolean | False | False | X | X |
| Inhibit Abnormal For SCADA | Permanently Inhibit the flag of abnormalForSCADA. | Boolean | False | False | X | X |
| Inhibit Audible Tone | Permanently Inhibit the flag of audibleTone. | Boolean | False | False | X | X |
| Inhibit Logging and Alarm List | Permanently Inhibit the flag of loggingAndAlarmList. | Boolean | False | False | X | X |
| Inhibit Unacknowledged Alarm List | Permanently Inhibit the flag of unacknowledgedAlarmList. | Boolean | False | False | X | X |
| Initially Inhibit | A flag indicating that when the system first comes online, alarm indications for this SCADA entry will initially be inhibited. | Boolean | False | False | X | X |
| Invert Analog Via Secondary Site | True = Negate the analog value when received from the secondary site. | Boolean | False | False | X |  |
| Invert Extended Status via ISD | True = The extended status bit (XIS) will be inverted when received from the primary site. |  | False | False |  | X |
| Invert Extended Status Via Sec Site | True = The extended status bit (XIS) will be inverted when received from the secondary site. |  | False | False |  | X |
| Invert Sign | When set to true, this flag specifies that the analog value, as received by SCADA, is inverted before using in other applications. | Boolean | False | False | X |  |
| Invert Status | True = The status point value, as received by SCADA, is inverted before using in other applications. |  | False | False |  | X |
| Invert Status Bit Received Via ISD | True = The status bit (SIS) will be inverted when received from the primary site. |  | False | False |  | X |
| Invert Status Bit Received Via Sec Site | True = The status bit (SIS) will be inverted when received from the secondary site. |  | False | False |  | X |
| ISD Name | Dollar-separacted SCADA Composite ID. | String | None | False | X | X |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ | X | X |
| Log for Control Issued | True = Controls issued on this point will be logged in the system activity log. |  | False | False |  | X |
| Logging and Alarm List | Permanently Inhibit the flag of loggingAndAlarmList. | Boolean | False | False | X | X |
| Mapped In OAG | T = This data-point is also represented in the OAG model as a data item (designated member of a data packet). | Boolean | False | False | X | X |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | XYZ | X | X |
| Momentary Change Detection | True = a momentary change detection status will be returned. Momentary change detection status informs the computer of changes that occur between scans. |  | False | False |  | X |
| Negate Value Received from ISD | When set to true, this flag specifies that the polarity of the analog value received via ISD will be switched. | Boolean | False | False | X |  |
| Negative Uni-Polar Clamping | True = positive values will be forced (clamped) to zero before updating into the database. | Boolean | False | False | X |  |
| No ISD Download | True = Even though the Point is associated with a remote site, the Point will not be included in the Intersite Data download request for status values to the remote site. The remote site is only used for determining which site to send Supervisory Controls to. |  | False | False |  | X |
| No Warning if Hanging | Don't issue warning message if a lone Topology Node is defined, which is not defined on any other record within the Substation. |  | False | False |  | X |
| Not In Service | flag indicating not in service. | Boolean | False | False | X | X |
| Override Default Inhibit Definition | A flag indicating that that the Operator Inhibit Definition overrides the Global Default Inhibit. | Boolean | False | False | X | X |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ | X | X |
| Peak Data | When set to true, this flag specifies that the Peak Data Processing task will sample this analog. | Boolean | False | False | X |  |
| Positive Uni-Polar Clamping | True = negative values will be forced (clamped) to zero before updating into the database. | Boolean | False | False | X |  |
| Record Historical Data | When set to true, this flag specifies that state changes on the analog are recorded in the historical data review file. | Boolean | False | False | X | X |
| Remote Site Normally Calculated | Remote site normally calculated. | Boolean | False | False | X | X |
| Remote Site Normally Estimated | Remote site normally estimated. | Boolean | False | False | X | X |
| Remote Site Normally Manually Entered | Remote site normally manually entered. | Boolean | False | False | X | X |
| Remote Site Normally Telemetered | Remote site normally telemetered. | Boolean | False | False | X | X |
| Require EXECUTE Step | True = a supervisory control action is not initiated when a control action is received, and must wait for an additional EXECUTE action. | Boolean | False | False | X | X |
| Require SELECT Step | True = a separate SELECT action is required before a supervisory control action. | Boolean | False | False | X | X |
| Return to Normal Alarm Delay Time | The number of seconds for the alarm to remain on the persistance alarm list before toning/alarming because it remained in the normal state. | Boolean | False | False | X | X |
| scanRate |  | Double Float | 0 | 3 | X | X |
| SE Deadband | Display values of good quality which are different than a good quality state-estimated value by more than this amount are considered anomalous, and automatically substituted with the state-estimated value, if the global Automatic State-Estimator Replacement function is enabled. | Boolean | False | False | X |  |
| Sensor Accuracy | The limit, expressed as a percentage of the sensor maximum, that errors will not exceed when the sensor is used under reference conditions. | Double Float | None | 45 | X | X |
| Skip Limit Checking | When set to true, this flag specifies disable reasonability limit checking for this analog. | Boolean | False | False | X |  |
| status Bit Live Indication | T = S bit true indicates LIVE, false indicates DEAD; F = S bit true indicates DEAD, false indicates LIVE. |  | False | False |  | X |
| Tabular Display Priority | Priority of tabulay display. | Long Integer | 0 | 3 | X | X |
| Tap Changer Timeout | The timeout between steps of a multiple raise/lower supervisory control sequence for a tap changer. |  | False | False |  | X |
| Three State | True = A three-state point is modeled. |  | False | False |  | X |
| Time Delay | The number of seconds after the control request is successfully issued before sending a demand scan request to the associated RTU. | Boolean | False | False | X | X |
| Time Stamp | The time when the value was last updated. | Date Time | None | 39876 | X | X |
| Unacknowledged Alarm List | Permanently Inhibit the flag of unacknowledgedAlarmList. | Boolean | False | False | X | X |
| Value | Value of measurement. | Float | None | 4 | X | X |
| VMD Scope | True when value has VMD scope. | Boolean | False | False | X | X |
| Zero Clamping Deadband | If value is greater than zero, then any value between zero and the entered value will be forced (clamped) to zero for update into the database. | Boolean | False | False | X | 0 |
| Zonal Attribute | Temp Attribute to support dual SCADA feeds. | Boolean | False | False | X | X |

#### Linkage

The required links for SCADA AnalogValues and DiscreteValues are defined in the table below.

| Link Name | Description | Path Name | Analog | Discrete |
| --- | --- | --- | --- | --- |
| MeasurementValueBelongTo(Site) | Identifies a SCADA Site that is used to transfer data measured by this measurement. W.r.t. to Nodal model, sites, QSE1-QSE3 and TSP1-TSP3are usually used with certain exceptions. | List_Information/Site | X | X |
| MeasurementValueHasSecondary(Site) | Identifies a backup SCADA Site that may be used to transfer data measured by this measurement. W.r.t. to Nodal model, sites, QSE4-QSE7 and TSP4-TSP7 are usually used with certain exceptions. | List_Information/Site | X | X |
| MeasurementValueCalculatedBy(Calculation) | Identifies the Calculation to which this measurement belongs. |  | X | X |
| MeasurementValueGroupedBy(MeasurementGroup) | Identifies the measurement group to which this measurement belongs. | Points to the Measurement Group created under a MeasurementLocation | X | X |
| AnalogValueBelongTo (Analog Alarm Category) | Identifies whether an Analog Value belongs to Analog Alarm Category | List_Information/Analog Alarm Categories | X |  |
| AnalogValueHasNameof(AnalogName) | The name of the Analog value | List_Information/Analog Names | X |  |
| AnalogValueHasA(Accuracy Class) | Identifies if the Analog value has an accuracy class | List_Information/Accuracy Classes | X |  |
| DiscreteValueBelongTo (Discrete Alarm Category) | Identifies whether a Discrete Value belongs to Discrete Alarm Category | List_Information/Discrete Alarm Categories |  | X |
| DiscreteValueHasNameof(DiscreteName) | The name of the Discrete value | List_Information/Discrete Names |  | X |
| MeasurementValueHas(ConversionTable) | Identifies whether a Discrete value has a Conversion Table | List_Information/Conversion Tables |  | X |
| DiscreteValueHasTypeof(DiscreteType) | Identifies whether a Discrete Value has type of Discrete type. | List_Information/Discrete Type |  | X |

### Modeling Approach for Auxiliary SCADA Lists

This subsection briefly describes the various auxiliary SCADA lists in the ERCOT CIM model that are utilized when creating SCADA Analog and/or Discrete MeasurementValues.

- Sites: The Sites table is used to define valid SCADA sites, including the local site. Each Point, Analog, and Count Record in the model must be associated with a SCADA Site record in this table. Only data retrieved via intersite data will be associated with any site other than the local site name. In the ERCOT model, DE is the designated local site. 	The various other sites currently defined and used in the ERCOT model are, QSE1, QSE2, QSE3, QSE4, QSE5, QSE6, QSE7, SI, TSP1, TSP2, TSP3, TSP4, TSP5, TSP6, TSP7, etc..

- Analog Alarm Category: This reference table is used to define Analog alarm category information for the SCADA subsystem. The Analog alarm categories currently defined and used in the ERCOT model are: AL and BB.

- Discrete Alarm Category: This reference table is used to model SCADA Discrete Alarm Category information. The Discrete alarm categories currently defined and used in the ERCOT model are, AL, BB, AL, AV, B1, B2, B3, B4, and SS.

- Analog Name: This reference table is used to define various types of Analog measurements that can be defined in the ERCOT CIM model. Some of the Analog Names currently defined and used in the ERCOT model are, AMP, MW, MVA, MVAR, HZ etc.

- Discrete Name: This reference table is used to define various types of Discrete measurements that can be defined in the ERCOT CIM model. Some of the Discrete Names currently defined and used in the ERCOT model are, ST, AVR, RBST, etc.

- Permission Areas: This reference table is used to define valid areas of responsibility for SCADA measurements. The Permission areas currently defined and used in the ERCOT CIM model are, AL, COMMS, EAST, ECAR, ERCOT, GEN, NORT, SOUT, and SYSTEM.

- Conversion Tables: This reference table is used to specify a method of data conversion to be utilized for measurements. The only conversion table used in the ERCOT model is the OAG (Open Access Gateway).

- Accuracy Class: This reference table holds accuracy information for measurement, generation and load schedules. The accuracy classes that are currently defined and used in the ERCOT CIM model are, DCLN, KCL, KV, LD, LDHR, LDHW, LDLR, LDLW, LDMR, LDMW, etc..

- Analog Limit Names: This reference table is used to define valid Limit names and parameters to be used when defining Limit. The Analog Limit names currently defined and used in the ERCOT model are: 15MN, DA15, DAEM, DANR, DM15, DMEM, DMNR, EMGY, etc..

- Discrete Type: This reference table is used to define parameters for switching devices, such as breakers or disconnects, in the SCADA topology model. The various Discrete Types defined currently defined and used in the ERCOT model are, CA_M, COO, HU_T, IN_T, MNB, MOB, MOO, N_A, N_T, O_C, O_C1, etc.

- DeviceTypeName: This reference table is used to define the SCADA device type names  The various Discrete Types defined currently defined and used in the ERCOT model are, BKR, BS, BUS, CAP, CB, LD, GEN etc.. More DeviceTypeNames can be found by navigating to .other Orphans/DeviceTypeName

# Modeling ICCP

## 14.1 Modeling Approach for ICCP

This section describes the approach for modeling ICCP (Inter Control Center Protocol). It is used to provide data exchange between control centers, utilities, power pools, regional control centers and Non-Utility Generators. The data that is sent can be periodic system data, block data transfer, information messages, device control requests etc. Figure below shows the modeling of MVAR telemetry that is sourced from ICCP for a load as modeled in the Information Model Manager hierarchy.

Figure 32 - Information Model Manager hierarchical view of ICCP-sourced measurements in the ERCOT model

As mentioned earlier the ERCOT CIM model allows multiple AnalogValues and/or DiscreteValues to be associated with the same Analog and/or Discrete measurement parent. This feature is exploited when modeling Analog and/or Discrete measurements that are sourced from ICCP in the ERCOT model. In practice the ERCOT CIM model allows a maximum of three AnalogValue and/or DisceteValues to reside under the same Analog and/or Discrete parent. As mentioned in the earlier section on SCADA one amongst these three AnalogValues and/or DiscreteValues is the SCADA MeasurementValue that holds information necessary to define the instance in the EMS SCADA database and the other two may be utilized to provide information relevant to the ICCP source. An Analog and/or Discrete measurement may contain two ICCP MeasurementValues in the scenarios when the telemetered ICCP value is desired to be visible in both ERCOT TSP and ERCOT QSE ICCP database. The modeling of ICCP will be described in the sections to follow.

## Modeling Approach for ICCP AnalogValue and DiscreteValue

The ERCOT CIM model utilizes AnalogValue and DiscreteValues to model ICCP related data. The current section will identify the modeling subtleties of ICCP MeasurementValues. As mentioned earlier the ICCP AnalogValue and/or DiscereteValue is created under an Analog and/or Discrete measurement in the Information Model Manager hierarchy. In the figure below the AnalogValue, ICCP_Value is the ICCP AnalogValue that holds information relevant to the ICCP source of the MVAR Analog measurement. It is imperative for a SCADA AnalogValue/DiscreteValue to be defined under the same Analog parent utilizing the modeling approach described in the previous sections.

### Attributes

The attributes for ICCP AnalogValues and DiscreteValues are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data | Analog | Discrete |
| --- | --- | --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 | X | X |
| Abnormal Alarm Delay Time | The number of seconds for the alarm to remain on the persistance alarm list before toning/alarming because it remained in the violated state. | Integer |  |  |  |  |
| Abnormal For Alarm | This flag is used to cause alarm messages for abnormals to have their date/time displayed in black in the Alarm displays instead of red (assuming the HABITAT FG element set). | Boolean |  |  |  |  |
| Abnormal For SCADA | Setting this flag to true does not affect Alarm displays, but forces the record to appear Normal on SCADA displays. | Boolean |  |  |  |  |
| Alias Name | Free text name of the object or instance. | String |  |  |  |  |
| Allow SELECT Step | TRUE = a separate SELECT action is allowed (but not required) prior to the supervisory control action. | Boolean |  |  |  |  |
| Audible Tone | A flag indicating that notifications of alarm conditions via audible tones and horns will be suppressed. | Boolean |  |  |  |  |
| Auto Ack and Delete Alarms | Automatically acknowledge and delete alarms if the Analog is manually entered or successfully controlled by the operator to a normal state. | Boolean |  |  |  |  |
| Auto Acknowledge | When set to true, this flag specifies that alarms will be automatically acknowledged on return to normal. This will only occur if the Alarm Return to Violations flag is not set on the Limit Names table. | Boolean |  |  |  |  |
| Block via Primary Site | Block Value and Quality update via Primary Site: Do not allow update from the primary site. | Boolean |  |  |  |  |
| Block via Secondary Site | Block Value and Quality update via Secondary Site: Do not allow update from the secondary site. | Boolean |  |  |  |  |
| Component Status | True when value represents status of communication path component. | Boolean |  |  |  |  |
| Control Demand Scan | True = Issues a demand scan request to the RTU at a configurable number of seconds after any successful control requests are issued. This feature is primarily used by measurements with a slow scan rate to provide more timely feedback on the success or failure of the control operation. | Boolean |  |  |  |  |
| Control MMI Sequence | true = override any default settings. | Boolean |  |  |  |  |
| Description | Description of the object or instance. | String |  |  |  |  |
| Enable Auto SE Replacement | TRUE = Allow automatic State Estimator replacement. Automatically substitute the display value with a good quality state estimated value if the quality of the telemetered analog becomes SUSPECT. | Boolean |  |  |  |  |
| From External Program | When set to true, this flag specifies the source of the data is an external program. | Boolean |  |  |  |  |
| From State Estimator | When set to true, this flag specifies the source of the data is state estimator. | Boolean |  |  |  |  |
| General Read Access | This flag is used in conjuction with MeasurementValue_ReadBy association to identify read privileges on a MeasurementValue. When MeasurementValue_ReadBy is non-null the value of this boolean will not matter, i.e. only the MeasurementValueSource identified by the association will have read permissions on the model. When MeasurementValue_ReadBy is null, a true value on this boolean will be interpreted as read privileges being available to all MeasurementValueSource, and a false value on this boolean will be interpreted as read privileges being not available to any MeasurementValueSource. | Boolean |  |  |  |  |
| HABC Name | Connection ID of value using HABConnect. | String |  |  |  |  |
| Historical Recording Deadband | Threshold (percentage currently recorded analog data) above which additional data points should not retained. | Float |  |  |  |  |
| ICCP Data Set Period | ICCP data set period used for the measurement. | Long Integer | None | 3 | X | X |
| ISD Name | Dollar-separacted SCADA Composite ID. | String |  |  |  |  |
| Inhibit Abnormal For Alarm | Permanently Inhibit the flag of abnormalForAlarm. | Boolean |  |  |  |  |
| Inhibit Abnormal For SCADA | Permanently Inhibit the flag of abnormalForSCADA. | Boolean |  |  |  |  |
| Inhibit Audible Tone | Permanently Inhibit the flag of audibleTone. | Boolean |  |  |  |  |
| Inhibit Logging and Alarm List | Permanently Inhibit the flag of loggingAndAlarmList. | Boolean |  |  |  |  |
| Inhibit Unacknowledged Alarm List | Permanently Inhibit the flag of unacknowledgedAlarmList. | Boolean |  |  |  |  |
| Initially Inhibit | A flag indicating that when the system first comes online, alarm indications for this SCADA entry will initially be inhibited. | Boolean |  |  |  |  |
| Invert Analog Via Secondary Site | TRUE = Negate the analog value when received from the secondary site. | Boolean |  |  |  |  |
| Invert Sign | When set to true, this flag specifies that the analog value, as received by SCADA, is inverted before using in other applications. | Boolean |  |  |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |  |  |
| Logging and Alarm List | Permanently Inhibit the flag of loggingAndAlarmList. | Boolean |  |  |  |  |
| Mapped In OAG | T = This data-point is also represented in the OAG model as a data item (designated member of a data packet). | Boolean |  |  |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |  |  |  |
| Negate Value Received from ISD | When set to true, this flag specifies that the polarity of the analog value received via ISD will be switched. | Boolean |  |  |  |  |
| Negative Uni-Polar Clamping | True = positive values will be forced (clamped) to zero before updating into the database. | Boolean |  |  |  |  |
| Not In Service | flag indicating not in service. | Boolean |  |  |  |  |
| Override Default Inhibit Definition | A flag indicating that that the Operator Inhibit Definition overrides the Global Default Inhibit. | Boolean |  |  |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |  |  |
| Peak Data | When set to true, this flag specifies that the Peak Data Processing task will sample this analog. | Boolean |  |  |  |  |
| Positive Uni-Polar Clamping | TRUE = negative values will be forced (clamped) to zero before updating into the database. | Boolean |  |  |  |  |
| Record Historical Data | When set to true, this flag specifies that state changes on the analog are recorded in the historical data review file. | Boolean |  |  |  |  |
| Remote Site Normally Calculated | Remote site normally calculated. True for ICCP, false otherwise. | Boolean | False | False | X | X |
| Remote Site Normally Estimated | Remote site normally estimated. True for ICCP, false otherwise. | Boolean | False | False | X | X |
| Remote Site Normally Manually Entered | Remote site normally manually entered. True for ICCP, false otherwise. | Boolean | False | False | X | X |
| Remote Site Normally Telemetered | Remote site normally telemetered. True for ICCP, false otherwise. | Boolean | True | False | X | X |
| Require EXECUTE Step | True = a supervisory control action is not initiated when a control action is received, and must wait for an additional EXECUTE action. | Boolean |  |  |  |  |
| Require SELECT Step | TRUE = a separate SELECT action is required before a supervisory control action. | Boolean |  |  |  |  |
| Return to Normal Alarm Delay Time | The number of seconds for the alarm to remain on the persistance alarm list before toning/alarming because it remained in the normal state. | Long Integer |  |  |  |  |
| SE Deadband | Display values of good quality which are different than a good quality state-estimated value by more than this amount are considered anomalous, and automatically substituted with the state-estimated value, if the global Automatic State-Estimator Replacement function is enabled. | Float |  |  |  |  |
| Sensor Accuracy | The limit, expressed as a percentage of the sensor maximum, that errors will not exceed when the sensor is used under reference conditions. | Float |  |  |  |  |
| Skip Limit Checking | When set to true, this flag specifies disable reasonability limit checking for this analog. | Boolean |  |  |  |  |
| Tabular Display Priority | Priority of tabulay display. | Integer |  |  |  |  |
| Time Delay | The number of seconds after the control request is successfully issued before sending a demand scan request to the associated RTU. | Integer |  |  |  |  |
| Time Stamp | The time when the value was last updated. | String |  |  |  |  |
| Unacknowledged Alarm List | Permanently Inhibit the flag of unacknowledgedAlarmList. | Boolean |  |  |  |  |
| VMD Scope | True when value has VMD scope. | Boolean |  |  |  |  |
| Value | Value of measurement. | Float |  |  |  |  |
| Zero Clamping Deadband | If value is greater than zero, then any value between zero and the entered value will be forced (clamped) to zero for update into the database. | Float |  |  |  |  |
| Zonal Attribute | Temp Attribute to support dual SCADA feeds. | Boolean |  |  |  |  |
| byPass | When set to true, this flag specifies allowing bypass entry of Suspect values if telemetered from a remote site or SCADA Front End. | Boolean |  |  |  |  |
| from Calculation | Value is from calculation. | Boolean |  |  |  |  |
| from Manual Entry | Value is from manual entry. | Boolean |  |  |  |  |
| from Remote | Value is from remote. | Boolean |  |  |  |  |
| scanRate |  | Integer |  |  |  |  |

### Linkage

The required links for ICCP AnalogValues and DiscreteValues are defined in the table below.

| Link Name | Description | Path Name | Analog | Discrete |
| --- | --- | --- | --- | --- |
| Measurement Value Source | MeasurementValueSource describes the alternative sources updating a MeasurementValue. | Network/Companies / MeasurementValueSource | X | X |

## Modeling Approach for MeasurementValueQuality

MeasurementValueQuality codes are flags which are utilized to know the quality of the data that is received or sent by or to ERCOT. There are various quality codes that are used by ERCOT and the MarketParticipant to communicate about the quality of data. In the ERCOT model a MeasurementValueQuality must be modeled under the ICCP AnalogValue or DiscreteValue. The following figure shows this hierarchical association between AnalogValue/DisceretValue and a MeasurementValueQuality the MeasurementValueQuality, ICCP_Quality modeled under the ICCP AnalogValue ICCP_Value.

### Attributes

The attributes for ICCP MeasurementValueQuality are shown in the table below

| Attribute | Description | Data Type | Default Value | Sample Data | Analog | Discrete |
| --- | --- | --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 |  |  |
| hasCOV | Whether or not ICCP item has Change of Value modifier. | Boolean | False | False | X | X |
| hasquality | Whether or not ICCP item has Quality modifier. | Boolean | False | False | X | X |
| hasTimeStamp | Whether or not ICCP item has Timestamp modifier. | Boolean | False | False | X | X |
| ZonalAttribute | Temporary attribute to support dual SCADA feeds. | Boolean | False | False | X | X |
| Alias Name | Free text name of the object or instance. | String | None | XYZ | X | X |
| Bad Reference | Measurement value may be incorrect due to a reference being out of calibration. | Boolean | False | False | X | X |
| Description | Description of the object or instance. | String | None | XYZ | X | X |
| Estimator Replaced | Value has been replaced by State Estimator. estimatorReplaced is not an IEC61850 quality bit but has been put in this class for convenience. | Boolean | False | False | X | X |
| Failure | This identifier indicates that a supervision function has detected an internal or external failure, e.g. communication failure. | Boolean | False | False | X | X |
| LocalName | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ | X | X |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | XYZ | X | X |
| Old Data | Measurement value is old and possibly invalid, as it has not been successfully updated during a specified time interval. | Boolean | False | False | X | X |
| Operator Blocked | Measurement value is blocked and hence unavailable for transmission. | Boolean | False | False | X | X |
| Oscillatory | To prevent some overload of the communication it is sensible to detect and suppress oscillating (fast changing) binary inputs. If a signal changes in a defined time (tosc) twice in the same direction (from 0 to 1 or from 1 to 0) then oscillation is detected and the detail quality identifier 'oscillatory' is set. If it is detected a configured numbers of transient changes could be passed by. In this time the validity status 'questionable' is set. If after this defined numbers of changes the signal is still in the oscillating state the value shall be set either to the opposite state of the previous stable value or to a defined default value. In this case the validity status 'questionable' is reset and 'invalid' is set as long as the signal is oscillating. If it is configured such that no transient changes should be passed by then the validity status 'invalid' is set Immediately in addition to the detail quality identifier 'oscillatory' (used for status information only). | Boolean | False | False | X | X |
| Out of Range | Measurement value is beyond a predefined range of value. | Boolean | False | False | X | X |
| Over Flow | Measurement value is beyond the capability of being represented properly. For example, a counter value overflows from maximum count back to a value of zero. | Boolean | False | False | X | X |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ | X | X |
| Source | Source gives information related to the origin of a value. The value may be acquired from the process, defaulted or substituted. | Enumeration | PROCESS | PROCESS | X | X |
| Suspect | A correlation function has detected that the value is not consitent with other values. Typically set by a network State Estimator. | Boolean | False | False | X | X |
| Test | Measurement value is transmitted for test purposes. | Boolean | False | False | X | X |
| Validity | Validity may be good, questionable or invalid. Refer to the Validity enumeration for more details. | Enumeration | GOOD | GOOD | X | X |

### Linkage

The required links for ICCP MeasurementValueQuality are defined in the table below.

| Link Name | Description | Path Name | Analog | Discrete |
| --- | --- | --- | --- | --- |
| MeasurementValueQualityMemberOfMeasurementValue | A MeasurementValue has a MeasurementValueQuality associated with it. |  | X | X |

# Modeling Ratings

### Modeling Approach for Ratings

In the network model static ratings are required to be defined for different equipment types (eg. lines, transformers, etc.). In addition to defining operational thresholds for devices, these ratings help define the reasonable boundary conditions for analog measurements telemetered on the devices as well.  The Network Operations Model must use rating categories for Transmission Elements as defined in the ERCOT Operating Guides. ERCOT shall use Dynamic Ratings, where available, in the Network Operations Model, and the CRR Network Models. ERCOT shall use Dynamic Ratings in place of the Normal Rating, Emergency Rating and 15-Minute Rating as applicable as provided under paragraphs (a) or (b) in section 3.10.8 as mentioned in the Nodal Protocols for Transmission Elements established in the Network Operations Model.

ERCOT will continue to use Transmission Element Ratings supplied by TSPs as ERCOT operational limits.  A comprehensive, device-independent template has been provided by ERCOT that can be utilized to model Transmission Element Ratings and define ERCOT operational limits per ERCOT operational requirements.  While model ownership of the ERCOT operational limits will be reflected as being with the TSPs, ERCOT takes full responsibility for their content, application, and use.

Ratings are defined under the OwnerShareRating class.Modeling Approach for SCADAAnalogLimitSetSCADA AnalogLimitSets (AnalogLimitSet.forNetwork = False) define a group of Limits that help set the bounds of SCADA Analog telemetry. In the current ERCOT model SCADA AnalogLimitSets are modeled for Transfomers, Lines, and busbars only. Figure below shows the modeling of SCADA AnalogLimitSets for a busbaras modeled in MAGE. In the figure below the SCADA AnalogLimitSet, ALS is modeled under the Analog measurement named, KV. Note that every Analog can contain only one SCADA AnalogLimitSet definition.

Figure 33 - Information Model Manager Hierarchical View of SCADA Limits in the ERCOT Model

#### Attributes

The attributes for AnalogLimitSet are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 |
| ForNetwork | In the case of SCADA limits this boolean should be set to False. | Boolean | False | False |
| IsPercentageLimits | Tells if the limit values are in percentage of normalValue or the specified Unit for Measurements and Controls. | Boolean | False | False |
| ZonalAttribute | Temp Attribute to support dual SCADA feeds. | Boolean | False | False |
| Alias Name | Free text name of the object or instance. | String | None | XYZ |
| Description | Description of the object or instance. | String | None | XYZ |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | 123 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ |
| Type | This value should be set to Limits when ForNetwork is False. | Enumerator | None | limits |

#### Linkage

No required links.

### Modeling Approach for SCADA AnalogLimit

The ERCOT data dictionary utilizes the AnalogLimits to specify the limit values for the Analog measurement.  AnalogLimits are modeled under the AnalogLimitSet. The attribute limittype is utilized to classify the type of the AnalogLimit being modeled. The commonly utilized types are fifteen minute rating, two hour rating, normal rating and conductor rating. In the ERCOT CIM model every AnalogLimitSet can have a maximum of four distinctly typed AnalogLimits as its children. In the figure below, four AnalogLimits, namely 15MN, CONDUCTOR, EMGY and NRML are modeled as under of the AnalogLimitSet, ALS.

#### Attributes

The attributes for AnalogLimit are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 |
| LowerThreshhold | The value below which the Analog is considered in violation of the limit. When the Upper Threshold is null, only the Lower Threshold is checked for violation. | Float | None | -24 |
| UpperThreshhold | The value above which the Analog is considered in violation of the limit. When the low limit is null, only the high limit is checked for violation. This value must be greater than the Lower Threshold. | Float | None | 24 |
| Deadband | Amount, expressed as a percentage of the range between upper and lower threshold, used in the limit comparison to eliminate extraneous alarms generated when an Analog value oscillates around a limit. When either threshold is null, the percentage is that of the non-null limit. | Double Float | None | 5 |
| LimitType | Type of limit. | Enumeration | None | Normal Rating |
| ForbiddenRegion | T = The Analog is in violation if it is smaller than the Upper Threshold and larger than the Lower Threshold. | Boolean | False | False |
| IgnoreLimitChecking | T = The limit should be ignored when checking the Analog for limit violations. | Boolean | False | False |
| UsePercentage | T = The value displayed in the deadband field (below) is the percentage deadband. Otherwise, the value displayed is the numeric deadband. | Boolean | False | False |
| Value | The value to supervise against. Should be Null for SCADA AnalogLimit. | Double Float | None | Null |
| Zonal Attribute | Temp Attribute to support dual SCADA feeds. | Boolean | False | False |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | 123 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ |
| Alias Name | Free text name of the object or instance. | String | None | XYZ |

#### Linkage

The required links for AnalogLimit are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Belong To (LimitAlarmCategory) | Describes the type of alarm to be raised when the limit is violated. This association should be populated for SCADA AnalogLimits. | List_Information/LimitAlarmCategory |
| Belongs To (ModelingAuthoritySet) | Describes the modeling authority set that the analog limit belongs to. |  |
| Has Name Of (AnalogLimitName) | Describes the type of AnalogLimit. This association should be populated for SCADA AnalogLimits. | List_Information/AnalogLimitNames |

### Modeling Approach for Ratings AnalogLimit

The ERCOT data dictionary utilizes the AnalogLimits to specify the limit values for the Analog measurement.  AnalogLimits are modeled under the Rating instance. The attribute limittype is utilized to classify the type of the AnalogLimit being modeled. The commonly utilized types are fifteen minute rating, two hour rating, normal rating and conductor rating. In the ERCOT CIM model every AnalogLimitSet can have a maximum of four distinctly typed AnalogLimits as its children. In the figure, four AnalogLimits, namely 15MN, CONDUCTOR, EMGY and NRML are modeled under StaticRating.

15.1.3.1 Attributes

The attributes for AnalogLimit are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 |
| Value | The value to supervise against. Should be Null for SCADA AnalogLimit. | Double Float | None | Null |
| Deadband | Amount, expressed as a percentage of the range between upper and lower threshold, used in the limit comparison to eliminate extraneous alarms generated when an Analog value oscillates around a limit. When either threshold is null, the percentage is that of the non-null limit. | Double Float | None | 5 |
| LimitType | Type of limit. | Enumeration | None | Normal Rating |
| LowerThreshhold | The value below which the Analog is considered in violation of the limit. When the Upper Threshold is null, only the Lower Threshold is checked for violation. | Float | None | -24 |
| UpperThreshhold | The value above which the Analog is considered in violation of the limit. When the low limit is null, only the high limit is checked for violation. This value must be greater than the Lower Threshold. | Float | None | 24 |
| ForbiddenRegion | T = The Analog is in violation if it is smaller than the Upper Threshold and larger than the Lower Threshold. | Boolean | False | False |
| IgnoreLimitChecking | T = The limit should be ignored when checking the Analog for limit violations. | Boolean | False | False |
| UsePercentage | T = The value displayed in the deadband field (below) is the percentage deadband. Otherwise, the value displayed is the numeric deadband. | Boolean | False | False |
| Zonal Attribute | Temp Attribute to support dual SCADA feeds. | Boolean | False | False |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | 123 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ |
| Alias Name | Free text name of the object or instance. | String | None | XYZ |

#### Linkage

No required links

# Modeling Transformers

## Modeling Approach

A Transformer is defined as an energy transformation device that transforms alternating current or voltage at one level to alternating current or voltage at another level depending on the application of the device. The two most common usages of Power Transformers are as a voltage Step-Up Transformer from a generation site distribution level to transmission level and as a Step-Down Transformer from transmission level to load end users. ERCOT shall develop the naming convention with the assistance of the TSP and the approval of TAC

Transformers are modeled under a Substation in the ERCOT Model. The three types of transformers currently modeled are Two-winding, Three-winding and phase shifting transformers. Three-winding transformers are modeled as three two-winding transformers with a common tie at 1Kv and are associated to a TransformerKluge. A Power Transformer is required to have a PowerTransformer class, 2 TransformerWinding being the Primary and Secondary, Terminal for each end and a unique TapChanger for a TransformerWinding specifying if it is a Load Tap Changer or a Fixed Tap.  Each TSP shall coordinate with the operators of the Resources connected to their respective systems to establish the proper transformer tap positions (no-load taps) and report any changes to ERCOT using the NOMCR process or other ERCOT prescribed means.

The following subsections shows the hierarchical association on modeling PowerTransformer, TransformerWinding,TapChanger and TransformerKluge.

## Modeling Approach for Powertransformer

PowerTransformer is modeled under Substation as a child instance. Transformer Type should be defined in this class depending on its operational use. The Transformer Types are voltageControl (regulates voltage), phaseControl (phase shifters), voltageAndPhaseControl and fix.

Figure below shows the parent/child hierarchy of a PowerTransformer in Information Model Manager.

Figure 34 - Hierarchy for PowerTransformer

### Attributes

The attributes for a PowerTransformer are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| 15 minute rating Max Shadow Price | States the 15 minute rating Max Shadow price for a Transformer. | DoubleFloat |  |  |
| Alias Name | Free text name of the object or instance | String |  |  |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean |  |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean |  |  |
| Description | Description of the object or instance | String |  |  |
| Emergency Max Shadow Price | States the Emergency Max Shadow price for a Transformer | DoubleFloat |  |  |
| Local Name | The local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, Voltage Level, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Magnetizing Saturation Flux | Core magnetizing saturation curve knee flux level. | PerCent |  |  |
| Magnetizing Saturation Voltage | The reference voltage at which the magnetizing saturation measurements were made. | Voltage |  |  |
| Magnetizing Susceptance Saturation | Core shunt magnetizing susceptance in the saturation region, in per cent. | PerCent |  |  |
| Max Shadow Price | States the Max Shadow price for a Power Transformer. | DoubleFloat |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer |  |  |
| PSS/E ID | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly name units, loads, branches, and transformers. | Integer |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Phases | Describes the phases carried by a power transformer. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | PhaseCode |  |  |
| RUC Monitored | he Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean |  |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean |  |  |
| Transformer Cooling Type | Type of transformer cooling. | EnumTransformerCoolingType |  |  |
| Transformer Type | Transformer Type. | EnumTransformerType |  |  |
| TEID | Transmission Element ID. | Integer |  |  |
| Voltage Sensitivity | Sensitivity of voltage to the transformer tap ratio | PerCent |  |  |
| Contingency Component |  |  |  |  |
| Height | Height |  |  |  |
| Label Height | Label Height |  |  |  |
| Label Width | Label Width |  |  |  |
| Label x co-ordinate | Label x co-ordinate |  |  |  |
| Label y co-ordinate | Label y co-ordinate |  |  |  |
| Width | Width |  |  |  |
| X co-ordinate | X co-ordinate |  |  |  |
| Y co-ordinate | Y co-ordinate |  |  |  |

### Linkage

The required links for a PowerTransformer are defined in table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

## Modeling Approach for POWERTRANSFORMEREND

PowerTransformerEnd is modeled under PowerTransformer as a child instance. This is where the Impedance, Transformer Winding Ratings, Connection Type (Wye or Delta) and Winding Type (Primary and Secondary) are defined.

Figure above shows the parent/child hierarchy of a PowerTransformerEnd in Information Model Manager.

### Attributes

The attributes for a PowerTransformerEnd are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Alias Name | Free text name of the object or instance | String |  |  |
| Connection Type | The type of connection of the winding (e.g. Delta, Wye, zigzag). | EnumWindingConnection |  |  |
| Contingency_Element |  |  |  |  |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean |  |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean |  |  |
| Description | Description of the object or instance |  |  |  |
| Emergency Rating – Transformer Winding | The MVA that the winding can carry under emergency conditions. | ApparentPower |  |  |
| Grounded – Transformer Winding | Set if the winding is grounded. | Boolean |  |  |
| Insulation kV – Transformer Winding | Basic insulation level voltage rating. | Voltage |  |  |
| Local Name | The local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, Voltage Level, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |  |
| Normal Rating | The normal rating, in MVA, for the winding. | ApparentPower |  |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer |  |  |
| PSS/E ID | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly name units, loads, branches, and transformers. | Integer |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Phases | Describes the phases carried by a power transformer. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | PhaseCode |  |  |
| RUC Monitored | he Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean |  |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean |  |  |
| Rated KV – Transformer Winding | KV rating of the winding | Voltage |  |  |
| Remove | The equipment is removed from the network. | Boolean |  |  |
| Remove Enable | The equipment can be removed from the network. | Boolean |  |  |
| Short Term Rating – Transformer Winding | MVA that the winding can carry for a short period of time. | ApparentPower |  |  |
| TEID | Transmission Element ID. | Integer |  |  |
| Winding Type – Transformer Winding | The type of winding, i.e., Primary, Secondary, Tertiary, Quaternary. | EnumWindingType |  |  |
| B – Transformer Winding | Magnetizing branch susceptance (B mag). | Susceptance |  |  |
| bmag Sat – Transformer Winding | Shunt magnetizing susceptance in saturation region. | Susceptance |  |  |
| Contingency Component |  |  |  |  |
| End Number |  |  |  |  |
| G – Transformer Winding | Magnetizing branch conductance (G mag). | Conductance |  |  |
| gmag Sat – Transformer Winding | Shunt magnetizing conductance in saturation region. | Conductance |  |  |
| height |  |  |  |  |
| knee Sat – Transformer Winding | Magnetization curve saturation knee flux level (pu volts/pu hz) | Float |  |  |
| Label Height | Label Height |  |  |  |
| Label Width | Label Width |  |  |  |
| Label x co-ordinate | Label x co-ordinate |  |  |  |
| Label y co-ordinate | Label y co-ordinate |  |  |  |
| R – Transformer Winding | Positive sequence series resistance of the winding. | Resistance |  |  |
| r0 – Transformer Winding | Zero sequence series resistance of the winding. | Resistance |  |  |
| Rground – Transformer Winding | Ground resistance path through connected grounding transformer. | Resistance |  |  |
| X – Transformer Winding | Positive sequence series reactance of the winding. | Reactance |  |  |
| X co-ordinate | X co-ordinate |  |  |  |
| x ground – Transformer Winding | Ground reactance path through connected grounding transformer. | Reactance |  |  |
| x0 – Transformer Winding | Zero sequence series reactance of the winding. | Reactance |  |  |
| Y co-ordinate | Y co-ordinate |  |  |  |

### Linkage

The required links for a PowerTransformerEnd are defined in table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| BaseVoltage | Link to BaseVoltage to which this TransformerWinding belongs. | Network/Base Voltage |
| PowerSystemResource - Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies |
| PowerSystemResource - Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |
| PowerTransformerEnd_HasAPower TransformerEndHasATerminal | Used to link the powertraformerend to one of the windings of the powertransformer. | Network/ERCOT_Texas_Network/ERCOT Substations/WZ_COAST/BBP/UXF5/UXF6 |

## Modeling Approach for TapChanger

TapChanger is modeled under TransformerWinding as a child instance. TapChangers can be a Load Tap Changer or a Fixed tap (LTC Control Mode is set to “off”). If the Transformer is a Phase Shifting Transformer, a PhaseShifterImpedanceCurve should be associated with the TapChanger. All the properties of a TapChanger such as Step Size, Step Voltage Increment, Step Phase Increment, etc. are defined in this class.  Each Generation Entity and each TSP shall schedule generation Outages at mutually agreeable times to implement tap position changes when necessary. If mutual agreement cannot be reached, then ERCOT shall decide where to set the tap position to be implemented by the Generation Entity at the next generation Outage, considering expected impact on system security, future Outage plans, and participants.

Figure above shows the parent/child hierarchy of a TapChanger in Information Model Manager.

### Attributes

The attributes for a TapChanger are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| AVR Enabled | T =Automatic Voltage Regulation is enabled | Boolean |  |  |
| AWR Enabled | T = automatic MW control is enabled | Boolean |  |  |
| Alias Name | Free text name of the object or instance | String |  |  |
| Coupled To Transformer - TapChanger | T = indicates that the phase shifter is coupled to a transformer winding | Boolean |  |  |
| Description | Description of the object or instance |  |  |  |
| Flow Sensitivity - TapChanger | The sensitivity of the regulated MW flow to angle changes, in MW per degree | Float |  |  |
| High Step - TapChanger | Highest possible tap step position, advance from neutral | TapStep |  |  |
| Initial Delay - TapChanger | For an LTC, the delay for initial tap changer operation (first step change). | Seconds |  |  |
| LTC Control Mode | For an LTC, the tap changer control mode, e.g.: Off, Local, Volt, MVAr | EnumTransformerControlMode |  |  |
| Load-Based Regulation Enabled - TapChanger | T = Load-Based Voltage Regulation is enabled | Boolean |  |  |
| Local Name | The local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, Voltage Level, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Low Step - TapChanger | Lowest possible tap step position, from neutral | TapStep |  |  |
| Maximum kV - TapChanger | The maximum voltage regulation for TapChangers. Note that this is a fixed parameter which is not a function of time (i.e., not a regulation schedule). | Voltage |  |  |
| Minimum kV - TapChanger | The minimum voltage regulation for TapChangers. Note that this is a fixed parameter which is not a function of time (i.e., not a regulation schedule). | Voltage |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |  |
| Neutral Angle - TapChanger | The CIM currently has no way of defining the angle associated with the neutral position of a TapChanger belonging to a phase shifter. Thus a neutralAngle attribute (measured in degrees) has been added to the TapChanger class. This attribute only appears in XML when the parent PowerTransformer is a phase shifter, i.e., when PowerTransformer.transformerType = "phaseControl" or "voltageAndPhaseControl". | AngleDegrees |  |  |
| Neutral KV - TapChanger | Voltage at which the winding operates at the neutral tap setting. | Voltage |  |  |
| Neutral Step - TapChanger | The neutral tap step position for this winding. | TapStep |  |  |
| Normal Step - TapChanger | The tap step position used in 'normal' network operation for this winding. For a 'Fixed' tap changer indicates the current physical tap setting. | TapStep |  |  |
| PAR Maximum MW - TapChanger | PAR maximum MW value (MW). | ActivePower |  |  |
| PAR Minimum MW - TapChanger | PAR minimum MW value (MW). | ActivePower |  |  |
| PAR Optimization - TapChanger | PAR optimization flag. | Boolean |  |  |
| PAR Ramp Rate - TapChanger | PAR optimiation ramp rate (MW per minute). | ActivePower |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Step Phase Shift Increment - TapChanger | Phase shift, in degrees, per step position. A positive value indicates a positive phase shift from the winding where the tap is located to the other winding (for a two-winding transformer), or to the &quot;T&quot; point (for a three-winding transformer). | AngleDegrees |  |  |
| Step Voltage Increment - TapChanger | Tap step increment, in per cent of nominal voltage, per step position. | PerCent |  |  |
| Subsequent Delay - TapChanger | For an LTC, the delay for subsequent tap changer operation (second and later step changes). | Seconds |  |  |
| teid | Transmission Element ID. | Integer |  |  |
| Contingency Component |  |  |  |  |

### Linkage

The required links for a TapChanger are entered in BOLD in table below. The path name shows where the links can be found in the model.  Definitions for all of the links can be found by clicking on the help button at the bottom of the links screen.

The required Links for a TapChanger varies depending on the operational use of the Transformer. Important points to consider are as follows:

- “Regulated By (LoadBasedRegulationCurve)” has to be filled if the TapChanger is the LTC side.

- “Regulates (Measurement)” maybe filled if the TapChanger is the LTC side if Voltage or MW Flow Regulation is desired.

- “Regulates (Terminal)” should be filled if the TapChanger is the LTC side with the linkage shown in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Regulated By (LoadBasedRegulationCurve) | Regulated By (LoadBasedRegulationCurve)” may be filled if the TapChanger is the LTC side | Schedules/Regulation Schedule |
| Regulates (Measurement) | An LTC may regulate a specific measurement from the network, typically voltage. A phase shifter would typically be used to regulate a real power (MW) flow measurement. An LTC with significant phase shift characteristics could be used to regulate MW flow instead of voltage. |  |
| Regulates (Terminal) | Regulates (Terminal)” should be filled if the TapChanger is the LTC side | Network/ERCOT Texas Network/ERCOT Substations/Sub Geographical Region/Substation/PowerTransformer/TransformerWinding/Terminal |
| RegulationSchedule | An LTC may have a regulation schedule. | Schedules/Regulation Schedules/Schedule |
| PowerSystemResource - Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies |
| PowerSystemResource - Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

## Modeling Approach for Transformerkluge

This class is used for Three Winding Transformers. In ERCOT CIM Model, Three winding transformers are modeled as a three 2-winding transformers with a common tie at 1KV. TransformerKluge is modeled under sysOrphan as a child instance. The 2-winding transformers that comprises the Three Winding Transformer are linked together in this class through the “Has A (PowerTransformer)” links tab.

Figure below shows the parent/child hierarchy of a TransformerKluge in Information Model Manager.

Figure 35 - Hierarchy for TransformerKluge

### Attributes

The attributes for a TransformerKluge are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Alias Name | Free text name of the object or instance | String |  |  |
| Description | Description of the object or instance. | Boolean |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |  |
| PSS/E 3 Winding ID | Attribute will be used to store the three winding transformer ID and Mark which transformers are to be grouped as three winding Transformers. | String2 |  |  |
| PSS/E 3 Winding Name | Attribute will be used to store the three winding transformer name. | String12 |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |

### Linkage

The required links for a TransformerKluge are defined in table below

| Link Name | Description | Path Name |
| --- | --- | --- |
| Has A (PowerTransformer) | Indicates the Power Transformers associated to a Three Winding Transformer | Network/ERCOT Texas Network/ERCOT Substations/Sub Geographical Region/Substation/PowerTransformer |

# Modeling Load

## Modeling Approach

In the ERCOT CIM model, Loads are any classes that inherit from the class: EnergyConsumer. EnergyConsumer is an abstract class and should not be used for real loads.

CustomerLoad inherits from ConformLoad and is used in the ERCOT model. StationSupply also inherits from EnergyConsumer and is used in the ERCOT model. Loads of type StationSupply and CustomerLoad should be modeled under a VoltageLevel in a Substation.  ERCOT shall develop the naming convention with the assistance of the TSP and the approval of TAC.  Individual Load connections may be combined, at the discretion of ERCOT, with other Load connections on the same transmission line to represent a Model Load to facilitate state estimation of Loads that do not telemeter Load measurements. ERCOT shall define Model Loads, which may be one or more combined Loads, for use in its Network Operations Model. A Model Load cannot be used to represent Load connections that are in different Load Zones.

## Modeling Approach for CustomerLoad

Conforming loads can be modeled as an instance of the CustomerLoad class. The instance needs to be contained in an equipmentContainer of the class VoltageLevel. The VoltageLevel needs to be contained in a Substation.

The CustomerLoad class is used to model the location in which power is being removed from the transmission grid.  Each CustomerLoad class represents a single transformer in the field.  The amount of power consumed by the CustomerLoad is dictated by an associated hourly schedule.

Each CustomerLoad instance should be associated with one instance of SettlementNOIELoadZone, or one instance of DCTie, or its parent Substation should be associated with one instance of SettlementLoadZone.

If a Load is assigned to a NOIE load zone, then its ConnectivityNode can ONLY have loads that are assigned to the same NOIE load zone, i.e. cannot have other loads at the same ConnectivityNode assigned to different load zone

In other words, all loads that connect to the same ConnectivityNode must belong to the same load zone. All those loads must either be associated to the same NOIE load zone, or none of them has this association.

In situations where a portion of a load is both NOIE and non-NOIE, the TSP can model the load transformer as a PowerTransformer and then model a NOIE load and a non-NOIE load below the transformer.

CustomerLoad and Load instances cannot have association to PrivateAreaNetwork of type ERCOTPANTYPE.PrivateUseNetwork or SelfServe or BLT_Normally_out.

Figure 36 – Customer Load

### Attributes

The attributes for a CustomerLoad are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 |
| Alias Name | Free text name of the object or instance. | String |  |  |
| Conforming Load Flag | Flag is set to TRUE if the load is conforming, i.e., tracks the area load to which the energy consumer belongs. | Boolean | True |  |
| Customer Count | Number of individual customers represented by this Demand. | Counter |  | 123 |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Description | Description of the object or instance. | String |  |  |
| Fixed Reactive Power | Reactive component of the load that is a fixed quantity, MVAr. | ReactivePower |  |  |
| Fixed Reactive Power Percent | Fixed MVAr as per cent of load area fixed MVAr. | Percent |  |  |
| Fixed Real Power | Real component of the load that is a fixed quantity, MW. | ActivePower |  |  |
| Fixed Real Power Percent | Fixed MW as per cent of load area fixed MW. | Percent |  | 45.1856 |
| Interruptible | Used to designate the device model to be used when processing a StaticVarCompensator for planning models | Boolean |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Longitude | Longitude coordinates. | Float |  |  |
| Maximum MVAR | Maximum Reactive POWER LOAD. | Float |  | 80 |
| Maximum MW | Maximum REAL POWER LOAD. | Float |  | 80 |
| Minimum MVAR | MINIMUM Reactive POWER LOAD. | Float |  | -80 |
| Minimum MW | MINIMUM REAL POWER LOAD. | Float |  | 0 |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  | 470542 |
| Nominal Reactive Power | Nominal value for reactive power, MVAr. | ReativePower |  | 5 |
| Nominal Reactive Power Percent | Nominal MVAr as per cent of load group nominal MVAr. | Percent | 100 |  |
| Nominal Real Power | Nominal value for real power, MW. Nominal real power is adjusted according to the load profile selected for the consumer. It equates to one per unit in the load profile. | ActivePower |  | 95 |
| Nominal Real Power Percent | Nominal MW as per cent of load group nominal MW. | Percent | 100 |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | PhaseCode |  |  |
| Power Factor | Power factor for nominal portion of load. Defined as MW/MVA. | PowerFactor |  | 0.999991 |
| PSS/E ID | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly name units, loads, branches, and transformers. | String |  | 1 |
| Reactive Power Frequency Exponent | Exponent of per unit frequency effecting reactive power | Exponent |  |  |
| Reactive Power Voltage Exponent | Exponent of per unit voltage effecting reactive power. | Exponent |  |  |
| Real Power Frequency Exponent | Exponent of per unit frequency effecting real power. | Exponent |  |  |
| Real Power Voltage Exponent | Exponent of per unit voltage effecting real power. | Exponent |  |  |
| Remove | The equipment is removed from the network. | Boolean | False |  |
| Remove Enable | The equipment can be removed from the network. | Boolean | False |  |
| RUC Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Transmission Element ID | Transmission Element ID. | Integer |  |  |
| Contingency_Element |  | Boolean |  |  |
| contingencyComponent |  | Boolean |  |  |
| height | height |  |  |  |
| label height | Label height |  |  |  |
| label width | Label width |  |  |  |
| label x co-ordinate | Label x co-ordinate |  |  |  |
| label y co-ordinate | Label y co-ordinate |  |  |  |
| width | width |  |  |  |
| x co-ordinate | X co-ordinate |  |  |  |
| y co-ordinate | Y co-ordinate |  |  |  |

### Linkage

The required links for a CustomerLoad are shown in the table below.

| Link Name | Description | Path |
| --- | --- | --- |
| EnergyConsumers Conform Load- ConformLoadGroup | Consumers may be assigned to a load area. | Schedules/Load Area Schedules/ERCOT/SubLoadArea |
| PowerSystemResource PowerSystemResource- Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies |
| PowerSystemResource PowerSystemResource- Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |
| EnergyConsumerEnergyConsumer-PlanningArea | Planning Area | Network/Planning_Groups/Planning_Zone/GONZALES |
| EnergyConsumerEnergyConsumer-PlanningZone | Planning Zone | Network/Planning_Areas/LCRA TSC |

## Modeling Approach for StationSupply

Loads that are not customer load can be modeled as an instance of the StationSupply class. A StationSupply load may be either conforming or non-conforming. The instance needs to be contained in an EquipmentContainer of the class VoltageLevel. The VoltageLevel needs to be contained in a Substation.

The StationSupply class is used to model the power necessary to support the generation of power (i.e. feed water pumps, condenser pumps, etc.).  The amount of power consumed by the station supply will be dependent on the output of an associated generator.

Figure 37 – NonConform Load

### Attributes

The required attributes for a StationSupply are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 |
| Alias Name | Free text name of the object or instance. | String |  |  |
| Conforming Load Flag | Flag is set to TRUE if the load is conforming, i.e., tracks the area load to which the energy consumer belongs. | Boolean | True |  |
| Customer Count | Number of individual customers represented by this Demand. | Counter |  | 123 |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Description | Description of the object or instance. | String |  |  |
| Fixed Reactive Power | Reactive component of the load that is a fixed quantity, MVAr. | ReactivePower |  |  |
| Fixed Reactive Power Percent | Fixed MVAr as per cent of load area fixed MVAr. | Percent |  |  |
| Fixed Real Power | Real component of the load that is a fixed quantity, MW. | ActivePower |  |  |
| Fixed Real Power Percent | Fixed MW as per cent of load area fixed MW. | Percent |  | 45.1856 |
| Latitude | Latitude coordinates. | Float |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Longitude | Longitude coordinates. | Float |  |  |
| Maximum MVAR | Maximum Reactive POWER LOAD. | Float |  | 80 |
| Maximum MW | Maximum REAL POWER LOAD. | Float |  | 80 |
| Minimum MVAR | MINIMUM Reative POWER LOAD. | Float |  | -80 |
| Minimum MW | MINIMUM REAL POWER LOAD. | Float |  | 0 |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  | 470542 |
| Nominal Reactive Power | Nominal value for reactive power, MVAr. | ReativePower |  | 5 |
| Nominal Reactive Power Percent | Nominal MVAr as per cent of load group nominal MVAr. | Percent |  |  |
| Nominal Real Power | Nominal value for real power, MW. Nominal real power is adjusted according to the load profile selected for the consumer. It equates to one per unit in the load profile. | ActivePower |  | 95 |
| Nominal Real Power Percent | Nominal MW as per cent of load group nominal MW. | Percent |  |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | PhaseCode |  |  |
| Power Factor | Power factor for nominal portion of load. Defined as MW/MVA. | PowerFactor |  | 0.999991 |
| PSS/E ID | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly name units, loads, branches, and transformers. | String |  | 1 |
| Reactive Power Frequency Exponent | Exponent of per unit frequency effecting reactive power | Exponent |  |  |
| Reactive Power Voltage Exponent | Exponent of per unit voltage effecting reactive power. | Exponent |  |  |
| Real Power Frequency Exponent | Exponent of per unit frequency effecting real power. | Exponent |  |  |
| Real Power Voltage Exponent | Exponent of per unit voltage effecting real power. | Exponent |  |  |
| Remove | The equipment is removed from the network. | Boolean | False |  |
| Remove Enable | The equipment can be removed from the network. | Boolean | False |  |
| RUC Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Step | Schedule is step function. | Boolean | False |  |
| teid | Transmission Element ID. | Integer |  |  |
| width | width | Integer |  |  |
| x co-ordinate | x co-ordinate | Integer |  |  |
| y co-ordinate | y co-ordinate | Integer |  |  |

### Linkage

The required associations for a StationsSupply are shown in the table below.

| Link Name | Description | Path |
| --- | --- | --- |
| EnergyConsumers NonConformLoad-NonConformLoadGroup | Consumers may be assigned to a load area. | Schedules/Load Area Schedules/ERCOT/SubLoadArea |
| PowerSystemResource PowerSystemResource- Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies |
| PowerSystemResource PowerSystemResource- Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |
| EnergyConsumerEnergyConsumer-PlanningArea | Planning Area | Network/Planning_Groups/Planning_Zone/GONZALES |
| EnergyConsumerEnergyConsumer-PlanningZone | Planning Zone | Network/Planning_Areas/LCRA TSC |

## Modeling Approach for ConformLoadGroup

All the ConformingLoads should be assigned to ConformLoadGroup. These are the Loads that follow a daily and seasonal load variation pattern. ConformLoadGroup should be created under a LoadArea/SubLoadArea under ‘Schedules/Load Area Schedules’.

Figure 38 – Conform Load Group

### Attributes

The required attributes for a ConformLoadGroup are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 |
| Alias Name | Free text name of the object or instance. | String |  |  |
| Description | Description of the object or instance. | String |  |  |
| Forecast Enabled | Forecast enabled. | Boolean | False |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |

### Linkage

There are no required associations for a ConformLoadGroup.

## Modeling Approach for ConformLoadSchedule

A curve of load versus time (X-axis) showing the active power values (Y1-axis) and reactive power (Y2-axis) for each unit of the period covered. This curve represents a typical pattern of load over the time period for a given day type and season. ERCOT needs TSP’s to submit 168 values for each curve. A template will be provided to help in entering this data.

ConformLoadSchedule should be created under a LoadArea/SubLoadArea/ConformLoadGroup under ‘Schedules/Load Area Schedules’.

### Attributes

Attributes for a ConformLoadSchedule are shown in the table below.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| name | Name of the instance of this class | String | CB_1 |
| Alias Name | Free text name of the object or instance. | String |  |
| Description | Description of the object or instance. | String |  |
| End Time | End Time. | Time | 01:00:00AM |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |
| Start Time | Start Time. | Time | 12:00:00AM |
| Time Step | Time Step | Seconds |  |
| Value 1 Unit | Value 1 Unit. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | String | MW |
| Value 2 Unit | Value 2 Unit. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | String | MVAR |

### Linkage

The required links for ConformLoadSchedule are below.

| Link Name | Description | Path |
| --- | --- | --- |
| SeasonDayTypeSChedules Based On (DayType) | Day Type for the Conform Load Schedule | List_Information/DayTypes/Day |

## Modeling Approach for NONConformLoadGroup

All the NonConformingLoads should be assigned to NonConformLoadGroup. These are the Loads that does not follow a daily and seasonal load variation pattern. NonConformLoadGroup should be created under a LoadArea/SubLoadArea under ‘Schedules/Load Area Schedules’.

Figure 39 – NonConform Load Group

### Attributes

The required attributes for a NonConformLoadGroup are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 |
| Alias Name | Free text name of the object or instance. | String |  |  |
| Description | Description of the object or instance. | String |  |  |
| Forecast Enabled | Forecast enabled. | Boolean | False |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |

### Linkage

There are no required associations for a NonConformLoadGroup.

## Modeling Approach for NONConformLoadSchedule

A curve of load versus time (X-axis) showing the active power values (Y1-axis) and reactive power (Y2-axis) for each unit of the period covered. This curve represents a typical pattern of load over the time period for a given day type and season. ERCOT needs TSP’s to submit 168 values for each curve. A template will be provided to help in entering this data.

ConformLoadSchedule should be created under a LoadArea/SubLoadArea/NonConformLoadGroup under ‘Schedules/Load Area Schedules’.

### Attributes

Attributes for a NonConformLoadSchedule are shown in the table below.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| name | Name of the instance of this class | String | CB_1 |
| Alias Name | Free text name of the object or instance. | String |  |
| Description | Description of the object or instance. | String |  |
| End Time | End Time. | Time | 01:00:00AM |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |
| Start Time | Start Time. | Time | 12:00:00AM |
| Time Step | Time Step | Seconds |  |
| Value 1 Unit | Value 1 Unit. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | String | MW |
| Value 2 Unit | Value 2 Unit. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | String | MVAR |

### Linkage

The required links for NonConformLoadSchedule are below.

| Link Name | Description | Path |
| --- | --- | --- |
| SeasonDayTypeSChedules Based On (DayType) | Day Type for the Conform Load Schedule | List_Information/DayTypes/Day |

# Modeling Curves

This section will cover modeling of Curves which include LoadBasedRegulationCurve, MVArCapabilityCurve, PhaseShifterImpedanceCurve, RampRateCurves, StationSupplyWRCurve, and TransformerImpedanceCurve.

## Modeling Approach

The ERCOT CIM data dictionary defines a Curve as relationship between an independent variable (X-axis) and one or two dependent   variables (Y1-axis and Y2-axis), which can also serve as schedules. There are six types of curves which are LoadBasedRegulationCurve, MVArCapabilityCurve, PhaseShifterImpedanceCurve, RampRateCurves, StationSupplyWRCurve, and TransformerImpedanceCurves. Figure below shows a RampRateCurve as modeled in Information Model Manager, with parent/child associations labeled, the screenshot should look similar for the other five types of curves with the exception of the Parent instance of the curve.

The number of CurveData associated with the MVArCapabilityCurves and RampRateCurve should not exceed 10.

All x_axisdata data points in a MVArCapabilityCurve should be unique. Only one y1_axisdata point in a MVArCapabilityCurve can be 0. Only one y2_axisdata point in a MVArCapabilityCurve can be 0.

Number of CurveScheduleData under PhaseShifterImpedanceCurve and TransformerImpedanceCurve are the same as Number of TapChanger step within PowerTransformer where the curve is asscociated to.

Figure 40 - Modeled RampRateCurves with Parent/Child Associations

## Attributes

The attributes for a Curve are shown in the Table 1 below. There is an additional four columns representing each type of GeneratingUnit by which it will specified if an attribute is used within that type. The labels of these columns are LoadBasedRegulationCurve as LBRC, MVArCapabilityCurve as MVArCC, PhaseShifterImpedanceCurve as PSIC, RampRateCurves as RRC, StationSupplyWRCurve as SSWRC, and TransformerImpedanceCurve as TIC.

| Attribute | Description | Data Type | Default Value | Sample Data | LBRC | MVarCC | PSIC | RRC | SSWRC | TIC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 | X | X | X | X | X | X |
| curveStyle | The style or shape of the curve. | EnumCurveStyle | None | straightLineYValues | X | X | X | X | X | X |
| xUnit | The X-axis units of measure. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | String20 | None |  | X | X | X | X | X | X |
| y1Unit | The Y1-axis units of measure. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | String20 | None |  | X | X | X | X | X | X |
| rampRateCurveId | Ramp Rate Curve ID. | String5 | None |  |  |  |  | X |  |  |
| y2Unit | The Y2-axis units of measure. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | String20 | None |  | X | X | X | X | X | X |
| coolantTemperature | The machine's coolant temperature in degrees Celsius (e.g., ambient air or stator circulating water). | Temperature | None |  |  | X |  |  |  |  |
| hydrogenPressure | The hydrogen coolant pressure. | Pressure | None |  |  | X |  |  |  |  |
| Emergency | Denote the type of ramp rate. | Boolean | None |  |  |  |  | X |  |  |

In table below, it specifies what are the curveStyle, xUnit, y1Unit, and y2Unit of each type of curve.

Curve Style and Unit Table

| Curve Name | Curve Style | X Unit | Y1 Unit | Y2 Unit |
| --- | --- | --- | --- | --- |
| LoadBasedRegulationCurve | straightLineYValues | MW | KV | KV |
| MVArCapabilityCurve | straightLineYValues | MW | MVAr | MVAr |
| PhaseShifterImpedanceCurve | straightLineYValues | Degrees | Ratio | None |
| RampRateCurves | straightLineYValues | MW | MW/Min | MW/Min |
| StationSupplyWRCurve | straightLineYValues | MW | MW | MVAr |
| TransformerImpedanceCurve | straightLineYValues | Impedance | Tap | None |

## Linkage

The required links for all Curves types are defined in Table below.

| Link Name | Description | Path Name | LBRC | MVarCC | PSIC | RRC | SSWRC | TIC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SynchronousMachine | Curve is part of A Synchronoues Machine | Network/ERCOT_Texas_Network/ERCOT Substations/SubgeographicalRegion/Substation/VoltageLevel/SynchronousMachine |  | X |  |  |  |  |
| Configuration | Curve is part of B Configuration | Network/ERCOT_Texas_Network/ERCOT Substations/SubGeographicalRegion/Substation/ResouceController/CombinedCyclePlant/LogicalConfiguration/Configuration |  |  |  | X |  |  |
| Member Of (EnergyConsumerResource) | Curve is part of C EnergyConsumer Resource | Network/ERCOT Texas Network/ERCOT Substations/SubGeographicalRegion/Substation/VoltageLevel/CustomerLoad/EnergyConsumerResource |  |  |  | X |  |  |
| Member Of (GeneratingUnit) | Curve is part of D GeneratingUnit | Network/ERCOT_Texas_Network/ERCOT Substations/SubgeographicalRegion/Substation/ResourceController/GeneratingUnit |  |  |  | X |  |  |
| StationSupply | Curve is part of E StationSupply | Network/ERCOT_Texas_Network/ERCOT Substations/SubgeographicalRegion/Substation/VoltageLevel/StationSupply |  |  |  |  | X |  |

# Modeling CurveData

## Modeling Approach

CureveData instances can be created both by ERCOT and Market Participants. CurveData contains data point values for defining a Curve or Schedule. CurveData should be created as a child of one of allowed instances of Curve namely TransformerImpedanceCurve, StationSupplyWRCurve or PhaseShifterImpedanceCurve.

Figure 41 - CurveData

## Attributes

The following table shows all the attributes that are available for a CurveData.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 |
| Alias Name | Free text name of the object or instance | String | None |  |
| Local Name | The localName is a human readable name of the object | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs | String | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |
| X Axis Data | The data value of the X-axis variable, depending on the X-axis units | Double Float | 15 |  |
| Y1 Axis Data | The data value of the first Y-axis variable, depending on the Y-axis units | Double Float | 1 |  |
| Y2 Axis Data | The data value of the second Y-axis variable (if present), depending on the Y-axis unit. | Double Float | 1 |  |

## Linkage

There are no required links to the CurveData.

# Modeling RegularTimePoint

## Modeling Approach

Instances of RegularTimePoint can be created both by Market Participants and ERCOT. RegularTimePoint represents Time Points for a Schedule where the time between the points is constant.

Figure 42 - RegularTimePoint

## Attributes

The following table shows all the attributes that are available for a RegularTimePoint.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 |
| RT Name | Equivalent of IdentifiedObject.name. | String | None | SUN_0 |
| Sequence Number | Sequence Number. | Number | None | 1 |
| Value 1 | Value 1. | Float | None | 9.99 |
| Value 2 | Value 2. | Float | None | 0.1 |

## Linkage

There are no required links to the RegularTimePoint.

# Modeling Terminal

## Modeling Approach

Terminal’s can be created by TSP’s. Terminal is an electrical connection point to a piece of conducting equipment. Terminals are connected at physical connection points called 'connectivity nodes'. A Terminal should always be connected to conducting Equipment.

Terminals connected to Equipment can not be connected to the same ConnectivityNode. The Terminals have to connect to a different ConnectivityNode.

Terminal associated to Equipment should have unique names.

Figure 43 - Terminal

## Attributes

The following table shows all the attributes that are available for a Terminal.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 |
| Alias Name | Free text name of the object or instance. | String |  |  |
| Description | Description of the object or instance. | String |  |  |
| Edge Val | edgeVal is a concatenation of all edge coordinates |  |  |  |
| From X offset | From X offset |  |  |  |
| From X pern | From X perm |  |  |  |
| From Y offset | From Y offset |  |  |  |
| From Y perm | From Y perm |  |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |  |
| Near | Flag indicating whether the terminal is a near terminal of a branch. | Boolean |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| PSS/E Bus Name | Store the PSS/E bus name that will be associated with the grouping of Connectivity Nodes. | String |  |  |
| PSS/E Bus Number | Attribute will be used to store the PSS/E bus number that will be associated with the grouping of Connectivity Nodes. | Number |  |  |
| To X offset | To X offset |  |  |  |
| To X perm | To X perm |  |  |  |
| To Y offset | To Y offset |  |  |  |
| To Y perm | To Y perm |  |  |  |
| Height | Height |  |  |  |
| label height | Label height |  |  |  |
| label width | Label width |  |  |  |
| label x co-ordinate | Label x coordinate |  |  |  |
| label y co-ordinate | Label y coordinate |  |  |  |
| monitoredEnd | Flag indicating whether the end of a branch/xfmr is monitored | Boolean |  |  |
| phases | Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | Dropdown Value |  |  |
| sequenceNumber |  | Integer |  |  |
| width | Width |  |  |  |
| x co-ordinate | X co-ordinate |  |  |  |
| y co-ordinate | Y co-ordinate |  |  |  |

## Linkage

There are no required links to a Terminal.

# Modeling ConnectivityNode

## Modeling Approach

ConnectivityNodes are points where Terminals of Conducting Equipment are connected together with zero impedance. A ConnectivityNode is created under a ConnectivityNodeGroup in Information Model Manager. ConnectivityNodeGroup’s are created under a VoltageLevel.

ConnectivityNodes must be associated to atleast 2 Terminals.

The ConnectivityNodes in a ConnectivityNodeGroup must be in the same Substation i.e. ConnectivityNodes in a given ConnectivityNodeGroup cannot span multiple Substations.

Figure 44 - ConnectivityNode

## Attributes

The following table shows all the attributes that are available for a ConnectivityNode.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 |
| Alias Name | Free text name of the object or instance. | String |  |  |
| Busbar type | Define the type of busbar section associated with this connectivity node (Normal/Feeder Head/Injection Source) | Dropdown Value |  |  |
| Description | Description of the object or instance. | String |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| PSS/E Bus Name | Store the PSS/E bus name that will be associated with the most favored Connectivity Node in Connectivity Node to Bus Processing. | String |  |  |
| PSS/E Bus Number | The PSS/E bus number associated with this point in the network. This attribute should only be used to model ficticious PSS/E busbars that are not associated with physical busbar sections. | Integer |  |  |
| Slack Bus Priority | Swing Bus Definition. | Integer |  |  |
| Transmission Element ID | Transmission Element ID. | String |  |  |
| height | Height |  |  |  |
| width | Width |  |  |  |
| x co-ordinate | X co-ordinate |  |  |  |
| y co-ordinate | Y co-ordinate |  |  |  |

## Linkage

The required links for a ConnectivityNode are defined below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| ConnectivityNodeMemberOfEquipmentContainer | EquipmentContainer |  |

# Modeling ElectricalBus

## Modeling Approach

This section describes the approach for modeling an ElectricalBus. ElectricalBuses are modeled by both Market Participants and ERCOT.  Each Electrical Bus that operates as part of the ERCOT Transmission Grid in excess of 60 kV and that is required to model switching stations or transmission Loads shall be modeled.

ElectricalBus needs to be always contained in an instance of the class ConnectivityNode, which in turn is contained in an instance of the class ConnectivityNodeGroup. As per modeling approach for a HUBBus an ElectricalBus can become a part of the HUBBus definition by being contained under a ConnectivityNodeGroup which is associated to a HUBBus.

Every ElectricalBus should be within a LoadZone or a NOIELoadZone. All the loads connected to ElectricalBus should be in the same LoadZone or NOIELoadZone. If an ElectricalBus is connected to a DCTie Psuedo Load, then it cannot be connected to other loads. In situations where a portion of a load is both NOIE and non-NOIE, the TSP can model the load transformer as a PowerTransformer and then model a NOIE load and a non-NOIE load below the transformer.

The name of the Electrical Bus class is somewhat misleading.  It should be noted that instances of this class do not represent actual buswork in the field (see: BusbarSection).  Rather, the ElectricalBus class defines a location where an LMP will be calculated and where a settlement point may be located.

Definition

An abstract Market construct used to denote connectivity nodes of interest.  LMP prices will be determined at these nodes.  Electrical Buses are maintained by both TDSPs and ERCOT.

There are specific business rules for where Electrical Buses must be located in the model.  An Electrical Bus must be associated with a connectivity node when:

- A load is attached to the node directly and not through a switch.  The EB has to be associated to the same node that the Load/Unit is connected to.

- A unit is attached to the node.

- Three or more switches are attached to the node and the node has a voltage reading.

- A Resource Node is associated with the node.

- An EPS meter is associated with the node.

Additionally, Hub Buses (as defined in the protocols) are required to contain at least one Electrical Bus.  If none of the above criteria is met for the nodes contained within a Hub Bus, ERCOT must add an Electrical Bus to the model and associated to one of the associated nodes.

Electrical Buses are created and maintained by both TSPs and ERCOT.  TSPs will be responsible for maintaining Electrical Buses relating to their Connectivity Nodes (i.e. for loads, >3 Switches, and Hub Buses).  ERCOT will maintain, on behalf of the Resource Entity, the Electrical Buses related to Resource Nodes and EPS meters.

In general, TSPs will be responsible for Electrical Buses contained within their substations.  However, since EPS meters and Resource Nodes can be located in a TSP’s Substation, their will be certain cases where ERCOT will be responsible for Electrical Buses contained within a TDSP’s substation. In such cases, ERCOT will create and manage the necessary NOMCR(s).

Example #1:  A TSP is creating a NOMCR to reflect the future addition of a load transformer.  In addition to adding the load and associated switches, the TSP must create an Electrical Bus and associate it to the same connectivity node in which the load is attached.

Example #2:  An RE informs ERCOT of a future EPS meter configuration change.  ERCOT will create a NOMCR changing the associated connectivity node of the EPS meter.  Additionally, ERCOT will move the EPS meter-related electrical bus to the new connectivity node.

Figure 45 - ElectricalBus

## Attributes

Attributes for a ElectricalBus are shown in the table below.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |
| Alias Name | Free text name of the object or instance. |  |  |
| Description | Description of the object or instance. |  |  |
| Display LMP | Display LMP | Boolean | True |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |

## Linkage

The required links for an ElectricalBus are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| BaseVoltage | BaseVoltage of the ElectricalBus | Network/Base Voltage |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

# Modeling ConnectivityNodeGroup

## Modeling Approach

The ERCOT CIM model defines a ConnectivityNodeGroup as a grouping of Connectivity Nodes.  The TSP planners will need to identify the PSS/E Bus name and PSS/E Bus number for each ConnectivityNodeGroup.  The PSS/E Bus Name and PSS/E Bus Number must be unique within the Information Model Manager.  These values cannot be duplicated. See figure below as an example.

TSP’s will need to enter the PSS/E Bus number and PSS/E name in NOMCR’s to correctly identify the busses that will come through topology processor.  Without this data, topology processor cannot create the busses correctly.

This will require coordination between operations and planning in the TSP company.

Figure 46 – Connectivity Node Group

## Attributes

Attributes for a ConnectivityNodeGroup are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Description | Description of the object or instance | String | None |  |
| Latitude | Latitude coordinates | Float | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | Float | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| PSS/EBusName | The bus name which is used by planners to identify the bus Stores the PSS/E bus name that will be associated with the grouping of Connectivity Nodes. | String12 | None |  |
| PSS/EBusNumber | The bus number which is used by planners to identify the bus Attribute will be used to store the PSS/E bus number that will be associated with the grouping of Connectivity Nodes. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| teid | Transmission Element ID | Integer | Auto-populated |  |
| contingencyComponent | (True/False) | Boolean |  |  |

## Linkage

The required links for ConnectivityNodeGroup are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |
| PlanningArea | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly number areas. | Network/Companies |
| Planning Zone | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly number zones. | Network/Companies |

# Modeling OwnershareRating

## Modeling Approach

OwnerShareRating can be utilized on Power Equipments that can be co-rated by different companies defined as an owner of the equipments OwnerShareRating is modeled under ACLineSegment or TransformerWinding or Series Compensators as a child instanceRatings added on breakers are solely for planning purposes.

When defining an OwnerShareRating, the “Owned By (Dynamic Element)”, “Rated by (Ownership)” , “Reference (WeatherStation)” , and if possible “Reference (WeatherStationAlt)” should be properly linked according to their Path Name(see Linkage OwnerShareRating below).

Figure below shows the parent/child hierarchy of a OwnerShareRating in Information Model Manager.

Figure 47 - Hierarchy for OwnerShareRating

## Attributes

The attributes for an OwnerShareRating are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. |  |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

## Linkage

The required links for OwnerShareRating are defined in table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Owned By (DynamicElement) | Indicates DynamicElement for which Rating is being provided. | .other Orphans/DynamicElement/Line |
| Rated By (Ownership) | Owner of the Equipment | Network/Companies/Company/Ownership |
| Reference (WeatherStation) | Weather Station the Equipment is assigned to. | .other Orphans/WeatherStation/Weather Stations |
| Reference (WeatherStationAlt) | Alternate Weather Station that the owner intends to assign to the Equipment. | .other Orphans/WeatherStation/Weather Stations |

# Modeling BusbarSection

## Modeling Approach

A BusbarSection conducts electricity within a Substation or other electrical apparatus.

A BusbarSection is modeled under a VoltageLevel in a Substation.  A Terminal is modeled under a BusbarSection as a connection points to the circuit. SCADA values modeled under the Terminal provide the AnalogValues(MVAR and MW) of the busbar to the model. Figure below shows the parent/child hierarchy of a BusbarSection in Information Model Manager.

Figure 48 - Hierarchy for BusbarSection

## Attributes

The attributes for an BusbarSection are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Contingency_Element | (True/False) | Boolean |  |  |
| DAM Monitored | Boolean flags to indicate Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| Description | Description of the object or instance | String |  |  |
| Latitude | Latitude coordinates. | int |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | int |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | int |  |  |
| PSSE ID | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers. | String |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | String |  |  |
| RUC Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Remove | The equipment is removed from the network. | Boolean | False |  |
| Remove Enabled | The equipment can be removed from the network. | Boolean | False |  |
| Transmission Element ID | Transmission Element ID. | Number |  |  |
| contingencyComponent | (True/False) | Boolean |  |  |
| height | Height |  |  |  |
| label height | Label height |  |  |  |
| label width | Label width |  |  |  |
| label x co-ordinate | Label x co-ordinate |  |  |  |
| label y co-ordinate | Label y co-ordinate |  |  |  |
| width | Width |  |  |  |
| x co-ordinate | X co-ordinate |  |  |  |
| Y co-ordinate | Y co-ordinate |  |  |  |

## Linkage

The required links for BusbarSection are defined in table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| BaseVoltage | A link to a BaseVoltage. | Network/Base Voltage |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

# Modeling DynamicElement

## Modeling Approach

Dynamically rated elements such as Transmission Lines, Zero Impedance Branches and Transformers are required to have DynamicElement class defined as a reference for Dynamic Ratings Application. For Transmission Lines and Zero Impedance Branches, DynamicElement is modeled under ACLineSegment class as a child instance. On Transformers, DynamicElement is modeled under PowerTransformer as a child instance.

Figure below shows the parent/child hierarchy of a DynamicElement in IMM.

Figure 49 - Hierarchy for DynamicElement

## Attributes

The attributes for an DynamicElement are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Line? | True if the dynamic element is a line. | Boolean | True |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Transformer | True if the dynamic element is a transformer. | Boolean | False |  |
| Zero Impedance Branch | True if the dynamic element is a zero impedance branch. | Boolean | False |  |

## Linkage

There are no required links for a DynamicElement.

# Classes Only Modeled By ERCOT

Modeling guidelines for the classes described beyond this point are classes that will only be allowed to be submitted by ERCOT. These classes will appear in models posted by ERCOT.

However there are classes that can be modeled by TDSP or ERCOT.  ERCOT would model for an RE.  For example, SVC in section 59.

# Modeling BaseVoltage

## Modeling Approach

BaseVoltage’s are created by ERCOT. These are a collection of Base Voltages which are used to verify that the BusbarSection, BaseVoltage and other voltage attributes in the CIM are given a value existing in the collection.

Figure 50 - BaseVoltage

## Attributes

The following table shows all the attributes that are available for a BaseVoltage.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| Name | Name of the instance of this class | String |  | 69 KV |
| Alias Name | Free text name of the object or instance | String | None |  |
| Color | Color for equipment at this voltage. | Integer | 0 |  |
| Description | Description of the object or instance. | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs | String | None |  |
| Nominal Voltage | The PowerSystemResource's base voltage | Float | None | 69 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

## Linkage

There are no required linkages to the BaseVoltage.

# Modeling Company

## Modeling Approach

Instances of this class are created by ERCOT based on the Registration Information. A Company is a legal entity that owns and operates power system resources and is a party to interchange and transmission contracts.

Figure 51 - Company

## Attributes

The following table shows all the attributes that are available for a Company.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Name | Name of the instance of this class | String |  | CB_1 |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Company Type | The type of company, e.g.: pool, municipal, private. | String | None |  |
| Cooperative | Cooperative boolean. | Boolean | False |  |
| DUNS | DUNS Number | String | None |  |
| Description | Description of the object or instance. | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None |  |
| Municipality | Municipality boolean. | Boolean | False |  |
| PSS/E ID | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly number owners. | Number | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Primary Phone | Primary Phone number for contact. | String | None |  |
| QSE ID | A 14 character QSE ID used for ERCOT LFC. | String | None |  |
| QSE OPA ID | A 6 character QSE OPA ID for the QSE operating in the QSE Simulator. | String | None |  |
| Secondary Phone | Secondary Phone number for contact. | String | None |  |
| Transmission Element ID | Transmission Element ID. | Number | None |  |

## Linkage

There are no required linkages to the Company.

# Modeling SubgeographicalRegion

## Modeling Approach

SubgeographicalRegion’s can be created only by ERCOT. It is a subset of a geographical region of a power system network model.

Figure 52 - SubGeographicalRegion

## Attributes

The following table shows all the attributes that are available for a SubGeographicalRegion.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Name | Name of the instance of this class | String |  | CB_1 |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Description | Description of the object or instance. | String | None |  |
| PSS/E ID | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly number Alternate Areas and Zones. | Integer | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| is WeatherZone | Indicates whether a SubGeographicalRegion is a Weather Zone. | Boolean | False |  |

## Linkage

There are no required links to the SubgeographicalRegion.

# Modeling Geographical Region

## Modeling Approach

Geograpraphical Regions are created by ERCOT. A GeographicalRegion represents a region of a power system network model. Examples are “ERCOT Substations”, “ERCOT-AC Lines”, “ERCOT-Series Compensators”.

Figure 53 - GeographicalRegion

## Attributes

The following table shows all the attributes that are available for a GeographicalRegion.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Name | Name of the instance of this class | String |  | ERCOT Substations |
| Alias Name | Free text name of the object or instance | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

## Linkage

There are no required links to the GeographicalRegion

# Modeling Market Objects

Market Objects include classes of the type:

- SettlementHUB

- AggregateHUB

- HUBBus

- PricingVector

- ResourceNode

- EPSMeter

- SettlementLoadZone

- SettlementNOIELoadZone

## Modeling Approach for SettlementHUB

This section describes the approach for modeling a SettlementHUB. SettlementHUB’s are modeled by ERCOT. A SettlementHUB is a designated Settlement Point for an ERCOT HUB.The SettlementHUB should only be contained within an instance of class sysOrphan, named “ERCOT_Settlement_Hubs”. There are four SettlementHUBs currently defined in ERCOT Model

- HB_HOUSTON

- HB_NORTH

- HB_SOUTH

- HB_WEST

Figure 54 - SettlementHub

### Attributes

The following table shows all the attributes that are available for a SettlementHub.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | HB_HOUSTON |
| Alias Name | Free text name of the object or instance | String | None |  |
| Local Name | The localName is a human readable name of the object | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs | String | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage

There are no required links.

## Modeling Approach for AggregateHUB

This section describes the approach for modeling an AggregateHUB. AggregateHUB’s are modeled by ERCOT. There are two AggregateHubs “HB_HUBAVG” and “HB_BUSAVG”  defined in the ERCOT model based on the HUB Calculation Methods.

### HB_HUBAVG

The HB_HUBAVG for both Day-Ahead and Real-Time is the simple average of four prices from the applicable time period: the North 345 kV Hub price, the South 345 kV Hub price, the Houston 345 kV Hub price, and the West 345 kV Hub price.

Like SettlementHUB’s, this AggregateHUB should only be contained within an instance of class sysorphan named “ERCOT_Settlement_Hubs”.

#### Attributes

Attributes for a AggregateHub are shown in the table below..

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |
| AggregateHub.hubCalculationMethod | HubCalculationMethod should be set to ERCOT_HUBS | Enumeration | None. |

#### Linkage

Below are the required linkages to AggregateHub.

| AssociationName | Class | Description |
| --- | --- | --- |
| AggregateHub.SettlementHUB | SettlementHUB | In this particular case all the SettlementHubs that are defined under “ERCOT_Settlement_Hubs” must be associated to “ERCOT_HUB_AVG”. |

### HB_BUSAVG

The HB_BUSAVG is the simple average of the Hub Bus prices for each hour of the Settlement Interval of the DAM in the Day-Ahead and is the simple average of the time weighted Hub Bus prices for each 15-minute Settlement Interval in Real-Time, for each Hub Bus included in this Hub.

Like SettlementHUB’s, this AggregateHUB should only be contained within an instance of class sysorphan  named “ERCOT_Settlement_Hubs”.

#### Attributes

Attributes for a AggregateHub are shown in the table below.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |
| AggregateHub.hubCalculationMethod | HubCalculationMethod should be set to ALL_ERCOT_345KV_HUBBUSES | Enumeration | None. |

#### Linkage

| AssociationName | Class | Description |
| --- | --- | --- |
| AggregateHub.SettlementHUB | SettlementHUB | In this particular case all the SettlementHubs that are defined under “ERCOT_Settlement_Hubs” must be associated to “ERCOT_345KV_HUBBUSES_AVG”. |

## Modeling Approach for HUBBus

This section describes the approach for modeling a HUBBus. HUBBus’ are modeled by ERCOT. A HUBBus by definition is an energized Electrical Bus or group of energized Electrical Buses defined as a single element in the Hub definition.

A HUBBus can be associated to de-energized Electrical Buses, but the LMP of these Electrical Buses are ignored when calculating the HUBBus price.

HUBBus needs to be contained within an instance of the class SettlementHUB.

Figure 55 - HubBus

#### Attributes

Attributes for a HubBus are shown in the table below.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |

#### Linkage

| AssociationName | Class | Description |
| --- | --- | --- |
| HUBBus.SettlementHub | SettlementHUB | HUBBus needs to be contained in an instance of the class SettlementHUB |
| ConnectivityNodeGroup.HasAHUBBus | ConnectivityNode | “ConnectivityNodeGroup.HasAHUBBus” is a Required Linkage. HUBBus must be associated to a ConnectivityNodeGroup that has at least one ElectricalBus under it. If a HUBBus is associated to more than one ConnectivityNodeGroups then all the associated ConnectivityNodeGroups must belong to the same station. |

## Modeling Approach for PricingVector

This section describes the approach for modeling a PricingVector. PricingVector’s are modeled by ERCOT. PricingVector is the location where the metered price is calculated. PricingVector needs to be always contained with in an instance of the class ElectricalBus.

PricingVector’s name should be unique with in the model. PricingVector’s can not be connected to BusbarSection or EndCap.

Figure 56 - PricingVector

### Attributes

Attributes for a PricingVector are shown in the table below.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |
| teid | Transmission Element ID | Integer | Autopopulated |
| Positive Flow In | Determines metered direction of EPS Meter | Boolean | True |

### Linkages

| AssociationName | Class | Description |
| --- | --- | --- |
| PricingVector.ElectricalBus | ElectricalBus | PricingVector needs to be always contained in an instance of the class ElectricalBus. |
| PricingVector.Terminal | Terminal | PricingVector must be associated to a terminal where the price is calculated. |

## Modeling Approach for EPSMeter

This section describes the approach for modeling an EPSMeter. EPSMeters are modeled by ERCOT. EPSMeter is a meter polled directly by ERCOT for use in the financial settlement of the market. EPSMeter needs to be contained only with in the instance of class Sysorphan  with EPS_Meter as its name.

### Attributes

Attributes for a EPSMeter are shown in the table below.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |
| AcceptedStatus | EPS meter location has been accepted by settlements. | Boolean | false |
| RID | Resource number for EPS meter Identifier | String | Autopopulated |
| teid | Transmission Element ID | Integer | Autopopulated |

### Linkage

| AssociationName | Class | Description |
| --- | --- | --- |
| PricingVector.EPSMeter_HasA | PricingVector | PricingVector should be associated to a EPSMeter. |

## Modeling Approach for ResourceNode

This section describes the approach for modeling a ResourceNode. ResourceNode’s are modeled by ERCOT.  ResourceNode’s are used to identify ElectricalBuses at which a Settlement Point Price is calculated and used in Settlement.  ResourceNode needs to be always contained within an instance of the class ElectricalBus.  In order to properly locate ResourceNodes, ERCOT may create and maintain new ElectricalBuses.

ResourceNode’s should not be associated to a LoadResource or a ControllableLoadResource. ResourceNode’s that are associated to a PrivateUseNetwork should not be connected to a Physical GeneratingUnit. Every GeneratingUnit should be associated to ResourceNode unless the GeneratingUnit is part of a DCTie or Non-Modeled-Generation or Block Load Transfer or Retired or Mothballed.

Figure 57 - ResourceNode

### Attributes

Attributes for a ResourceNode are shown in the table below.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |
| Alias Name | Free text name of the object or instance | String | None |
| Local Name | The localName is a human readable name of the object | String | None |
| Model Resource ID | A Model Authority issues mRIDs | String | None |

### Linkage

| AssociationName | Class | Description |
| --- | --- | --- |
| ResourceNode.ElectricalBus | ElectricalBus | ResourceNode needs to be always contained in an instance of the class ElectricalBus. |

## Modeling Approach for SettlementLoadZone

The ERCOT CIM model defines a SettlementLoadZone as Settlement Point for ERCOT Load Zones. ERCOT will designate Settlement Load Zones to specific zones allowing for additional subdivision of the network to facilitate analyses and documentation.

SettlementLoadZone needs to be contained only with in the instance of class sysorphan  with “ERCOT Settlement Zones” as its name.

The SettlementLoadZones will be pre-populated and maintained by ERCOT in the Information Model Manager. This data may change with future settlement load zones additions.

Each SettlementLoadZone name and SettlementLoadZone  PSS/E ID must be unique within the Information Model Manager.  These values cannot be duplicated. See figure below as an example.

Figure 58 - SettlementLoadZone

### Attributes

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| PSS/E ID | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage

| AssociationName | Class | Description |
| --- | --- | --- |
| Substation.SettlementLoadZone | Substation | All the Substations with Loads must be associated to at least one SettlementLoadZone |

## Modeling Approach for SettlementNOIELoadZone

The ERCOT CIM model defines a SettlementNoieLoadZone as Settlement Point for ERCOT NOIE Load Zones.

ERCOT will designate SettlementNoieLoadZones to specific zones allowing for additional subdivision of the network to facilitate analyses and documentation.

The SettlementNoieLoadZones will be pre-populated and maintained by ERCOT in the Information Model Manager. This data may change with future settlement load zones additions.

Each SettlementNoieLoadZone name and SettlementNoieLoadZone  PSS/E ID must be unique within the Information Model Manager.  These values cannot be duplicated. See figure below as an example.

SettlementNOIELoadZone needs to be contained only with in the instance of class Sysorphan with “NOIE_Load_Zones” as its name.

Figure 59 - SettlementNOILoadZone

### Attributes

| Attribute | Description | Data Type | Default Value |
| --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |
| Alias Name | Free text name of the object or instance. | String | None |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |
| PSS/E ID | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String | None |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |

### Linkage

There are no required links.

# Modeling Generation

This section will cover modeling of GeneratingUnits, CombinedCyclePlants, ControllableLoadResources and LoadResources.

## Modeling Generating Unit

GeneratingUnit is modeled using a ResourceController, GeneratingUnit, and SynchronousMachine. Figure below shows a GeneratingUnit as modeled in Information Model Manager, with parent/child associations labeled. In this figure a ResourceController named GEN_RC is modeled under a Substation. A GeneratingUnit, GEN is located under the ResourceController, GEN_RC. Within the same Substation, under VoltageLevel, 13.8 a SynchronousMachine is modeled.

Figure 60 – Modeled Generating Unit with Parent/Child Associations

### Modeling Approach for Resource Controller

The ERCOT CIM data dictionary defines a ResourceController as a plant controller. A ResourceController is modeled under a Substation.  Figure below shows a ResourceController in Information Model Manager, with parent/child associations labeled. Every GeneratingUnit in the network model must be contained within a ResourceController. Only in the case of CombinedCyclePlants, multiple GeneratingUnits may be present within the same ResourceController.  Refer to the above figure for the hierarchy of the ResourceController.

#### Attributes

The attributes for a ResourceController are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Alias Name | Free text name of the object or instance | String |  |  |
| Description | Description of the object or instance | String |  |  |
| FrequencyBias - ResourceController | Frequency Bias | Float |  |  |
| Gross - ResourceController | Gross | Boolean |  |  |
| teid | Transmission Element ID | Integer |  |  |
| externalJointUnit | External Jointly Owned Unit | Boolean |  |  |
| jointUnit | Jointly Owned Unit | Boolean |  |  |
| physical | Physical Unit | Boolean |  |  |
| Latitude | Latitude coordinates. | Float |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Longitude | Longitude coordinates. | Float |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |

#### Linkage

The required links for a ResourceController are defined in defined in the table.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

### Modeling Approach for Generating Unit

The ERCOT CIM model defines a GeneratingUnit as a single or set of SynchronousMachines for converting mechanical power into alternating-current power. A GeneratingUnit is modeled under a ResourceController. An emergency and a normal rampratecurve must be modeled under every market participating GeneratingUnit. Modeling of curves in is covered in detail elsewhere in this document.

In the ERCOT CIM model a GeneratingUnit can be of five different types: HydroGeneratingUnit, NuclearGeneratingUnit, ThermalGeneratingUnit, SolarGeneratingUnit, and WindGeneratingUnit. Below figure below shows a GeneratingUnit in Information Model Manager, with parent/child associations labeled.

Figure 61 – Modeled Generating Unit with Parent/Child Association

#### Attributes

The attributes for all five types of GeneratingUnit are shown in the table below.  There is an additional four columns representing each type of GeneratingUnit by which it will specified if an attribute is used within that type. The labels of these columns are H for HydroGeneratingUnits, N for NuclearGeneratingUnits, T for ThermalGeneratingUnits, S for SolarGenerationUnits, and W for WindGeneratingUnits.

| Attribute | Description | Data Type | Default Value | Sample Data | H | N | T | W | S |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  | X | X | X | X | X |
| teid | Transmission Element ID | Integer | Auto-populated |  | X | X | X | X | X |
| coldStartTime – GeneratingUnit | coldStartTime | Float | False |  | X | X | X | X | X |
| commercialOperationsDate – GeneratingUnit | Commericial operations date. | Date | None |  | X | X | X | X | X |
| controlPulseHigh – GeneratingUnit | Pulse high limit which is the largest control pulse that the unit can respond to. | Seconds | 0.5 |  | X | X | X | X | X |
| controlPulseLow – GeneratingUnit | Pulse low limit which is the smallest control pulse that the unit can respond to. | Seconds | 0.5 |  | X | X | X | X | X |
| controlResponseRate – GeneratingUnit | MW change for a control pulse of one second in the most responsive loading level of the unit. | PowerROCPerSec | 2 |  | X | X | X | X | X |
| efficiency | The efficiency of the unit in converting mechanical energy, from the prime mover, into electrical energy. | PU | 1 |  | X | X | X | X | X |
| freqBias – GeneratingUnit | Unit Regulating Frequency Bias as MW per 0.1 Hz. | Float | None |  | X | X | X | X | X |
| freqDevDeadband – GeneratingUnit | Frequency deviation deadband for Feed-Forward correction. | Float | None |  | X | X | X | X | X |
| genOperatingMode – GeneratingUnit | Operating mode for secondary control, e.g.: Off, Manual, Fixed, LFC, AGC, EDC, RPN, MRN, or REG. | EnumGeneratorOperatingMode | 0 |  | X | X | X | X | X |
| governorMPL – GeneratingUnit | Governor motor position limit. | PU | 1 |  | X | X | X | X | X |
| Governor Speed Changer Droop | Governor Speed Changer Droop. | PerCent | 5 |  | X | X | X | X | X |
| highReasonabilityLimit – GU | High reasonability limit. | ActivePower | None |  | X | X | X | X | X |
| Hot-to-intermediate Time (Seasonal) - GU | Hot-to-intermediate time (Seasonal). | Float | None |  | X | X | X | X | X |
| Hot Start Time – GeneratingUnit | Hot start time. | Float | None |  | X | X | X | X | X |
| Intermediate-to-Cold Time (Seasonal) - GU | Intermediate-to-cold time (Seasonal). | Float | None |  | X | X | X | X | X |
| Low Reasonability Limit – GeneratingUnit | Low reasonability limit. | ActivePower | None |  | X | X | X | X | X |
| Low Reasonability Ramp Rate Limit – GeneratingUnit | Low reasonability ramp rate limit. | ActivePower | None |  | X | X | X | X | X |
| Maximum Daily Starts (Seasonal Parameter) - GU | Maximum daily starts (seasonal parameter). | Float | None |  | X | X | X | X | X |
| Maximum Operating MW – GeneratingUnit | This is the maximum operating MW limit the dispatcher can enter for this unit. | ActivePower | None |  | X | X | X | X | X |
| Maximum On-Line Time – GeneratingUnit | Maximum On-Line time. | Float | None |  | X | X | X | X | X |
| Maximum Weekly Energy (seasonal parameter) - GU | Maximum weekly energy (seasonal parameter). | Float | None |  | X | X | X | X | X |
| Maximum Weekly Starts (seasonal parameter) - GU | Maximum weekly starts (seasonal parameter). | Float | None |  | X | X | X | X | X |
| Minimum Operating MW – GeneratingUnit | This is the minimum operating MW limit the dispatcher can enter for this unit. | ActivePower | 0 |  | X | X | X | X | X |
| Minimum Off-Line Time – GeneratingUnit | Minimum Off-Line time. | Float | None |  | X | X | X | X | X |
| Minimum On-line Time – GeneratingUnit | Minimum On-Line time. | Float | None |  | X | X | X | X | X |
| Model Detail | Detail level of the generator model data. | Classification | 3 |  | X | X | X | X | X |
| Penalty Factor – GeneratingUnit | The unit's penalty factor as calculated by the Network Sensitivity function. | PenaltyFactor | 1 |  | X | X | X | X | X |
| Primary Fuel Type – GeneratingUnit | Primary fuel type. | EnumERCOTFuelType | None |  | X | X | X | X | X |
| Qualification Status – GeneratingUnit | Qualification status. | Boolean | FALSE |  | X | X | X | X | X |
| Seasonal Max Sustainable Rating - GU | Seasonal maximum sustainable rating. | ActivePower | None |  | X | X | X | X | X |
| Seasonal Min Emergency Rating - GU | Seasonal minimum emergency rating. | ActivePower | None |  | X | X | X | X | X |
| Seasonal Min Sustainable Rating - GU | Seasonal minimum sustainable rating. | ActivePower | None |  | X | X | X | X | X |
| Secondary Fuel Type – GeneratingUnit | Secondary fuel type. | EnumERCOTFuelType | None |  | X | X | X | X | X |
| Step Change – GeneratingUnit | Unit allowable step change which specifies the maximum stored energy in the boiler. | ActivePower | 5 |  | X | X | X | X | X |
| Alias Name | Free text name of the object or instance. | String | None |  | X | X | X | X | X |
| Alloc Spin Res MW – GeneratingUnit | The planned unused capacity (spinning reserve) which can be used to support emergency load. | ActivePower | None |  | X | X | X | X | X |
| Auto Cntrl Margin MW – GeneratingUnit | The planned unused capacity which can be used to support automatic control overruns, in MW. | ActivePower | None |  | X | X | X | X | X |
| Base MW – GeneratingUnit | For dispatchable units, this value represents the economic MW basepoint, for units that are not dispatchable, this value represents the fixed generation value. The value must be between the operating low and high limits. | ActivePower | None |  | X | X | X | X | X |
| Black Start – GeneratingUnit | Determines if a unit is qualified to black start. | Bool | FALSE |  | X | X | X | X | X |
| Block Load Transfer – GeneratingUnit | Block load transfer. | Boolean | FALSE |  | X | X | X | X | X |
| Control Deadband – GeneratingUnit | Unit control error deadband. When a unit's desired MW change is less than this deadband, then no control pulses will be sent to the unit. | ActivePower | None |  | X | X | X | X | X |
| DAM_Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | FALSE |  | X | X | X | X | X |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | FALSE |  | X | X | X | X | X |
| Description | Description of the object or instance. | String1000 | None |  | X | X | X | X | X |
| Disp Reserve Flag – GeneratingUnit | Display Reserve Flag | Boolean | FALSE |  | X | X | X | X | X |
| Energy Min MW – GeneratingUnit | Energy Minimum MW. | HeatPerHour | None |  | X | X | X | X | X |
| Fast Start Flag – GeneratingUnit | Fast Start Flag. | Boolean | FALSE |  | X | X | X | X | X |
| Frequency DeadBand Hz – GeneratingUnit | Allowable deviation of the unit frequency. | Float | None |  | X | X | X | X | X |
| Fuel Priority – GeneratingUnit | Fuel Priority. | Priority | None |  | X | X | X | X | X |
| Generator Control Mode | Select the unit control mode as Setpoint (S) or Pulse (P). | EnumGeneratorControlMode | None |  | X | X | X | X | X |
| Gen Control Source | The source of controls for a generating unit, i.e., Unavailable, Off-AGC, On-AGC, Plant Control. | EnumGeneratorControlSource | None |  | X | X | X | X | X |
| High Control Limit – GeneratingUnit | High limit for secondary (AGC) control. | ActivePower | None |  | X | X | X | X | X |
| High Reasonability Ramp Rate Limit – GeneratingUnit | High reasonability ramp rate limit. | ActivePower | None |  | X | X | X | X | X |
| Initial MW – GeneratingUnit | Default generation for use when the operating type is fixed. An entry is required because the unit may later be placed in a fixed operating type mode even though that may not be the initial selection. | ActivePower | None |  | X | X | X | X | X |
| Intermediate Start Time – GeneratingUnit | Intermediate start time. | Float | None |  | X | X | X | X | X |
| localName | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  | X | X | X | X | X |
| Long PF – GeneratingUnit | Economic participation factor based on the slope of the unit incremental cost curve at the current operating point of the unit. | ParticipationFactor | None |  | X | X | X | X | X |
| Low Control Limit – GeneratingUnit | Low limit for secondary (AGC) control. | ActivePower | None |  | X | X | X | X | X |
| Lower Ramp Rate – GeneratingUnit | Lower Ramp Rate. | PowerROCPerMin | None |  | X | X | X | X | X |
| Max Capacity Limit | Maximum possible capacity. | Integer | None |  | X | X | X | X | X |
| maxDownRampRate | Default maximum ramp rate in down direction. | Float | None |  | X | X | X | X | X |
| maximumAllowableSpinngReserve | Maximum allowable spinning reserve. Spinning reserve will never be considered greater than this value regardless of the current operating point. | ActivePower | None |  | X | X | X | X | X |
| maximumCurrentCapacity | (MW) Default current max capacity. | Float | None |  | X | X | X | X | X |
| maximumCurrentCapacityRef | (MW) Reference value for Advisory ECO maximum. | Float | None |  | X | X | X | X | X |
| maximumEconomicMW | Maximum high economic MW limit that should not exceed the maximum operating MW limit. | ActivePower | None |  | X | X | X | X | X |
| maximumEconomicMWRef | Maximum economic dispatch reference value. | Float | None |  | X | X | X | X | X |
| maxResponseReserveLimit | Maximum responsive reserve limit MW. | Float | None |  | X | X | X | X | X |
| maxSpinReserveContribution | Maximum Spinning Reserve Contribution. | Float | None |  | X | X | X | X | X |
| maxUpRampRate | Default maximum ramp rate in up direction. | Float | None |  | X | X | X | X | X |
| minCapacityLimit | The Lowest continuous economical capacity limit. | Integer | None |  | X | X | X | X | X |
| minimumEconomicMW | Low economic MW limit that must be greater than or equal to the minimum operating MW limit. | ActivePower | 0 |  | X | X | X | X | X |
| minimumOffTime | Minimum time interval between unit shutdown and startup. | Seconds | None |  | X | X | X | X | X |
| minResponseReserveLimit | Minimum responsive reserve limit MW. | Float | None |  | X | X | X | X | X |
| mRID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String100 |  |  | X | X | X | X | X |
| normalPF | Economic participation factor based on the slope of the unit incremental cost curve at the current operating point of the unit. | ParticipationFactor | 1 |  | X | X | X | X | X |
| onlineThresholdDeadbandPercent | Unit online threshold deadband percentage. | Float | None |  | X | X | X | X | X |
| OUSPriority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer | None |  | X | X | X | X | X |
| pathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String500 | None |  | X | X | X | X | X |
| psseid | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String2 | None |  | X | X | X | X | X |
| raiseRampRate | Raise Ramp Rate | PowerROCPerMin | None |  | X | X | X | X | X |
| ratedGrossMaxMW | The unit's gross rated maximum capacity (Book Value). | ActivePower | None |  | X | X | X | X | X |
| ratedGrossMinMW | The gross rated minimum generation level which the unit can safely operate at while delivering power to the transmission grid. | ActivePower | None |  | X | X | X | X | X |
| ratedNetMaxMW | The net rated maximum capacity determined by subtracting the auxiliary power used to operate the internal plant machinery from the rated gross maximum capacity. | ActivePower | None |  | X | X | X | X | X |
| reliabilityMustRun | TRUE - Unit is qualified to reliability must run. | Boolean | FALSE |  | X | X | X | X | X |
| reserveDiscountFactor | Reserve Discount Factor. | Float | None |  | X | X | X | X | X |
| resourceCategory | Type of resource. | String50 | None |  | X | X | X | X | X |
| RUC_Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | FALSE |  | X | X | X | X | X |
| RUC_Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | TRUE |  | X | X | X | X | X |
| shortPF | Short Participation Factor | ParticipationFactor | None |  | X | X | X | X | X |
| spinningReserveMax | Max spinning reserve from this unit. Usuallly derived from response rate. Applicable only to non-peakers. | Float | None |  | X | X | X | X | X |
| spinReserveRamp | Spin Reserve Ramp | PowerROCPerMin | None |  | X | X | X | X | X |
| startupTime | Time it takes to get the unit on-line, from the time that the prime mover mechanical power is applied. | Seconds | None |  | X | X | X | X | X |
| synCondenserCapable | Flag indicating whether the Resource is Synchronous Condenser capable. | Boolean | FALSE |  | X | X | X | X | X |
| tieLinePF | Unit frequency and tie-line regulation participation factor. | ParticipationFactor | 1 |  | X | X | X | X | X |
| wfrmcr | Wind /McCamey Flowgate Rights. | Boolean | FALSE |  | X | X | X | X | X |
| hydroUnitWaterCost | The equivalent cost of water that drives the hydro turbine, expressed as (dollars/cubic meter). | Float | None |  | X |  |  |  |  |
| boilerEfficiency | (%) Boiler efficiency factor. The heat rate curve will be divided by this factor to account for a dirty boiler or any other cause for loos of efficiency of the heat cycle. | Float | None |  |  |  | X |  |  |
| boilerColdStartEnergy | Boiler cold start engergy (MBTU). | Float | None |  |  |  | X |  |  |
| oMCost | Operating and maintenance cost for the thermal unit. | CostPerHeatUnit | None |  |  |  | X |  |  |
| turbineColdStartEnergy | Turbine cold start energy MBTU (used by UC only). | Float | None |  |  |  | X |  |  |

#### Linkage

The required links for all GeneratingUnit types are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| DCTie | Should be populated only when the unit is part of a DC Tie. | Network/DCTies |
| GenerationType | Type of GeneratingUnit ex: COAL, NUC | List_Information/GenerationType |
| PrivateAreaNetwork | Should be populated only when the unit is part of a PUN or if the unit is retired, mothballed or blockloadtransfer. | Network/PrivateAreaNetworks |
| ResourceNode | All market participating gen units should have this populated | Network/ERCOT Texas Network/ERCOT Substations/Weather_Zone/Substation/Voltage_Level/ConnectivityNodeGrou/ConnectivityNode/ElectricalBus/ |
| SubLoadArea | All units should be part of a subloadarea | Schedules/Load Area Schedules |
| PowerSystemResource-Operatorship | Operatorship | Network/Companies |
| PowerSystemResource-Ownership | Ownership | Network/Companies |

### Modeling Approach for Synchronous Machine

The ERCOT CIM data dictionary defines a SynchronousMachine as an electromechanical device that operates synchronously with the network. It is a single machine operating either as a generator or synchronous condenser or pump. In the ERCOT CIM model a SynchronousMachine is modeled under a VoltageLevel.   Every SynchronousMachine may have a MVArCapabilityCurve defined as a child under the SynchronousMachine. Modeling of MVarCapabilityCurve is described elsewhere in this document. A single Terminal must be modeled under a SynchronousMachine. One or many SCADA measurement/s may be modeled under the terminal.  Figure below shows a SynchronousMachine in Information Model Manager Model hierarchy.

Figure 62 – Synchronous Machine

#### Attributes

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| teid | Transmission Element ID | Integer | Auto-populated |  |
| inertia | The energy stored in the rotor when operating at rated speed. This value is used in the accelerating power reference frame for operator training simulator solutions. | Inertia | 5 |  |
| xSubtrans | Subtransient reactance. | Reactance | None |  |
| xTrans | Transient reactance. | Resitance | False |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| aVRToManualLag | Time delay, in seconds, required when switching from AVR to manual for a lagging MVAr violation. | Seconds | None |  |
| aVRToManualLead | Time delay, in seconds, required when switching from Automatic Voltage Regulation to Manual for a leading MVAr violation. | Seconds | None |  |
| baseMVAr | Default base MVAr value. This value represents the initial MVAr that can be used by any application function. | ReactivePower | None |  |
| condenserMW | Condensor MW | ActivePower | None |  |
| coolantCondition | Temperature or pressure of coolant medium. | Float | None |  |
| coolantType | Method of cooling the machine, e.g., air, hydrogen gas, water. | EnumCoolantType | None |  |
| DAM_Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | FALSE |  |
| DAM_Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | FALSE |  |
| description | Description of the object or instance. | String1000 | None |  |
| Latitude | Latitude coordinates. | Float | None |  |
| loadBasedRegulationEnabled | T = Load based voltage regulation enabled. | Boolean | False |  |
| localName | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | Float | None |  |
| manualToAVR | Time delay, in seconds, required when switching from Manual to Automatic Voltage Regulation. This value is used in the accelerating power reference frame for powerflow solutions. | Seconds | None |  |
| maximumKV | Maximum kV limit for the unit. | Voltage | None |  |
| maximumMVAr | Maximum MVAr limit. This is the maximum (nameplate) limit for the unit. | ReactivePower | None |  |
| minimumKV | Minimum kV limit for the unit. | Voltage | None |  |
| minimumMVAr | Minimum MVAr limit for the unit. | ReactivePower | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | None |  |
| operatingMode | Current mode of operation, i.e., generator or condenser. | EnumSynchronousMachineOperatingMode | None |  |
| OUSPriority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer | None |  |
| pathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String500 | None |  |
| phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | PhaseCode | None |  |
| psseid | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String2 | None |  |
| r | Positive sequence resistance of the synchronous machine. | Resistance | None |  |
| r0 | Zero sequence resistance of the synchronous machine. | Resistance | None |  |
| ratedMVA | Nameplate MVA rating for the unit. | ApparentPower | None |  |
| Reduce | Attribute will be used to mark generators on low voltage systems that should be reduced and attached directly to the Transmission Level. | Boolean | FALSE |  |
| referencePriority | Priority of unit for reference bus selection. 0 = don t care (default) 1 = highest priority. 2 is less than 1 and so on. | Integer | None |  |
| remove | The equipment is removed from the network. | Boolean | FALSE |  |
| removeEnable | The equipment can be removed from the network. | Boolean | FALSE |  |
| RUC_Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | None |  |
| RUC_Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | None |  |
| type | Modes that this synchronous machine can operate in, i.e., as a generator, condenser, or both. | EnumSynchronousMachineType | None |  |
| varManual | Manually entered MVAR overrides capability curve. | Boolean | False |  |
| x | Positive sequence reactance of the synchronous machine. | Reactance | 0.12 |  |
| x0 | Zero sequence reactance of the synchronous machine. | Reactance | 0.05 |  |
| xDirectSubtrans | Direct-axis subtransient reactance, also known as X'd. | Reactance | None |  |
| xDirectSync | Direct-axis synchronous reactance. The quotient of a sustained value of that AC component of armature voltage that is produced by the total direct-axis flux due to direct-axis armature current and the value of the AC component of this current, the machine running at rated speed. (Xd) | Reactance | None |  |
| xDirectTrans | Direct-axis transient reactance, also known as X”d. | Reactance | None |  |
| xQuadSubtrans | Quadrature-axis subtransient reactance, also known as X”q. | Reactance | None |  |
| xQuadSync | Quadrature-axis synchronous reactance (Xq) , the ratio of the component of reactive armature voltage, due to the quadrature-axis component of armature current, to this component of current, under steady state conditions and at rated frequency. | Reactance | None |  |
| xQuadTrans | Quadrature-axis transient reactance, also known as X'q. | Reactance | None |  |

#### Linkage

The required links for a SynchronousMachine are defined below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| BaseVoltage | Link to the BaseVoltage the SynchronousMachine belongs to. | Network/Base Voltage |
| AccuracyClass | A link to an AccuracyClass which should define the accuracy of a measurement. |  |
| LoadBasedRegulationCurve | Link to the LoadBasedRegulationCurve |  |
| Regulates (Terminal) | Terminal that is connected to this SynchronousMachine |  |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

## Modeling Combined Cycle PLant

This section concentrates on the modeling of combined cycle plants in the ERCOT CIM model, Instances of type CombinedCyclePlant, LogicalConfiguration, Configuration, TransState and ConfigurationMember are utilized when modeling a CombinedCyclePlant. Figure below shows a complete CombinedCyclePlant as modeled in Information Model Manager Hierarchy, with parent/child associations labeled. As can be seen in figure a CombinedCyclePlant named __SUB_CC is modeled under the ResourceController, RC. All GeneratingUnits that are part of __SUB_CC are modeled within the ResourceController RC as well. The following sections will describe the modeling of each of these classes in detail.

Figure 63 –Combined Cycle with Parent/Child Associations

### Modeling Approach for Combined Cycle Plant

The ERCOT CIM data dictionary defines a CombinedCyclePlant as a set of combustion turbines and steam turbines where the exhaust heat from the combustion turbines is recovered to make steam for the steam turbines, resulting in greater overall plant efficiency.  Figure below shows a Combined Cycle Plant modeled in Information Model Manager, with parent/child associations labeled. Notice the presence of a Pseudoterminal under the CombinedCyclePlant, SUB_CC. This Psuedoterminal does not connect to the network topology and is solely utilized for the purpose of readily displaying SCADA/ICCP telemetry being provided for the CombinedCycplePlant. Modeling of Pseudoterminals is described in detail elsewhere in the document.

Figure 64 – Modeled Combined Cycle Plant with Parent/Child Association

#### Attributes

The attributes for a CombinedCyclePlant are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| teid | Transmission Element ID | Integer | Auto-populated |  |
| commercialOperationsDate | Date commercial operations started. | Date | None |  |
| LogicalResourceNodeName | Logical resource node name. | String12 | None |  |
| blockLoadTransfer | Block load transfer. | Boolean | FALSE |  |
| combCyclePlantRating | The combined cycle plant's output rating, in MW | ActivePower | None |  |
| GstTpspiMax | GstTpspiMax | Float | None |  |
| GstTpspiMin | GstTpspiMin | Float | None |  |
| GtMax | GtMax | Float | None |  |
| GtMin | GtMin | Float | None |  |
| Latitude | Latitude coordinates. | Float | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | Float | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |
| qualificationStatus | Qualification status. | Boolean | FALSE |  |
| resourceCategory | Type of resource. | String50 | None |  |
| wfrmcr | Wind /McCamey Flowgate Rights.. | Boolean | FALSE |  |

#### Linkage

The required links for a CombinedCyclePlant are defined in the table.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

### Modeling Approach for Logical Configuration

The ERCOT CIM model utilizes an LogicalConfiguration as a collection of all configurations  in a Combined Cycle Plant that can be physically operated using the primary combustion turbines and primary steam turbines. As mentioned earlier one or many LogicalConfiguration/s can be present within a CombinedCyclePlant. - Figure below shows one such CombinedCyclePlant  as modeled in Information Model Manager hierarchy with 2/3 LogicalConfigurations.

Figure 65 – Modeled Logical Configuration with Parent/Child Association

#### Attributes

The attributes for a LogicalConfiguration are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Alias Name | Free text name of the object or instance | String |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |

#### Linkage

The required links for a LogicalConfiguration are defined below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Combined Cycle Plant | The Combined Cycle Plant link is used in order to associate Logical Configuration a with its respective Combined Cycle Plant | Network/ERCOT Substations/Weather_Zone/Substation/Resource_Controller |

### Modeling Approach for Configuration

The ERCOT CIM model utilizes instances of type Configuration to define the constituents and operational characteristics of the various combinations of combustion turbines and steam turbines a CombinedCyclePlant can operate with. In the ERCOT model as mentioned in the earlier sections, a Configuration can be created under a LogicalConfigurtion only. Every configuration must contain two (Emergency & Normal) RampRateCurves, and one/many ConfigurationMembers. Modeling of RampRateCurves is covered in detail elsewhere in the document. Within a single CombinedCyclePlant, every Configuration must be able to startup, shut down or transition to/from other Configuration in the same CombinedCyclePlant. Figure below shows a Combined Cycle Plant.

Figure 66 - Configuration

#### Attributes

The attributes for a Configuration are shown in below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Alias Name | Free text name of the object or instance | String |  |  |
| highReasonabilityLimit | High reasonability limit. | ActivePower | None |  |
| highReasonabilityRampRateLimit | High reasonability ramp rate limit. | ActivePower | None |  |
| hotintTime | Hot-to-intermediate time (Seasonal). | Float | None |  |
| hotStartTime | Hot start time. | Float | None |  |
| intColdTime | Intermediate-to-cold time (Seasonal). | Float | None |  |
| intStartTime | Intermediate start time. | Float | None |  |
| lowReasonabilityLimit | Low reasonability limit. | ActivePower | None |  |
| lowReasonabilityRampRateLimit | Low reasonability ramp rate limit. | ActivePower | None |  |
| maxDailyStarts | Maximum daily starts (seasonal parameter). | Float | None |  |
| maxONTime | Maximum On-Line time. | Float | None |  |
| maxWeeklyEnergy | Maximum weekly energy (seasonal parameter). | Float | None |  |
| maxWeeklyStarts | Maximum weekly starts (seasonal parameter). | Float | None |  |
| minOFFTime | Minimum Off-Line time. | Float | None |  |
| minONTime | Minimum On-Line time. | Float | None |  |
| primaryConfiguration | Primary configuration? | Boolean | FALSE |  |
| qualificationStatus | Qualification status. | Boolean | FALSE |  |
| seasonalMaxEmergencyRating | Seasonal maximum emergency rating. | ActivePower | None |  |
| seasonalMaxSustainableRating | Seasonal maximum sustainable rating. | ActivePower | None |  |
| seasonalMinEmergencyRating | Seasonal minimum emergency rating. | ActivePower | None |  |
| seasonalMinSustainableRating | Seasonal minimum sustainable rating. | ActivePower | None |  |
| coldStartTime | Cold Start Time | Float | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globaly unique. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |
| ShutdownFlag | Determines whether a Combined Cycle Plant can be shut-down in this Logical Configuration | Boolean | False |  |
| StartupFlag | Determines Whether a Combined Cycle Plant can be started in this Logical Configuration | Boolean | Flase |  |

#### Linkage

The required links for a Configuration are defined in the table below

| Link Name | Description | Path Name |
| --- | --- | --- |
| Logical Configuration | The Combined Cycle Plant link is used in order to associate Configuration a with its respective Logical Configuration | Network/ERCOT Substations/Weather_Zone/Substation/Resource_Controller/Combined_Cycle_Plant/ |

### Modeling Approach for TransState

The ERCOT CIM data dictionary uses  instances of type TransState to define the available transitions  between the various configurations of a  Combine Cycle Configurations. One/many TransStates may be defined for every Configuration within a CombinedCyclePlant. Every TransState is defined as an uptransition when the total number of primary members in the To-configuration are greater than or equal to the same in the From Configurations.  Figure below shows a Trans State modeled in Information Model Manager, with parent/child associations labeled.

Figure 67 - TransState

#### Attributes

The attributes for a TransState are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Alias Name | Free text name of the object or instance. | String |  |  |
| Description | Description of the object or instance | String |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ |
| upTransition | Up Transition | Boolean | False |  |

#### Linkage

The required links for a TransState are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| ToConfig_Configuration | The next Configuration that this configuration can traverse into. | Network/ERCOT Substations/Weather_Zone/Substation/Resource_Controller/Combined_Cycle_Plant/Logical_Configuration |
| FromConfig_Configuration | The current Configuration in which this TransState is under. |  |

### Modeling Approach for Configuration Member

The ERCOT CIM data dictionary utilizes instances of type  ConfigurationMember to identify the ThermalGeneratingUnits that are a member of CCP Configuration instance along with their operational nature (Steam/Gas Turbine) and primary/alternate status of the associated resource. In the ERCOT CIM model, one/many configurationmembers can be defined within a configuration. Figure below shows a ConfigurationMember modeled in Information Model Manager, with parent/child associations labeled.

Figure 68 -  Configuration Member

#### Attributes

The attributes for a ConfigurationMember are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Alias Name | Free text name of the object or instance. | String |  |  |
| Description | Description of the object or instance | String |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| primary | Determines if this is the primary unit in the Configuration that it falls under. | Boolean | FALSE |  |
| steam | Determines if this is a steam generating unit. | Boolean | FALSE |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |

#### Linkage

The required links for a ConfigurationMember are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| ThermalGeneratingUnit | The link determines which Unit is the Configuration Member. | Network/ERCOT Substations/Weather_Zone/Substation/Resource_Controller/Thermal_Generating_unit |
| Configuration | The link determines under which Configuration this Configuration Member falls into. | Network/ERCOT Substations/Weather_Zone/Substation/Resource_Controller/Combined_Cycle_Plant |

# Modeling Controllable Load Resources and Load resources

## Modeling Approach

The ERCOT CIM model defines a LoadResource as a load that is capable of providing Ancillary Service to the ERCOT System. A ControllableLoadResource is a LoadResource capable of controllably reducing or increasing consumption under dispatch control (similar to AGC) and that Information Model Manager immediately responds proportionally to frequency changes (similar to generator governor action).  Figures below show a ControllableLoadResource and LoadResource respectively in Information Model Manager.

Figure 69 – ControllableLoadResource

Figure 70 – LoadResource

## Attributes

The attributes for both ControllableLoadResources and LoadResources are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data | CLR | LR |
| --- | --- | --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |  |  |
| teid | Transmission Element ID | Integer | Auto-populated |  | X | X |
| maxWeeklyEnergy | Maximum weekly energy. | Float | None |  | X | X |
| minNoticeTime | Minimum notice time (seconds). | Float | None |  | X | X |
| Alias Name | Free text name of the object or instance. | String | None |  | X | X |
| blockLoadTransfer | Determines if the device is a block load transfer. | Boolean | False |  | X | X |
| commercialOperationsDate | Date commercial operations started. | Date | None |  | X | X |
| DAM_Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | FALSE |  | X | X |
| DAM_Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | FALSE |  | X | X |
| Latitude | Latitude coordinates. | Float | None |  | X | X |
| loadFreqBias | Regulating Frequency Bias as MW per 0.1 Hz. | Float | None |  | X | X |
| loadFreqDevDeadband | Frequency deviation deadband for Feed-Forward correction (in Hz). | Float | None |  | X | X |
| loadId | A 14 character load ID used in ERCOT LFC. | String14 | None |  | X | X |
| loadSubStationId | ID of load's substation. | String18 | None |  | X | X |
| localName | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  | X | X |
| Longitude | Longitude coordinates. | Float | None |  | X | X |
| maxDailyDeployment | Maximum daily deployments. | Float | None |  | X | X |
| maxInterruptionTime | Maximum interruption time. | Float | None |  | X | X |
| MaxPowerConsumption | Maximum power consumption for resource. | Float | None |  | X | X |
| maxWeeklyDeployment | Maximum weekly deployments. | Float | None |  | X | X |
| minInterruptionTime | Minimum interruption time. | Float | None |  | X | X |
| MinPowerConsumption | Minimum power consumption for resource. | Float | None |  | X | X |
| minRestorationTime | Minimum restoration time. | Float | None |  | X | X |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | None |  | X | X |
| OUSPriority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer | None |  | X | X |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  | X | X |
| psseid | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String2 | None |  | X | X |
| qualificationStatus | Qualification status. | Boolean | False |  | X | X |
| RelayType | Type of relay. | EnumRelayType | None |  | X | X |
| resourceCategory | Type of resource. | String50 | None |  | X | X |
| RUC_Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  | X | X |
| RUC_Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  | X | X |
| wfrmcr | Wind /McCamey Flowgate Rights. | Boolean | FALSE |  | X | X |

Table 1

## Linkage

The required links for both ControllableLoadResources and LoadResources are defined in table below.

| Link Name | Description | Path Name | CLR | LR |
| --- | --- | --- | --- | --- |
| HostControlArea | Link to HostcontrolArea | Network/HostControlAreas/ERCOT | X | X |
| PowerSystemResource-Ownership | Ownership | Network/Companies/CPS ENERGY (RE | X | X |
| PowerSystemResource -Operatorship | Operatorship | Network/Companies/CPS ENERGY (QSE) | X | X |

# Modeling Owner Share Limits

### Modeling Approach

Owner Share Limits are used for GeneratingUnits, ControllableLoadResource or LoadResource. OwnerShareLimit (OSL) is mainly used for modeling Jointly Owned Units (Split Generation Units). A OwnerShareLimit is created for each Owner. If there are 3 owners for a unit then 3 OwnerShareLimits are created for that unit. Each OSL is associated to an Ownership record which points to each of the owners.

At least one Ownersharelimit instance should be associated with every LoadResource, ControllableLoadResource, ThermalGeneratingUnit, HydroGeneratingUnit, WindGeneratingUnit, and NuclearGeneratingUnit.

Figure 71 – OwnerShareLimits

### Attributes

The attributes for an OwnerShareLimit are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Description | Description of the object or instance | String |  |  |
| teid | Transmission Element ID | Integer | Auto-populated |  |
| highReasonabilityLimit | highReasonabilityLimit split based on the ownership percentage. | ActivePower | None |  |
| lowReasonabilityLimit | lowReasonabilityLimit split based on the ownership percentage. | ActivePower | None |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Latitude | Latitude coordinates. | Float | None |  |
| localName | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | Float | None |  |
| maxWeeklyEnergy | Maximum weekly energy (seasonal parameter) split based on the ownership percentage. | Float | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |
| ContingencyComponent |  |  |  |  |

### Linkage

The required links for a OwnerShareLimits are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| GeneratingUnit | Determines which Generating Unit this owner share limit represents. | Network/ERCOT Substations/Weather_Zone/Substation |
| EnergyConsumerResource | Determines which Controllable Load Resource or Load Resource this owner share limit represents | Network/ERCOT Substations/Weather_Zone/Substation/Voltage_Level/Customer_Load |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

# Modeling Ownership

## Modeling Approach

In the ERCOT CIM model an owner is assigned to each piece of equipment.  The owner of the equipment is given the right to edit the equipment, add instances under the equipment, and add other owners or operators for the equipment.  It is possible to have multiple owners for a single piece of equipment.  An owner must be created under a company as an instance of the Ownership class and used as a link to a piece of equipment. In cases where the Transmission Element or equipment owner is not-registered with ERCOT, a generic equipment owner will be made available in NMMS for assignment.   This generic owner can be assigned as the owner by the TSP.  The designation will be subject to ERCOT validation.

Figure 72 - Ownership

## Attributes

The attributes for Ownership are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Own Percent | Owner share percentage | Float | None |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Description | Description of the object or instance | String |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| Own Percent | Owner share percentage |  |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Penalty Factor | Unused | Float | None |  |
| Transmission Element ID | Transmission Element ID |  |  |  |

## Linkage

None

# Modeling Operatorship

## Modeling Approach

In the ERCOT CIM model an operator is assigned to each piece of equipment.  The operator of the equipment is given the right to edit the equipment and add instances under the equipment.  An operator must be created under a Company and used as a link to equipment.

Figure 73 - Operatorship

## Attributes

The attributes for Operatorship are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | Company Name_Operator |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Description | Description of the object or instance | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| Operate Percent | Operator share percentage | Float | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

## Linkage

None

# Modeling DC Ties

DCTie is defined as a non-synchronous transmission interconnection between ERCOT and non-ERCOT electric power systems. A DC Tie includes a DC Tie Load -- A Load used to represent the withdrawal of power from the ERCOT System to a DC Tie and a DC Tie Resource.-- A Resource used to represent the injection of power into the ERCOT System from a DC Tie.  A DC Tie Load Zone contains only the Electrical Bus in the ERCOT Transmission Grid that connects the DC Tie and is used in the settlement of the DC Tie Load in that zone.

## Modeling Approach

This section describes the approach for modeling a DCTie. A DCTie needs to be contained only in the instance of class sysorphan (ERCOT Texas Network) An example of a DCTie DC_E is visible in the hierarchy view in the figure below. The attribute DC Tie Zone name for DC tie will always match the name field

Figure 74 - DcTie

## Attributes

The attributes for a DCTie are shown in the table below.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |
| DC Tie Zone name for DC tie | DC Tie Zone name for DC tie. | String |  |
| Alias Name | Free text name of the object or instance. | String |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |

## Linkage

The required links for a DCTie are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| TieCorridorPartOfDCTie | A Tie Corridor should be a Part of the DC tie to identify the lines that are part of the DC tie. This is a required association |  |
| GeneratingUnitPartOfDCTie | A Generating unit should be a Part of the DC tie to identify the units that are part of the DC tie. This is a required association |  |

# Modeling Contingencies

Contingencies are modeled to study the “What-if” situations. They are defined on Lines, PowerTransformers and generating units which are likely to affect the system reliability incase of a forced outage. Network Security Analysis application is used to gauge its impact before they occur and alert the operators to any potential overloads or serious voltage violations.

The initial load of base contingencies will be responsibility of ERCOT. These contingencies make up a set of base contingencies. Changes to the list of base contingencies will be submitted by Market Participants using SAMRs. ERCOT will approve or reject the CAMRs and notify the Market Participant. The approved changes are added by ERCOT Staff to the Network Operations Model via NOMCRs. The Information Model Manager (Information Model Manager) provides basic validation of the equipment names/ID’s as the contingency is defined.

## Modeling Approach for contingency

In ERCOT CIM model, Contingency is defined as “An event threatening system reliability, consisting of one or more Contingency Elements”.

The location of contingencies in the Network model is shown in the figure below. A new Contingency can be added under the object called “Contingencies” by right mouse clicking on it and selecting ‘New’. Note that duplicate names are not allowed in the model while creating an instance. Complete the required attributes and links for the instance created. The attributes and links for Contingencies are described in the following sections.

Figure 75 - Hierarchy of Contingencies

### Attributes

The following table shows the attributes and their descriptions for Contingencies.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Device Name | Device Name. | String100 |  | Contingency name |
| Device Type | Device Type. | String100 |  | Station_A XFMR 138/69 |
| Action Type | Action Type. | String100 |  |  |
| Active Mode | Contingency active mode. | Enumeration |  | Default |
| Alias Name | Free text name of the object or instance. | String |  | _CB |
| Contingency Classifcation | The type of contingency, e.g.: double circuit, manuallydefined, etc. | Enumeration |  |  |
| Enable Cascading | TRUE if Cascading contigency analysis needs to performed, default is FALSE. | Boolean |  | FALSE |
| Enable Redefinition | True=enable False=disable dynamic redefinition. | Boolean | FALSE | FALSE |
| Enable SPS | True=enable False=disable SPS functions. | Boolean | FALSE | FALSE |
| End Date | Final Date this Contingency is in use. | Absolute Date Time | 1/1/2100 | 1/1/2100 |
| Generation Loss | The amount (in MW) of generation the contingency is expected to lose. | Float |  | 9999 |
| Generator Participation Factor | Short/Long. | Enumeration |  | normal |
| Load Loss | The amount (in MW) of load loss expected from the contingency | Float |  | 9999 |
| Local Name | The local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, Voltage Level, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  | Station_A 138/69 transformer XFMR1 |
| Max Shadow Price | States the Max Shadow price for a Contingency. | Double Float | 99999 | 99999 |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  | 1785236 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Probability Of Occurrence | A number between 0 and 1. Contingencies with a probability less than 0.5 are considered 'low probability' contingencies. | Float |  | 1 |
| Process Type | Contingency process type. | Enumeration |  | Use Wide |
| Refactor | Set to TRUE to force a partial refactorization method when updating the matrices for the contingency solution. The default is FALSE, in this case the software will automatically determine whether a factor update or partial refactorization is more efficient for the contingency being processed, and use the most efficient method. | Boolean |  | FALSE |
| Response Time | The time frame of response in seconds for the components associated with this contingency. | Long Integer |  | 1 |
| RunFlag | Run Flag. | Boolean | TRUE | TRUE |
| Start Date | Starting Date this Contingency is expected to be in use. | Date Time | 1/1/2001 | 1/1/2001 |

### Linkage

No Required links

## Modeling Approach for Contingency Element

The ERCOT CIM model defines a ContingencyElement as an element of a system event to be studied by contingency analysis, representing a change in status of a single piece of equipment.

ContingencyElement is modeled under the object type ‘Contingency’ as a child instance. Duplicate names are not allowed for ContingencyElements. The location of the ContingencyElements in the model tree is shown below.

Figure 76 - Hierarchy for Contingency Elements

### Attributes

The following table shows the attributes and their descriptions for ContingencyElement.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Alias Name | Free text name of the object or instance. | String |  |  |
| CB Fault | Indicates TRUE if this CB is included in post contingency and related to CB fault due to the dynamic redefinition logic. | Boolean |  | TRUE |
| Local Name | The local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, Voltage Level, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  | 1785236 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Status | The status of contingency element, i.e. Open/Close for Switch, Removed or not for other conducting equipment. Status = TRUE for an OPEN Switch or Removed conducting equipment. | Boolean | TRUE | TRUE |
| tempEquipmentAssoc | Used to deal with Siemens Association linking issue | String |  |  |

### Linkage

The following table shows the links for ContingencyElement.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| ContingencyElementHasAEquipment | The equipment to be studied | Network/ERCOT Texas Network |

## Modeling approach for Contingency Groups

ContingencyGroup is used for activation of groups of contingencies. Contingencies can belong to multiple groups.

The following figure shows the location of the ContingencyGroups in the network model tree. A new contingency group can be created under the object called “Contingency Groups” by right mouse clicking on it and selecting ‘New’.

Figure 77 - Hierarchy for ContingencyGroups

### Attributes

The following table shows the attributes and their descriptions for ContingencyGroups.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Alias Name | Free text name of the object or instance. | String |  |  |
| Description | Description of the object or instance | String |  |  |
| Local Name | The local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, Voltage Level, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Maintain Sub Systems | This field sets whether the subsystems for the contingencies in this CTGGroup are maintained even though the group is inactive. When Maintain Subsystems set ON, and Study is set OFF, CA maintains the contingency local subsystems for base case changes. If Maintain Subsystems is set OFF and Study is set OFF, the subsystems are deleted. | Boolean | TRUE | TRUE |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  | 1785236 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Study | T=activate the contigencies in the group. | Boolean | TRUE | TRUE |

### Linkage

No required links.

## Modeling approach for Contingency Group Members

ContingencyGroupMembers are used to create many-to-many relationship between Contingency and Contingency Group. These are the contingencies that are studied as a group.

The following figure shows the location of the ContingencyGroupMember in the network model tree. A new contingency group member can be created under the object called “Contingency Groups” by right mouse clicking on it and selecting ‘New’.

Figure 78 - Hierarchy for Contingency Group Member

### Attributes

The following table shows the attributes and their descriptions for Contingency Group Members.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Alias Name | Free text name of the object or instance. | String |  |  |
| Local Name | The local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, Voltage Level, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  | 1785236 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |

### Linkage

The following table shows the links for ContingencyGroups.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| ContingencyGroupMemberHasAContingency | Contingency which is a member of this group | Contingencies_and_RASs /Contingencies |

# Modeling Remedial Action Schemes (RAS)

## Modeling Approach

Remedial Action Schemes encompass Remedial Action Plans (RAP), Special Protection Schemes (SPS), Remedial Action Plans Conditional (RAPC), and Mitigation Plans.  All RASs are in response to a specific Contingency.

Special Protection Schemes are automatic, relay controlled actions taken to relieve an overload condition on one or more Transmission Elements.  RAPs are manual corrective actions agreed upon between ERCOT and Market Participants to be taken to relieve an overload condition on one or more Transmission Elements. RAPCs are different from RAPs in that the corrective actions only relieve the overload under a specific system condition.  For example, if Line A is out of service AND contingency X occurs, and then the RAPC is put into affect.  If Line A is in-service AND contingency X occurs, then the RAPC is not implemented.  Mitigation Plans are similar to RAPs, except that Mitigation Plans can involve shedding of load.

## Modeling Approach RAS

Changes to the base Remedial Action Schemes will be submitted by Market Participants through PTC using a SAMR. ERCOT will approve or reject the SAMRs and notify the Market Participant.  The SAMR types for RAS include RAP, SPS, RAPC, and Mitigation Plans.  The approved changes are added by ERCOT Staff to the Network Operations Model using the NOMCR process. The Information Model Manager (Information Model Manager) provides a basic level of validation.

Figure below shows the Information Model Manager hierarchy for an example RASs.  An RAS has a Stage, the state of a remedial action scheme, and a Trigger Condition, which is the set of gates that would logically trigger the RAS.

Figure 79 - RAS

Under the Stage is a StageTrigger, or condition that is triggered within a Stage.  Under the Stage Trigger is the PrivateProtectiveActions, which are specific to a RAS trigger condition.  Under the PrivateProtectiveActions, the individual PrivateActions are housed and can include any of the actions listed in the table below.

| Protective Action | Description |
| --- | --- |
| ProtActACLineSegment | Protective action to put an ACLineSegment in-service/out-of-service. |
| ProtActAnalog | Base class for protective actions that are non-switching. |
| ProtActEnergyConsumer | RAS protective action associated with a load instance. |
| ProtActSeriesCompensator | Protective action to put a series compensator in-service/out-of-service. |
| ProtActStationReduction | Protective action to reduce station generation. |
| ProtActSwitch | Protective action to move a switch. |
| ProtActSynchronousMachine | Protective action to change output of a synchronous machine. |
| ProtActTransformerWinding | Protective action to put a TransformerWinding in-service/out-of-service. |
| ProtectiveAction | Base class for a protective action for RAS. |
| ProtectiveActionShared | Protective actions that can be shared among triggers. |

The collection of RAS logical Gates are housed under the TriggerCondition.  Each Gate can have various Pin inputs listed in the table below.

| PinType | Description |
| --- | --- |
| GateInputPin | Input pin for a special protection scheme gate. |
| PinBranchGroup | Branch flow summation input pin for RAS. |
| PinFlow | Network solution flow input pin for RAS. |
| PinGate | Input pin that maps to a Gate for RAS. |
| PinSwitch | Input pin that maps to network solution switch status for RAS. |
| PinTriggerCondition | Input pin that maps to a TriggerCondition for RAS. |
| PinVoltage | Input pin that maps to a network voltage for RAS. |

### Attributes

Class Attributes and Linkage tables have been combined wherever possible and when the classes are close in proximity to each other within the Network Model hierarchy.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Active | User specified active | Boolean | False |  |
| Is RAP | This is a remedial action plan (RAP) | Boolean | False |  |
| Is RAS | This is a remedial action scheme (RAS) | Boolean | False |  |
| Latitude | Latitude coordinates |  |  |  |
| Alias Name | Free text name of the object or instance. | String | None | RAS_12 |
| Local Name | The Local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | RAS_ab |
| Longitude | Longitude coordinates |  |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Float | None | 123456 |
| PathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Transmission Element ID | Transmission Element ID | Integer |  |  |
| contingencyComponent |  | Boolean |  |  |
| Show Telemetry on Display | Set Flase if no telemetry is available for the RAS | Boolean |  |  |

### Linkage

No required links

## Modeling Approach for RAS-Stage, Stage Trigger, Private Protective Actions

A Remedial Action Schemes’ Stage, TriggerCondition, or set of Gates that would logically trigger the RAS, and PrivateProtectiveActions, which are specific to a Trigger Condition share the same attributes.  Their attributes table has been combined but their Linkage tables remain separate.

### Attributes

The table below lists the attributes for RAS-Stage, StageTrigger, and PrivateProtectiveActions.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| AliasName | Free text name of the object or instance. | String | None | STAGE_12 |
| LocalName | The Local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | STAGE_ab |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Float | None | 123456 |
| PathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| noticeType (for PrivateProtectiveActions) | (message/alarm) | Enumeration |  |  |

### Linkage for RAS-Stage

The following table shows the required links for a Stage.

### Linkage for RAS-Stage Trigger

The following table shows the required links for Stage Trigger.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| TriggeredBy | Trigger Condition | Contingencies_and_RASs/RemedialActionSchemes/RAS_1/TRIG |

### Linkage for RAS- Private Protective Actions

No required links

## Modeling Approach for RAS-Protective Action ACLine Segment, Series   Compensator, Switch, and Transformer Winding

Four types of PrivateProtectiveActions do not directly include SCADA measurements. These include those for ACLine Segments, Series Compensators, Switches, and Transformer Windings.  Both their Attributes and Linkage tables are combined.  For a description of these classes, see section “Modeling Approach for RAS” above.

### Attributes

The table below lists the attributes for ProtectiveAction ACLine Segment, Series   Compensator, Switch, and Transformer Winding.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| inService | Element put in service | Boolean | False |  |
| enableArming | Enable Turn On. | Boolean | False |  |
| AliasName | Free text name of the object or instance. | String | None | PPA_12 |
| LocalName | The Local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | PPA_ab |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Float | None | 123456 |
| PathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage

The following table shows the required links for Protective Action ACLine Segment, Series   Compensator, Switch, and Transformer Winding. The particular Protective Action references the Transmission Element used in the Protective Action.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| References (Transmission Device), where Transmission Device is either a Switch, ACLine Segment, ect… | References device that performs Protective Action. | Network/ERCOT Texas Network/ERCOT Substations/WZ_NORTH_CENTRAL/Sub/138/SWITCH_123 |

## Modeling Approach for RAS-Protective Action Analog, Energy Consumer, Station Reduction, and Synchronous Machine

Four types of Private Protective Actions could include SCADA measurements. These include those for Analogs, Energy Consumers, Station Reductions, and Synchronous Machines.  Both their Attributes and Linkage tables are combined.  For a description of these classes, see section “Modeling Approach RAS”.

### Attributes

The table below lists the attributes for Protective Action Analog, Energy Consumer, Station Reduction, and Synchronous Machine.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Action Value | If no SCADA value, then is the value to reduce by | Float | None |  |
| Action Value from SCADA | True, the action value is obtained from SCADA otherwise from actionValue attribute | Boolean | False |  |
| Is Reduced To | If true, action is a 'reduce to' otherwise it is a 'reduce by'. | Boolean | False |  |
| inService | Element put in service | Boolean | False |  |
| enableArming | Enable Turn On | Boolean | False |  |
| AliasName | Free text name of the object or instance. | String | None | PPA_12 |
| LocalName | The Local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | PPA_ab |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Float | None | 123456 |
| PathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage

The following table shows the required links for Protective Action AnalogValue,EnergyConsumer, Substation, or SynchronousMachine.  The particular Protective Action references the Transmission Element used in the Protective Action.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| References (Element), where Element is either AnalogValue,EnergyConsumer, Substation, or SynchronousMachine | References element that performs Protective Action. | Network/ERCOT Texas Network/ERCOT Substations/WZ_NORTH_CENTRAL/Sub |

## Modeling Approach for RAS-Protective Action and Protective Action Shared

The ProtectiveAction class is the base class for the Remedial Action Scheme.  ProtectiveActionShared can be shared among triggers.  These classes’ Attributes tables are combined.

### Attributes

The table below lists the attributes for ProtectiveAction.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| enableArming | Enable Turn On. | Boolean | False |  |
| AliasName | Free text name of the object or instance. | String | None | PPA_12 |
| LocalName | The Local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | PPA_ab |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Float | None | 123456 |
| PathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage for RAS- Protective Action

The following table shows the required links for ProtectiveAction.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| Armed By(DiscreteValue) | Discrete Value |  |

### Linkage for RAS- Protective Action Shared

The following table shows the required links for ProtectiveActionShared.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| Armed By(DiscreteValue) | Discrete Value |  |
| Has (SharedProtectiveActions) | Protective actions that are shared among RemedialActionScheme trigger conditions such as a high flow |  |

## Modeling Approach for RAS- Trigger Condition

A TriggerCondition is the set of gates that would logically trigger the RAS.  The Gate class is mentioned in a later section.

### Attributes

The table below lists the attributes for a TriggerCondition.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Local Name | The Local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | PPA_ab |
| Alias Name | Free text name of the object or instance | String |  |  |
| Description | Description of the object or instance | String |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Float | None | 123456 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Not Used | Trigger Condition Text to Display – Select how text should be extracted to display on Onelines | Boolean |  |  |

### Linkage

The following table shows the required links for a TriggerCondition.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| Has Resulting (Gate) | Gate | Contingencies_and_RASs/RemedialActionSchemes/RAS/TRG/GT |

## Modeling Approach for RAS- Gate

The Gate class is a SpecialProtectionScheme gate which evaluates to Boolean.  The types of inputs available to the Gate class are mentioned in the section that follows.

### Attributes

The table below lists the attributes for a Gate.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Alias Name | Free text name of the object or instance | String |  |  |
| Threshold Value | Threshold value for gate type of (GE,GT,LE,LT,NE,EQ) with single gate input | Float |  |  |
| Change Threshold | Use change limit for voltages. | Boolean | False |  |
| Count to Coduct | Number of High inout signals for a high export signal to be conducted | Integer |  |  |
| Emergency Threshold | Use the branch emergency limit as threshold. | Boolean | False |  |
| Gate Type | Gate Type. | Enum GateType |  |  |
| Level | Level of the gate. | Integer | 0 |  |
| Limit Percentage | Percentage of the limit. 90% should enter 90. | Float |  |  |
| Loadshed Threshold | Use the branch loadshed limit as threshold. | Boolean | False |  |
| Lower Threshold | Use lower limit (for FlowSummation and voltage). | Boolean | False |  |
| Normal Threshold | Use the branch normal limit as threshold. | Boolean | False |  |
| Upper Threshold | Use upper limit (for FlowSummation and voltage). | Boolean | False |  |
| Use Limit Threshold | Use the branch limit as threshold value, otherwise use Gate::thresholdValue. | Boolean | False |  |
| LocalName | The Local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | PPA_ab |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Float | None | 123456 |
| PathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage

No required links.

## Modeling Approach for RAS- Gate Input Pin, Pin Branch Group, Pin Branch Group, Pin Gate, Pin Switch, Pin Trigger Condition, and Pin Voltage

Each Gate can have various Pin inputs including GateInputPin, PinBranchGroup, PinGate, PinSwitch, PinTriggerCondition, and PinVoltage.  Their Attributes tables are combined, but their Linkage tables are listed separately.  PinFlow is discussed in the following section.  For a description of these classes, see section for “Modeling Approach RAS”.

### Attributes

The table below lists the attributes for GateInputPin, PinBranchGroup, PinBranchGroup, PinGate, PinSwitch, PinTriggerCondition, and PinVoltage.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Alias Name | Free text name of the object or instance | String |  |  |
| Flow MVA | If true the input is a MVA. | Boolean | False |  |
| Flow MVAR | If true the input is a MVAR. | Boolean | False |  |
| Flow MW | If true, the input is a MW. | Boolean | False |  |
| Negate | If true, input is negated first and then input to the gate. Only applicable to logical gates. | Boolean | False |  |
| Use Absolute Value | Use absolute value of input (only applies to analog inputs). | Boolean | False |  |
| LocalName | The Local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | PPA_ab |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Float | None | 123456 |
| PathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage for RAS- Gate Input Pin

The following table shows the required links for GateInputPin.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| HasAConductingEquipment | Conducting Equipment | Network/ERCOT_Texas_Network/ERCOT Substations/WZ_SOUTHERN/B_DAVIS/138/5200 |

### Linkage for RAS- Pin Branch Group

The following table shows the required links for PinBranchGroup.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| BelongsTo(BranchGroup) | Branch Group | Network/BranchGroup/N_TO_W |

### Linkage for RAS- Pin Gate

The following table shows the required links for PinGate.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| Has A (Gate) | Gate | Contingencies_and_RASs/RemedialActionSchemes/_a/TC1/Gate |

### Linkage for RAS- Pin Switch

The following table shows the required links for PinSwitch.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| Has A (Switch) | Switch | Network/ERCOT Texas Network/ERCOT Substations/WZ_COAST/SUB/138/DCS1 |

### Linkage for RAS- Pin Trigger Condition

The following table shows the required links for PinTriggerCondition.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| Has A (Trigger Condition) | Trigger Condition | Contingencies_and_RASs/RemedialActionSchemes/RAS/TrigCon |

### Linkage for RAS- Pin Voltage

The following table shows the required links for PinVoltage.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| Has A (ConnectivityNode) | Connectivity Node | Network/ERCOT Texas Network/ERCOT Substations/WZ_COAST/SUB/138/CN |

## Modeling Approach for RAS-Pin Flow

Each Gate can have various Pin inputs including PinFlow.  The other Pin classes, GateInputPin, PinBranchGroup, PinBranchGroup, PinGate, PinSwitch, PinTriggerCondition, and PinVoltage, are discussed in the section above.  For a description of these classes, see section for “Modeling Approach RAS”.

### Attributes

The table below lists the attributes for PinFlow.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Alias Name | Free text name of the object or instance | String |  |  |
| Description | Description of the object or instance | String |  |  |
| Either End | True if doing status input on a branch and want to check if either end is out. | Boolean | False |  |
| Flow MVA | If true the input is a MVA. | Boolean | False |  |
| Flow MVAR | If true the input is a MVAR. | Boolean | False |  |
| Flow MW | If true, the input is a MW. | Boolean | False |  |
| Input Is Flow | If true, the input is a flow, otherwise it is branch status. | Boolean | False |  |
| Into Bus | Flow into the bus is positive. | Boolean | False |  |
| Negate | If true, input is negated first and then input to the gate. Only applicable to logical gates. | Boolean | False |  |
| Out Of Bus | Flow out of the bus is positive. | Boolean | False |  |
| Use Absolute Value | Use absolute value of input (only applies to analog inputs). | Boolean | False |  |
| LocalName | The Local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | PPA_ab |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Float | None | 123456 |
| PathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage

The following table shows the required links for PinFlow.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| Has A (Terminal) | Terminal | Network/ERCOT Texas Network/ERCOT Substations/WZ_COAST/SUB/138/Device/Terminal |

# Modeling PrivateAreaNetworks

## Modeling Approach

In the ERCOT CIM model instance of type PrivateAreaNetwork are utilized for identifying individual GeneratingUnits that are Retired, Mothballed or Non-MarketParticipating (Non-Modeled Generation), pseudo Generation/Loads that are modeled to represent BlockLoadTransfers, loads that are part of a Self Serving Entity and to identify Load and/or GeneratingUnits that form a Private Use network. This modeling distinction is defined by the enumerated attribute networkType (labeled as “Type of Private Use Network” in Information Model Manager). ERCOT may require the owner or operator of a Private Use Network to provide information to ERCOT and the TSP on Transmission Facilities located within the Private Use Network for use in the Network Operations Model if the information is required to adequately model and determine the security of the ERCOT Transmission Grid, including data to perform loop flow analysis of Private Use Networks.

ERCOT shall review submittals of modeling data from owners or operators of Private Use Networks assure that it will result in correct analysis of ERCOT Transmission Grid security.

Figure below shows a PrivateAreaNetwork in the Information Model Manager hierarchical view.

Figure 80 - Information Model Manager hierarchical view of a PrivateAreaNetwork as modeled in the ERCOT model.

## Attributes

The attributes for PrivateAreaNetwork are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Type of Private Use Network | Describes the Type of Private Use Network | Enumeration | None | Retired Generation |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | 123 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ |
| Alias Name | Free text name of the object or instance. | String | None | XYZ |

## Linkage

No required links.

# Modeling Branch Group

## Modeling Approach

BranchGroup is defined as Directed Sum of terminal Flows. These groups are defined by operations for monitoring secure MW flows between different transfer areas.

This section describes the approach for modeling a BranchGroup. A BranchGroup needs to be contained only in the instance of class sysorphan (BranchGroup)

An example of a BranchGroup is visible in the hierarchy view in the figure.

Figure 81 - BranchGroup

## Attributes

The attributes for a BranchGroup are shown in the table below.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |
| Description | Description of the object or instance | String |  |
| Monitor Active Power | Monitor active power. ( True or False) | Boolean | True |
| Monitor Reactive Power | Monitor Reactive power. ( True or False) | Boolean | False |
| Alias Name | Free text name of the object or instance. | String |  |
| Eligible | Eligible Flag | Boolean | False |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |
| Max Shadow Price | States the Max Shadow price for a BranchGroup. | Double Float | 99999 |
| Maximum Active Power | Maximum Active Power | Double Float | 0 |
| Maximum MVAR | Maximum MVAR | Double Float |  |
| Maximum MW | Maximum MW | Double Float | 0 |
| Maximum Reactive Power | Maximum Reactive Power | Double Float | 0 |
| Minimum Active Power | Minimum Active Power | Double Float | 0 |
| Minimum MVAR | Minimum MVAR | Double Float |  |
| Minimum MW | Minimum MW | Double Float | 0 |
| Minimum Reactive Power | Minimum Reactive Power | Double Float | 0 |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |
| teid | Transmission Element ID | Integer |  |

## Linkage

The required links for a BranchGroup are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| MonitoredMemberOfMonitoredGroup | Branch Group Member of MonitoredGroup | List_Information/Monitored Groups/ISO |
| BranchGroupReferencesTerminal | BranchGroupReferencesTerminal |  |
| BranchGroupReferencesInverseTerminal | BranchGroupReferencesInverseTerminal |  |

# Modeling Branch Group Terminal

## Modeling Approach

BranchGroupTerminal is defined as Directed terminal flow to add into BranchGroup. This is one of the instances that is modeled by ERCOT.A BranchGroupTerminal needs to be contained only in the instance of class BranchGroup.

An example of a BranchGroupTerminal  AIRLIN_B_DAVI1 is visible in the hierarchy view in the below figure.

Figure 82 - BranchGroupTerminal

## Attributes

The attributes for a BranchGroupTerminal are shown in the table below.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |
| Description | Description of the object or instance | String |  |
| Alias Name | Free text name of the object or instance. | String |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |
| Positive Flow In | Positive Flow In | Boolean |  |

## Linkage

The required links for a BranchGroupTerminal are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| BranchGroupTerminalReferencesTerminal | BranchGroupTerminalReferencesTerminal | Network/ERCOT Texas Network/ERCOT-AC Lines/138/2967/1/2967_B |

# Modeling Endcap

## Modeling Approach

EndCap is defined as a cap to terminate the line or device

An example of an ENDCAP_TER1 is visible in the hierarchy view in the figure.

Figure 83 - EndCap

## Attributes

The attributes for an EndCap are shown in the table below.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |
| Description | Description of the object or instance | String |  |
| Alias Name | Free text name of the object or instance. | String |  |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean |  |
| DAM secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured | Boolean |  |
| Latitude | Latitude coordinates | Float |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |
| Longitude | Longitude coordinates | Float |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Long Int |  |
| PSS/E ID | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly name units, loads, branches, and transformers. | String |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |
| Phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | String |  |
| RUC Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured | Boolean |  |
| Remove | The equipment is removed from the network | Boolean |  |
| Remove Enable | The equipment can be removed from the network in the EMS | Boolean |  |
| teid | Transmission Element ID | Integer |  |

## Linkage

The Required links for an EndCap are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| BaseVoltage | A link to a BaseVoltage is only necessary when there is no VoltageLevel container used. If a VoltageLevel container is used the disconnector will inherit a BaseVoltage from the VoltageLevel. | Network/Base Voltage |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

# Modeling Tiecorridor

## Modeling Approach

TieCorridor is defined under a SubLoadArea and is linked to a TieLine

An example of a TieCorridor 10_A is visible in the hierarchy view in the figure.

Figure 84 - TieCorridor

## Attributes

The attributes for a TieCorridor are shown in the table below.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |
| Description | Description of the object or instance | String |  |
| Alias Name | Free text name of the object or instance. | String |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |
| Maximum MW Inflow Alarm Limit | Maximum MW Inflow Alarm Limit | Float |  |
| Maximum MW Outflow Alarm Limit | Maximum MW Outflow Alarm Limit | Float |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |
| Tie ID | Tie ID | Integer |  |
| Tie is Internal | Tie is Internal ? | Boolean |  |
| teid | Transmission Element ID | Integer |  |

## Linkage

The Required links for a TieCorridor are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| TieCorridorConnectsFromHostControlArea | To side of the Tie Corridor | Network/HostControlArea/ERCOT |
| TieCorridorConnectsToSubLoadArea | SubLoad Area the Tie corridor connects to | Schedules/Load Area Schedules/ERCOT/WXZNRTHC |
| TieCorridorConnectsToaHostControlArea | From Side of the Tie Corridor | Network/HostControlArea/ERCOT |

# Modeling PermissionArea

## Modeling Approach

PermissionArea is modeled under sysOrphan “Permission Areas” as a child instance. PermissionArea is used to define valid areas of responsibility for SCADA measurements. The Permission Areas currently defined and used in the ERCOT CIM model are AL, COMMS, EAST, ECAR, ERCOT, GEN, NORT, SOUT, and SYSTEM.

Figure below shows the parent/child hierarchy of a PermissionArea in Information Model Manager.

Figure 85 - Hierarchy for PermissionArea

## Attributes

The attributes for a PermissionArea are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. |  |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

## Linkage

None.

# Modeling Approach for DayType

## Modeling Approach

Group of similar days, e.g., Mon/Tue/Wed, Thu/Fri, Sat/Sun, Holiday1, Holiday2.

Figure 86 - DayType

## Attributes

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |
| Alias Name | Free text name of the object or instance. | String |  |
| Description | Description of the object or instance. | String |  |
| End Time | Time daytype ends | Time |  |
| Fri Flag | Indicates whether Friday is included in this Day Type. | Boolean |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |
| Mon Flag | Indicates whether Monday is included in this Day Type. | Boolean |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |
| Sat Flag | Indicates whether Saturday is included in this Day Type. | Boolean |  |
| Start Time | Time daytype starts |  |  |
| Sun Flag | Indicates whether Sunday is included in this Day Type. | Boolean |  |
| Thurs Flag | Indicates whether Thursday is included in this Day Type. | Boolean |  |
| Tues Flag | Indicates whether Tuesday is included in this Day Type. | Boolean |  |
| Wed Flag | Indicates whether Wednesday is included in this Day Type. | Boolean |  |

## Linkage

There are no required links.

# Modeling Approach for LoadType

## Modeling Approach

Container for shared attributes for loads of the same type.

Figure 87 - LoadType

## Attributes

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |
| Alias Name | Free text name of the object or instance. |  |  |
| Description | Description of the object or instance. |  |  |
| exp P Frequency | Load watts are proportional to (V**WVEXP)*(F**WFEXP). |  |  |
| exp P Voltage | Exp P Voltage. |  |  |
| exp Q Frequency | Load vars are proportional to (V**RVEXP)*(F**RFEXP). |  |  |
| exp Q Voltage | Exp Q Voltage. |  |  |
| Initial Time | The initial time on the cooling characteristic in seconds. |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. |  |  |
| Maximum Scaling | The maximum value that the load could be scaled by upon its reconection. |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |

## Linkage

There are no required links.

# Modeling Approach for SubLoadArea

The class is the second level in a hierarchical structure for grouping of loads for the purpose of load flow load scaling.

Figure 88 - SubLoadArea

## Attributes

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |
| Alias Name | Free text name of the object or instance. |  |  |
| Description | Description of the object or instance. |  |  |
| Forecast Enabled | Forecast enabled. |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |

## Linkage

There are no required links.

# Modeling Approach for Season

## Modeling Approach

A specified time period of the year, e.g., spring, summer, fall, winter.  Season Types may be defined with starting and ending month and day.  All defined season types must make up one year.

Figure 89 - Season

## Attributes

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |
| Alias Name | Free text name of the object or instance. | String |  |
| Description | Description of the object or instance. | String |  |
| End Date | Date season ends. | Time |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |
| Season Name | Name of the Season. | String | Winter |
| Start Date | Date season starts. | Time |  |

## Linkage

There are no required links.

# Modeling PseudoTerminal

## Modeling Approach

The pseudo terminal is defined to provide UI support and will be modeled by ERCOT. The psuedoterminal does not connect to into the network topology and is solely utilized for the purpose of readily displaying SCADA/ICCP telemetry being provided for the equipment.

PsuedoTerminal shoud not be Associated to a connectivityNode.

Psuedoterminal should not be associated to a RegulatingconductingEquipment.

Figure 90 - PseudoTerminal

## Attributes

The attributes for a PseudoTerminal are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Description | Description of the object or instance. | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None |  |
| Near | Flag indicating whether the terminal is a near terminal of a branch. | Boolean | False |  |
| PSS/E Bus Name | Store the PSS/E bus name that will be associated with the grouping of Connectivity Nodes. | String | None |  |
| PSS/E Bus Number | Attribute will be used to store the PSS/E bus number that will be associated with the grouping of Connectivity Nodes. | String | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

## Linkage

There are no required links for a PseudoTerminal.

# Modeling Planning Objects

## Modeling Approach for Planning Area

The ERCOT CIM model defines a planning area as planning areas.

Planning areas are commonly used to designate sections of the network which represent control areas between which there are scheduled flows.  Planning areas will be pre-populated and maintained by ERCOT in the Information Model Manager. This data may change with future planning area additions.

The each planning area name and PSS/E ID must be unique within the Information Model Manager.  These values cannot be duplicated. See figure below as an example.

Figure 91 - PlanningArea

### Attributes

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| PSS/E ID | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage

There are no required links for Planning Area.

## Modeling Approach for Planning Zones

The ERCOT CIM model defines planning zones as planning zones.

Planners designate buses to specific zones allowing for additional subdivision of the network to facilitate analyses and documentation.

The Planning zones will be pre-populated and maintained by ERCOT in the Information Model Manager. This data may change with future planning zones additions.

Each planning zone name and PSS/E ID must be unique within the Information Model Manager.  These values cannot be duplicated. See figure below as an example.

Figure 92 - PlanningZone

### Attributes

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| PSS/E ID | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage

There are no required links for PlanningZones.

## Modeling Approach for SubcontrolArea

The ERCOT CIM model defines a SubcontrolArea as an area defined for the purpose of tracking interchange with surrounding areas via tie points; may or may not serve as a control area. Right now, the Load area schedules are the same field as subcontrol area. The subcontrol area is a future area for data.

The subcontrol areas will be pre-populated and maintained by ERCOT in the Information Model Manager. This data may change with future subcontrol areas additions.

The each Subcontrol area name and PSS/E ID must be unique within the Information Model Manager.  These values cannot be duplicated. See figure below as an example.

Figure 93 - SubcontrolArea

### Attributes

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| PSS/E ID | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage

There are no required links to SubcontrolArea.

# Modeling VoltageMonitored

## Modeling Approach

Voltage throughout the ERCOT model is monitored under the VoltageMonitored class. This class is utilized by State Estimation and Contingency Analysis to achieve a more accurate solution by setting the Voltage Limits per the Operating Guide requirements. VoltageMonitored class is required on every VoltageLevel in a Substation.

VoltageMonitored is modeled under a VoltageLevel at a Substation as a child instance. When defining a VoltageMonitored class under a VoltageLevel, the “MonitoredGroup” and “Uses (VoltageLimitSet)” should be properly linked according to their Path Name(see Linkage VoltageMonitored below).

Figure below shows the parent/child hierarchy of a VoltageMonitored in IMM.

Figure 94 - Hierarchy for VoltageMonitored

## Attributes

The attributes for an VoltageMonitored are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Name | Free text name of the object or instance. | String | None |  |
| Eligible | Eligible. | Boolean | TRUE |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

## Linkage

The required links for a VoltageMonitored are defined in table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| MonitoredGroup | Group of Elements based on certain monitoring category. MonitoredGroups are defaulted to ISO | List_Information/Monitored Groups |
| Uses (VoltageLimitSet) | Contains the Voltage Limits defined per Voltage Limit Set | Contingencies_and_RASs/Voltage Limit Sets |

# Modeling VoltageLimitset

## Modeling Approach

VoltageLimitSet is referenced by VoltageMonitored class under a VoltageLevel at a Substation. This is where the tolerances and the exchange/deviation are defined according to the requirements of the desired Voltage Monitoring Application.

VoltageLimitSet is modeled under Voltage Limit Sets as a child instance.

Figure below shows the parent/child hierarchy of a VoltageLimitSet in IMM.

Figure 95 - Hierarchy for VoltageLimitset

## Attributes

The attributes for an VoltageLimitset are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Is Percentage Limits | Tells if the limit values are in percentage of normalValue or the specified Unit for Measurements and Controls. | Boolean | FALSE |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Type | Type | Enumeration | None |  |
| Zonal Attribute | Temporary attribute to support dual SCADA feeds. | Boolean | FALSE |  |
| for Network |  | Boolean | TRUE |  |

## Linkage

There are no required links for VoltageLimitSet.

# Modeling VoltageLimit

## Modeling Approach

VoltageLimit is modeled under VoltageLimitSet as a child instance. This is where the Emergency Exchange, Emergency High, Emergency Low, Normal Exchange, Normal High and Normal Low are defined.

Figure below shows the parent/child hierarchy of a VoltageLimit in IMM.

Figure 96 - Hierarchy for VoltageLimit

## Attributes

The attributes for an VoltageLimit are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Value | The value to supervise against. | Float | None |  |

## Linkage

There are no required links for VoltageLimit

# MODELING STATIC VAR COMPENSATOR (SVC)

## Modeling Approach for static var compensator (svc)

The ERCOT CIM model defines SVC as a facility for providing variable and controllable shunt reactive power. The SVC typically consists of a power transformer, filter, thyristor-controlled reactor, and thyristor-switched capacitor arms, and controls at a SVC site.  SVC may operate in fixed MVar output mode or in voltage control mode. When in voltage control mode, the output of the SVC will be proportional to the deviation of voltage at the controlled bus from the voltage set-point. The SVC characteristic slope defines the proportion. If voltage at controlled bus is equal to voltage set-point, SVC MVar output is zero.  The function of SVC is to provide dynamic voltage support on high-voltage electricity transmission networks.  It is a single equipment providing or absorbing VAR to the network to keep network voltage constantly at a set reference value.  Positive values is pertaining to capacitive ratings while negative values inductive ratings.

In the ERCOT CIM model a StaticVarCompensator is modeled under a VoltageLevel.   Every StaticVarCompensator will have a RegulationSchedule defined as a link under the StaticVarCompensator. Modeling of RegulationSchedule is a function of ERCOT based on historic performances of the SVC.  When a SVC is new to the system, a generic RegulationSchedule can be used.  A single Terminal must be modeled under a StaticVarCompensator. One or many SCADA measurement/s may be modeled under the terminal.  Figure below shows a StaticVarCompensator in Information Model Manager Model hierarchy.

Figure 97 – Static Var Compensator

## 59.2 Attributes

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | string |  |  |
| Automatic Voltage Regulation Enabled | T = Automatic voltage regulation enabled. | Bool | FALSE |  |
| Capacitive Rating - SVC | Maximum available capacitive reactive power. | Double float |  |  |
| Contingency Element | Contingency Element | Bool | FALSE |  |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Bool | FALSE |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Bool | TRUE |  |
| Fixed MVAR - SVC | Fixed MVAr | float |  |  |
| High Voltage Change Threshold | The upper bound of the voltage threshold. | float |  |  |
| Inductive Rating | Maximum available inductive reactive power. | Double float |  |  |
| Latitude | Latitude coordinates. | float |  |  |
| Load based Regulation Enabled | T = Load based voltage regulation enabled. | Bool | FALSE |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | string |  |  |
| Longitude | Longitude coordinates. |  |  |  |
| Low Voltage Change Threshold | The lower bound of the voltage threshold. | float |  |  |
| Max Time Steady State | The maximum duration allowed to exceed Q range in steady_state. | float |  |  |
| Maximum kV - SVC | SVC Voltage Regulation. The maximum voltage regulation for TapChangers. Note that this is a fixed parameter | float | 999 |  |
| minimum kV - SVC | SVC Voltage Regulation. The minimum voltage regulation for TapChangers. Note that this is a fixed parameter which is not a function of time (i.e., not a regulation schedule). | float | 0 |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | string |  |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Long Int |  |  |
| PSS/E ID | Attribute will give IMM modelers control over the PSS/E ID that the Topology Processor uses to properly name units, loads, branches, and transformers. | string |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Percent Reactive Power Transfer | Percent reactive power transfer. | float |  |  |
| Phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | string |  |  |
| Post Contingency MVAR Maximum | Post_contingency maximum MVAR limit. | float |  |  |
| Post Contingency MVAR Minimum | Post_contingency minimum MVAR limit. | float |  |  |
| RUC Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Bool | FALSE |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Bool | TRUE |  |
| Ramp Delay | The desired time delay before ramp (Seconds). Entered by the database model builder. | float |  |  |
| Ramp Duration Threshold | The threshold ramp duration. | float |  |  |
| Remove | The equipment is removed from the network. | Bool | TRUE |  |
| Remove Enable | The equipment can be removed from the network. | Bool | TRUE |  |
| SVC Control Mode | SVC control mode | Enumeration |  |  |
| SVC Export Mode | Used to designate the device model to be used when processing a StaticVarCompensator for planning models. | Enumeration | Generator |  |
| SVC Percentage Slope | The characteristics slope of an SVC defines how the reactive power output changes in proportion to the difference between the regulated bus voltage and the voltage setpoint. | Double float |  |  |
| SVC Setpoint Voltage | The reactive power output of the SVC is proportional to the difference between the voltage at the regulated bus and the voltage setpoint. When the regulated bus voltage is equal to the voltage setpoint, the reactive power output is zero. | float |  |  |
| Steady State MVAR Maximum | Steady state maximum MVAR limit. | float |  |  |
| Steady State MVAR Minimum | Steady state minimum MVAR limit. | float |  |  |
| Transmission Element ID | Transmission Element ID. | Long Int |  |  |
| Voltage Deviation | SVC DEVIATION (+/-) FROM TARGET. | float |  |  |
| b - SVC | SVC Shunt Admittance. The StaticVarCompensator class has been extended to include a "charging" attribute. The units are assumed to be in MVAR, as required by the CPSM Profile. | Double float | 0.0001 |  |
| contingencyComponent | Contingency Component | Bool | TRUE |  |

## 59.3 Linkage

| Attributes | Description | Description |
| --- | --- | --- |
| Power System Resource-Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies/… … |
| Power System Resource-Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies/… … |
| Regulating CondEq-Regulation Schedule | A type of conducting equipment that may have a voltage regulation schedule. | Schedules/RegulationSchedules/… … |
| Regulating CondEq-Terminal | Terminal of SVC. | Network/ERCOT_Texas_Network/ERCOT Substations/… … |
| Static Var Compensator Triggers TEID Auto Number |  | .General/.DoNotModify/TEIDautonum |

The required links for a Static Var Compensator are defined in Table below.

# Appendix A - Validation Rules – Required Fields

This appendix lists all of the validation rules for attributes that must be defined for a specific class. It also lists any validation for attributes that must be within a specific value range.

| ClassName | Attributes | Required | Range |
| --- | --- | --- | --- |
| AccumulatorLimit | value | x | >=0 |
| AccumulatorValue | cstatus | x |  |
| ACLineSegment | r | x | >= -500 and <= 500 |
| ACLineSegment | x | x | >= -1000 and <= 1000 |
| Address | City | x |  |
| Address | PostalCode | x |  |
| Address | State | x |  |
| Address | Street1 | x |  |
| AggregateHub | hubCalculationMethod | x |  |
| AlternateLimit | highLimit | x |  |
| AlternateLimit | lowLimit | x |  |
| AnalogLimit | LimitType | x |  |
| AreaReserveSpec | lowerRegMarginReqt | x | >= 0 |
| AreaReserveSpec | opReserveReqt | x | >= 0 |
| AreaReserveSpec | primaryReserveReqt | x | >= 0 |
| AreaReserveSpec | raiseRegMarginReqt | x | >= 0 |
| AreaReserveSpec | spinningReserveReqt | x | >= 0 |
| BasePower | basePower | x |  |
| BaseVoltage | nominalVoltage | x | >=0 and <= 1100 |
| BranchGroup | maximumActivePower | x |  |
| BranchGroup | maximumReactivePower | x |  |
| BranchGroup | minimumReactivePower | x |  |
| BranchGroup | monitorActivePower | x |  |
| BranchGroupTerminal | positiveFlowIn | x |  |
| Breaker | InTransitTime | x |  |
| CombinedCyclePlant | LogicalResourceNodeName | x |  |
| CombinedCyclePlant | aliasName | x |  |
| Company | companyType | x |  |
| Company | DUNS | x |  |
| Company | PrimaryPhone | x |  |
| Company | aliasName | x |  |
| Configuration | highReasonabilityLimit | x | >= lowReasonabilityLimit |
| Configuration | highReasonabilityRamp RateLimit | x | >= lowReasonabilityRampRateLimit |
| Configuration | hotintTime | x |  |
| Configuration | hotStartTime | x | <= intStartTime |
| Configuration | intColdTime | x |  |
| Configuration | intStartTime | x | <= coldStartTime |
| Configuration | lowReasonabilityLimit | x | >= 0 |
| Configuration | lowReasonabilityRampRateLimit | x |  |
| Configuration | maxDailyStarts | x |  |
| Configuration | maxONTime | x |  |
| Configuration | maxWeeklyEnergy | x |  |
| Configuration | maxWeeklyStarts | x | >= maxDailyStarts |
| Configuration | minOFFTime | x |  |
| Configuration | minONTime | x | <= maxONTime |
| Configuration | primaryConfiguration | x |  |
| Configuration | qualificationStatus | x |  |
| Configuration | seasonalMaxEmergencyRating | x | >= seasonalMinEmergencyRating |
| Configuration | seasonalMaxSustainableRating | x | >= seasonalMinSustainableRating |
| Configuration | seasonalMinEmergencyRating | x |  |
| Configuration | seasonalMinSustainableRating | x |  |
| ConformLoadSchedule | endTime | x |  |
| ConformLoadSchedule | startTime | x |  |
| ConformLoadSchedule | value1Unit | x |  |
| ConformLoadSchedule | value2Unit | x |  |
| ConnectivityNode | VoltageLevel | x |  |
| ConnectivityNodeGroup | PSS/EBuseName | x |  |
| ConnectivityNodeGroup | PSS/EBusNumber | x | can not be between 9400-9999 and 94000-99999 |
| Contact | EmailAddress | x |  |
| Contact | FirstName | x |  |
| Contact | LastName | x |  |
| Contact | PrimaryPhone | x |  |
| Contact | City | x |  |
| Contact | PostalCode | x |  |
| Contact | State | x |  |
| Contact | Street1 | x |  |
| Contingency | DeviceName | x |  |
| Contingency | DeviceType | x |  |
| ControllableLoadResource | maxDeploymentTime | x |  |
| ControllableLoadResource | maxWeeklyEnergy | x |  |
| ControllableLoadResource | minNoticeTime | x |  |
| ControllableLoadResource | rampRateSlopeDownLimit | x |  |
| ControllableLoadResource | rampRateSlopeUpLimit | x |  |
| ControllableLoadResource | maxDailyDeployment | x |  |
| ControllableLoadResource | maxInterruptionTime | x | >= minInterruptionTime |
| ControllableLoadResource | maxWeeklyDeployment | x | >= maxDailyDeployment |
| ControllableLoadResource | minInterruptionTime | x |  |
| ControllableLoadResource | minRestorationTime | x |  |
| ControllableLoadResource | aliasName | x |  |
| CurveData | xvalue | x |  |
| CurveData | y1value | x |  |
| CurveData | y2value | x |  |
| CustomerLoad | PowerFactor | x | >=0 and <=1 |
| CustomerLoad | pfixedPct | x |  |
| CustomerLoad | pnomPct | x |  |
| CustomerLoad | qfixed | x |  |
| CustomerLoad | qnomPct | x |  |
| DayType | FriFlag | x |  |
| DayType | MonFlag | x |  |
| DayType | SatFlag | x |  |
| DayType | SunFlag | x |  |
| DayType | ThursFlag | x |  |
| DayType | TuesFlag | x |  |
| DayType | WedFlag | x |  |
| DCTie | DCTieLZName | x |  |
| Disconnector | initiallyOpen | x |  |
| Disconnector | normalOpen | x |  |
| EnergyConsumer AltConnection | percentTransfer | x |  |
| EPSMeter | AcceptedStatus | x |  |
| EPSMeter | RID | x |  |
| FlowgateElement | biddable | x |  |
| FlowgateElement | endDate | x |  |
| FlowgateElement | monitored | x |  |
| FlowgateElement | rating | x |  |
| FlowgateElement | startDate | x |  |
| FlowgateGroup | infB | x |  |
| FlowgateGroup | infC | x |  |
| Gate | thresholdValue | x |  |
| GenericUnderfrequency Relay | relayDelayTime | x |  |
| HostControlArea | areaControlMode | x |  |
| HostControlArea | forGeneration | x |  |
| HostControlArea | forNetwork | x |  |
| HydroGeneratingUnit | coldStartTime | x |  |
| HydroGeneratingUnit | controlPulseHigh | x |  |
| HydroGeneratingUnit | controlPulseLow | x |  |
| HydroGeneratingUnit | controlResponseRate | x |  |
| HydroGeneratingUnit | efficiency | x | >= 0.001 and <= 1.2 |
| HydroGeneratingUnit | freqBias | x |  |
| HydroGeneratingUnit | freqDevDeadband | x |  |
| HydroGeneratingUnit | governorMPL | x |  |
| HydroGeneratingUnit | governorSCD | x |  |
| HydroGeneratingUnit | highReasonabilityLimit | x | >= lowReasonabilityLimit |
| HydroGeneratingUnit | highReasonabilityRampRateLimit | x | >= lowReasonabilityRampRateLimit |
| HydroGeneratingUnit | hotintTime | x |  |
| HydroGeneratingUnit | hotStartTime | x | <= intStartTime |
| HydroGeneratingUnit | intColdTime | x |  |
| HydroGeneratingUnit | intStartTime | x | <= coldStartTime |
| HydroGeneratingUnit | lowReasonabilityLimit | x | >= 0 |
| HydroGeneratingUnit | lowReasonabilityRampRateLimit | x |  |
| HydroGeneratingUnit | maxDailyStarts | x |  |
| HydroGeneratingUnit | maximumOperatingMW | x | equal to highReasonabilityLimit |
| HydroGeneratingUnit | maxONTime | x |  |
| HydroGeneratingUnit | maxWeeklyEnergy | x |  |
| HydroGeneratingUnit | maxWeeklyStarts | x | >= maxDailyStarts |
| HydroGeneratingUnit | minimumOperatingMW | x | >=0 and <= 999 and equal to lowReasonabilityLimit |
| HydroGeneratingUnit | minOFFTime | x |  |
| HydroGeneratingUnit | minONTime | x | <= maxONTime |
| HydroGeneratingUnit | modelDetail | x |  |
| HydroGeneratingUnit | penaltyFactor | x |  |
| HydroGeneratingUnit | seasonalMaxSustainableRating | x | >= seasonalMinSustainableRating |
| HydroGeneratingUnit | seasonalMinEmergencyRating | x |  |
| HydroGeneratingUnit | seasonalMinSustainableRating | x |  |
| HydroGeneratingUnit | stepChange | x |  |
| InductionMotorLoad | conformingLoadFlag | x |  |
| InductionMotorLoad | pfixedPct | x |  |
| InductionMotorLoad | pnomPct | x |  |
| InductionMotorLoad | qfixed | x |  |
| InductionMotorLoad | qnomPct | x |  |
| IrregularIntervalSchedule | startTime | x |  |
| IrregularIntervalSchedule | value1Unit | x |  |
| IrregularIntervalSchedule | value2Unit | x |  |
| IrregularTimePoint | time | x |  |
| IrregularTimePoint | value1 | x |  |
| IrregularTimePoint | value2 | x |  |
| LevelVsVolumeCurve | curveStyle | x |  |
| LevelVsVolumeCurve | xUnit | x |  |
| LevelVsVolumeCurve | y1Unit | x |  |
| LevelVsVolumeCurve | y2Unit | x |  |
| Load | conformingLoadFlag | x |  |
| Load | pfixedPct | x |  |
| Load | pnomPct | x |  |
| Load | qfixedPct | x |  |
| Load | qnomPct | x |  |
| LoadBasedRegulation Curve | curveStyle | x |  |
| LoadBasedRegulation Curve | xUnit | x |  |
| LoadBasedRegulation Curve | y1Unit | x |  |
| LoadBasedRegulation Curve | y2Unit | x |  |
| LoadBasedRegulation Curve | aliasName | x |  |
| LoadDemandModel | startTime | x |  |
| LoadDemandModel | value1Unit | x |  |
| LoadDemandModel | value2Unit | x |  |
| LoadResource | maxWeeklyEnergy | x |  |
| LoadResource | minNoticeTime | x |  |
| LoadResource | maxDailyDeployment | x |  |
| LoadResource | maxInterruptionTime | x | >= minInterruptionTime |
| LoadResource | maxWeeklyDeployment | x | >= maxDailyDeployment |
| LoadResource | minInterruptionTime | x |  |
| LoadResource | aliasName | x |  |
| MeasurementArgument | referenceName | x | Required if ReferenceFlag = True |
| MeasurementValue | cstatus | x |  |
| MeasurementValueSource | biverAus | x |  |
| MeasurementValueSource | biverTay | x |  |
| MeasurementValueSource | BufferTime | x |  |
| MeasurementValueSource | defaultDataSetPeriod | x |  |
| MeasurementValueSource | GraceTime | x |  |
| MeasurementValueSource | iccpDomainAus | x |  |
| MeasurementValueSource | iccpDomainTay | x |  |
| MeasurementValueSource | IntegrityPeriod | x |  |
| MeasurementValueSource | lnkapp | x |  |
| MeasurementValueSource | MaxDisPerDataset | x |  |
| MeasurementValueSource | maxScanRate | x |  |
| MeasurementValueSource | protocolVersion | x |  |
| MeasurementValueSource | remoteIdAus | x |  |
| MeasurementValueSource | remoteIdTay | x |  |
| MeasurementValueSource | savecaseType | x |  |
| MeasurementValueSource | trsfr | x |  |
| ModelVersion | date | x |  |
| ModelVersion | information | x |  |
| ModelVersion | version | x |  |
| MVArCapabilityCurve | curveStyle | x |  |
| MVArCapabilityCurve | xUnit | x |  |
| MVArCapabilityCurve | y1Unit | x |  |
| MVArCapabilityCurve | y2Unit | x |  |
| MVArCapabilityCurve | aliasName | x |  |
| NonConformLoad | conformingLoadFlag | x |  |
| NonConformLoad | pfixedPct | x |  |
| NonConformLoad | pnomPct | x |  |
| NonConformLoad | qfixedPct | x |  |
| NonConformLoad | qnomPct | x |  |
| NuclearGeneratingUnit | coldStartTime | x |  |
| NuclearGeneratingUnit | controlPulseHigh | x |  |
| NuclearGeneratingUnit | controlPulseLow | x |  |
| NuclearGeneratingUnit | controlResponseRate | x |  |
| NuclearGeneratingUnit | efficiency | x | >= 0.001 and <= 1.2 |
| NuclearGeneratingUnit | freqBias | x |  |
| NuclearGeneratingUnit | freqDevDeadband | x |  |
| NuclearGeneratingUnit | governorMPL | x |  |
| NuclearGeneratingUnit | governorSCD | x |  |
| NuclearGeneratingUnit | highReasonabilityLimit | x | >= lowReasonabilityLimit |
| NuclearGeneratingUnit | highReasonabilityRampRateLimit | x | >= lowReasonabilityRampRateLimit |
| NuclearGeneratingUnit | hotintTime | x |  |
| NuclearGeneratingUnit | hotStartTime | x | <= intStartTime |
| NuclearGeneratingUnit | intColdTime | x |  |
| NuclearGeneratingUnit | intStartTime | x | <= coldStartTime |
| NuclearGeneratingUnit | lowReasonabilityLimit | x | >= 0 |
| NuclearGeneratingUnit | lowReasonabilityRampRateLimit | x |  |
| NuclearGeneratingUnit | maxDailyStarts | x |  |
| NuclearGeneratingUnit | maximumOperatingMW | x | equal to highReasonabilityLimit |
| NuclearGeneratingUnit | maxONTime | x |  |
| NuclearGeneratingUnit | maxWeeklyEnergy | x |  |
| NuclearGeneratingUnit | maxWeeklyStarts | x | >= maxDailyStarts |
| NuclearGeneratingUnit | minimumOperatingMW | x | equal to lowReasonabilityLimit |
| NuclearGeneratingUnit | minOFFTime | x |  |
| NuclearGeneratingUnit | minONTime | x | <= maxONTime |
| NuclearGeneratingUnit | modelDetail | x |  |
| NuclearGeneratingUnit | penaltyFactor | x |  |
| NuclearGeneratingUnit | seasonalMaxSustainableRating | x | >= seasonalMinSustainableRating |
| NuclearGeneratingUnit | seasonalMinEmergencyRating | x |  |
| NuclearGeneratingUnit | seasonalMinSustainableRating | x |  |
| NuclearGeneratingUnit | stepChange | x |  |
| OwnerShareLimits | highReasonabilityLimit | x | >= lowReasonabilityLimit |
| OwnerShareLimits | lowReasonabilityLimit | x |  |
| OwnerShareLimits | maxWeeklyEnergy | x |  |
| OwnerShareLimits | aliasName | x |  |
| Ownership | ownPercent | x | >= 0 and <= 100 |
| PenstockLossCurve | curveStyle | x |  |
| PenstockLossCurve | xUnit | x |  |
| PenstockLossCurve | y1Unit | x |  |
| PenstockLossCurve | y2Unit | x |  |
| PhaseShifterImpedance Curve | curveStyle | x |  |
| PhaseShifterImpedance Curve | xUnit | x |  |
| PhaseShifterImpedance Curve | y1Unit | x |  |
| PhaseShifterImpedance Curve | y2Unit | x |  |
| PhaseShifterImpedance Curve | aliasName | x |  |
| PowerTransformer | bmagSat | x |  |
| PowerTransformer | PSS/E ID | x |  |
| PowerTransformer | transformerType | x |  |
| PowerTransformer | voltageSensitivity | x |  |
| ProtectedSwitch | initiallyOpen | x |  |
| RampRateCurve | Emergency | x |  |
| RampRateCurve | curveStyle | x |  |
| RampRateCurve | xUnit | x |  |
| RampRateCurve | y1Unit | x |  |
| RampRateCurve | y2Unit | x |  |
| RampRateCurve | aliasName | x |  |
| Rating | ratingType | x |  |
| Rating | TempPoint | x |  |
| Rating | forNetwork | x |  |
| recloseMaxAngle | recloseMaxAngle | x | >=0 and <=90 |
| RegulationSchedule | startTime | x |  |
| RegulationSchedule | value1Unit | x |  |
| RegulationSchedule | value2Unit | x |  |
| RemedialActionScheme | active | x |  |
| RemedialActionScheme | isRAP | x |  |
| RemedialActionScheme | isRAS | x |  |
| ResourceController | externalJointUnit | x |  |
| ResourceController | frequencyBias | x |  |
| ResourceController | gross | x |  |
| ResourceController | jointUnit | x |  |
| ResourceController | physical | x |  |
| SeasonDayTypeSchedule | startTime | x |  |
| SeasonDayTypeSchedule | value1Unit | x |  |
| SeasonDayTypeSchedule | value2Unit | x |  |
| SeriesCompensator | r | x |  |
| SeriesCompensator | x | x |  |
| ShuntCompensator | aVRDelay | x |  |
| ShuntCompensator | maximumkV | x |  |
| ShuntCompensator | minimumkV | x |  |
| ShuntCompensator | nominalkV | x |  |
| ShuntCompensator | nominalMVAr | x |  |
| ShuntCompensator | switchingPriority | x |  |
| ShuntCompensator | voltSensitivity | x |  |
| ShuntCompensator | avrEnabled | x |  |
| StaticVarCompensator | b | x |  |
| StaticVarCompensator | capacitiveRating | x | > 0 |
| StaticVarCompensator | fixedMVAr | x | < 0 |
| StaticVarCompensator | highVoltageChangeThreshold | x |  |
| StaticVarCompensator | inductiveRating | x | < 0 |
| StaticVarCompensator | lowVoltageChangeThreshold | x |  |
| StaticVarCompensator | maximumkV | x |  |
| StaticVarCompensator | minimumkV | x | Removed with MGRR__0020 |
| StaticVarCompensator | steadyStateMVARMax | x | postContingencyMVARMax >steadyStateMVARMax > steadyStateMVARMin > postContingencyMVARMin |
| StaticVarCompensator | steadyStateMVARMin | x | postContingencyMVARMax >steadyStateMVARMax > steadyStateMVARMin > postContingencyMVARMin |
| StationSupply | pfixedPct | x |  |
| StationSupply | pnomPct | x |  |
| StationSupply | PowerFactor | x |  |
| StationSupply | qfixed | x |  |
| StationSupply | qnomPct | x |  |
| StationSupplyWRCurve | aliasName | x |  |
| SubControlArea | ControlAreaNumber | x |  |
| SubGeographicalRegion | isWeatherZone | x |  |
| SubGeographicalRegion | aliasName | x | if isWeatherZone=true |
| Substation | forNetwork | x |  |
| Substation | forScada | x |  |
| SynchronousMachine | baseMVAr | x |  |
| SynchronousMachine | inertia | x |  |
| SynchronousMachine | maximumKV | x | >=0 and <= 1100 |
| SynchronousMachine | maximumMVAr | x |  |
| SynchronousMachine | minimumKV | x | >=0 and <= 1100 |
| SynchronousMachine | minimumMVAr | x |  |
| SynchronousMachine | r | x |  |
| SynchronousMachine | ratedMVA | x | >= maximumMVAr |
| SynchronousMachine | x | x | >=0 and <= 500 |
| SynchronousMachine | xSubtrans | x |  |
| SynchronousMachine | xTrans | x |  |
| TapChanger | avrEnabled | x |  |
| TapChanger | awrEnabled | x |  |
| TapChanger | highStep | x | >=0 and <= 99 |
| TapChanger | initialDelay | x |  |
| TapChanger | lowStep | x | >=0 and <= 99 |
| TapChanger | LTCControlMode | x |  |
| TapChanger | maximumkV | x |  |
| TapChanger | minimumkV | x | Removed with MGRR__0020 |
| TapChanger | neutralAngle | x |  |
| TapChanger | neutralKV | x | >=0 and <= 1100 |
| TapChanger | neutralStep | x | >=0 and <= 99 |
| TapChanger | normalStep | x | >=-99 and <= 99 , >= lowStep and <= highStep |
| TapChanger | stepVoltageIncrement | x | >=0 and <= 100 |
| TapChanger | subsequentDelay | x |  |
| ThermalGeneratingUnit | coldStartTime | x |  |
| ThermalGeneratingUnit | controlPulseHigh | x |  |
| ThermalGeneratingUnit | controlPulseLow | x |  |
| ThermalGeneratingUnit | controlResponseRate | x |  |
| ThermalGeneratingUnit | efficiency | x | >= 0.001 and <= 1.2 |
| ThermalGeneratingUnit | freqBias | x |  |
| ThermalGeneratingUnit | freqDevDeadband | x |  |
| ThermalGeneratingUnit | governorMPL | x |  |
| ThermalGeneratingUnit | governorSCD | x |  |
| ThermalGeneratingUnit | highReasonabilityLimit | x | >= lowReasonabilityLimit |
| ThermalGeneratingUnit | highReasonabilityRampRateLimit | x | >= lowReasonabilityRampRateLimit |
| ThermalGeneratingUnit | hotintTime | x |  |
| ThermalGeneratingUnit | hotStartTime | x | <= intStartTime |
| ThermalGeneratingUnit | intColdTime | x |  |
| ThermalGeneratingUnit | intStartTime | x | <= coldStartTime |
| ThermalGeneratingUnit | lowReasonabilityLimit | x | >= 0 |
| ThermalGeneratingUnit | lowReasonabilityRampRateLimit | x |  |
| ThermalGeneratingUnit | maxDailyStarts | x |  |
| ThermalGeneratingUnit | maximumOperatingMW | x | equal to highReasonabilityLimit |
| ThermalGeneratingUnit | maxONTime | x |  |
| ThermalGeneratingUnit | maxWeeklyEnergy | x |  |
| ThermalGeneratingUnit | maxWeeklyStarts | x | >= maxDailyStarts |
| ThermalGeneratingUnit | minimumOperatingMW | x | >=0 and <= 999 and equal to lowReasonabilityLimit |
| ThermalGeneratingUnit | minOFFTime | x |  |
| ThermalGeneratingUnit | minONTime | x | <= maxONTime |
| ThermalGeneratingUnit | modelDetail | x |  |
| ThermalGeneratingUnit | penaltyFactor | x |  |
| ThermalGeneratingUnit | seasonalMaxSustainableRating | x | >= seasonalMinSustainableRating |
| ThermalGeneratingUnit | seasonalMinEmergencyRating | x |  |
| ThermalGeneratingUnit | seasonalMinSustainableRating | x |  |
| ThermalGeneratingUnit | stepChange | x |  |
| TransformerWinding | connectionType | x |  |
| TransformerWinding | emergencyMVA | x | <= shortTermMVA |
| TransformerWinding | grounded | x |  |
| TransformerWinding | r | x | >=-50 and <= 500 |
| TransformerWinding | ratedMVA | x |  |
| TransformerWinding | shortTermMVA | x |  |
| TransformerWinding | x | x | >= -1000 and <= 1000 |
| TransformerKludge | PSS/E ID | x |  |
| TransformerKludge | PSS/E Name | x |  |
| WindGeneratingUnit | coldStartTime | x |  |
| WindGeneratingUnit | controlPulseHigh | x |  |
| WindGeneratingUnit | controlPulseLow | x |  |
| WindGeneratingUnit | controlResponseRate | x |  |
| WindGeneratingUnit | efficiency | x | >= 0.001 and <= 1.2 |
| WindGeneratingUnit | freqBias | x |  |
| WindGeneratingUnit | freqDevDeadband | x |  |
| WindGeneratingUnit | governorMPL | x |  |
| WindGeneratingUnit | governorSCD | x |  |
| WindGeneratingUnit | highReasonabilityLimit | x | >= lowReasonabilityLimit |
| WindGeneratingUnit | highReasonabilityRampRateLimit | x | >= lowReasonabilityRampRateLimit |
| WindGeneratingUnit | hotintTime | x |  |
| WindGeneratingUnit | hotStartTime | x | <= intStartTime |
| WindGeneratingUnit | intColdTime | x |  |
| WindGeneratingUnit | intStartTime | x | <= coldStartTime |
| WindGeneratingUnit | lowReasonabilityLimit | x | >= 0 |
| WindGeneratingUnit | lowReasonabilityRampRateLimit | x |  |
| WindGeneratingUnit | maxDailyStarts | x |  |
| WindGeneratingUnit | maximumOperatingMW | x | equal to highReasonabilityLimit |
| WindGeneratingUnit | maxONTime | x |  |
| WindGeneratingUnit | maxWeeklyEnergy | x |  |
| WindGeneratingUnit | maxWeeklyStarts | x | >= maxDailyStarts |
| WindGeneratingUnit | minimumOperatingMW | x | >=0 and <= 999 and equal to lowReasonabilityLimit |
| WindGeneratingUnit | minOFFTime | x |  |
| WindGeneratingUnit | minONTime | x | <= maxONTime |
| WindGeneratingUnit | modelDetail | x |  |
| WindGeneratingUnit | penaltyFactor | x |  |
| WindGeneratingUnit | seasonalMaxSustainableRating | x | >= seasonalMinSustainableRating |
| WindGeneratingUnit | seasonalMinEmergencyRating | x |  |
| WindGeneratingUnit | seasonalMinSustainableRating | x |  |
| WindGeneratingUnit | stepChange | x |  |

# Appendix B - Validation Rules – Required associations

This appendix lists all of the validation rules for associations that must be defined for a specific class.

| ClassA | ClassB |
| --- | --- |
| Accumulator | MeasurementType |
| Accumulator | Operatorship |
| Accumulator | Ownership |
| Accumulator | Terminal |
| Accumulator | Unit |
| AccumulatorLimitSet | Accumulator |
| AccumulatorValue | MeasurementGroup |
| AccumulatorValue | MeasurementValueSource |
| AccumulatorValue | PermissionArea |
| AccumulatorValue | RemoteSource |
| ACLineSegment | BaseVoltage |
| ACLineSegment | Operatorship |
| ACLineSegment | Ownership |
| AggregateHub | SettlementHUB |
| AlternateLimit | AlternateLimitSet |
| Analog | Operatorship |
| Analog | Ownership |
| Analog | PowerSystemResource |
| Analog | Unit |
| AnalogLimit | AnalogLimitSet |
| AnalogLimitSet | Analog |
| AngleDifference | MonitoredGroup |
| Bay | Operatorship |
| Bay | Ownership |
| BranchGroup | MonitoredGroup |
| Breaker | Operatorship |
| Breaker | Ownership |
| BusbarSection | BaseVoltage |
| BusbarSection | Operatorship |
| BusbarSection | Ownership |
| BWRSteamSupply | Operatorship |
| BWRSteamSupply | Ownership |
| CAESPlant | Operatorship |
| CAESPlant | Ownership |
| CogenerationPlant | Operatorship |
| CogenerationPlant | Ownership |
| CombinedCyclePlant | Operatorship |
| CombinedCyclePlant | Ownership |
| CombustionTurbine | Operatorship |
| CombustionTurbine | Ownership |
| ConformLoad | ConformLoadGroup |
| ConnectivityNode | EquipmentContainer |
| ConnectivityNodeGroup | Operatorship |
| ConnectivityNodeGroup | Ownership |
| ConnectivityNodeGroup | PlanningArea |
| ConstantArugment | FunctionArgument |
| ConstantArgurment | ConstantValue |
| ControllableLoadResource | Operatorship |
| ControllableLoadResource | Ownership |
| ControllableLoadResource | Operatorship |
| ControllableLoadResource | Ownership |
| CurrentRelay | Operatorship |
| CurrentRelay | Ownership |
| CurveData | Curve |
| CustomerLoad | ConformLoadGroup |
| CustomerLoad | Operatorship |
| CustomerLoad | Ownership |
| Disconnector | Operatorship |
| Disconnector | Ownership |
| Discrete | MeasurementType |
| Discrete | Operatorship |
| Discrete | Ownership |
| Discrete | PowerSystemResource |
| Discrete | Unit |
| EndCap | EquipmentContainer |
| EndCap | Operatorship |
| EndCap | Ownership |
| EPSMeter | PricingVector |
| FlowgateGroup | MonitoredGroup |
| HydroGeneratingUnit | Operatorship |
| HydroGeneratingUnit | Ownership |
| InductionMotorLoad | Operatorship |
| InductionMotorLoad | Ownership |
| Load | ConformLoadGroup |
| Load | EquipmentContainer |
| Load | Operatorship |
| Load | Ownership |
| LoadResource | EnergyConsumer |
| LoadResource | Operatorship |
| Measurement | Unit |
| Measurement | PowerSystemResource |
| MeasurementArgument | FunctionArgument |
| MeasurementArgument | MeasurementValue |
| MeasurmentLocation | DeviceType |
| MeasurementLocation | PermissionArea |
| MeasurementValueQuality | MeasurementValue |
| Monitored | MonitoredGroup |
| MonitoredRating | MonitoredGroup |
| MVArCapabilityCurve | SynchronousMachine |
| NuclearGeneratingUnit | Operatorship |
| NuclearGeneratingUnit | Ownership |
| OwnerShareLimits | Operatorship |
| OwnerShareLimits | Ownership |
| PowerTransformer | Operatorship |
| PowerTransformer | Ownership |
| ResourceController | Operatorship |
| ResourceController | Ownership |
| SeriesCompensator | Operatorship |
| SeriesCompensator | Ownership |
| SettlementLoadZone | Substation |
| ShuntCompensator | Operatorship |
| ShuntCompensator | Ownership |
| StaticVarCompensator | Operatorship |
| StaticVarCompensator | Ownership |
| StationSupply | Operatorship |
| StationSupply | Ownership |
| StringMeasurement | Unit |
| StringMeasurementValue | PermissionArea |
| SubGeographicalRegion | GeographicalRegion |
| Substation | SubGeographicalRegion |
| Substation | Operatorship |
| Substation | Ownership |
| SynchronousMachine | Operatorship |
| SynchronousMachine | Ownership |
| TapChanger | Operatorship |
| TapChanger | Ownership |
| ThermalGeneratingUnit | CombinedCyclePlant |
| ThermalGeneratingUnit | Operatorship |
| ThermalGeneratingUnit | Ownership |
| TransformerKluge | PowerTransformer |
| TransformerWinding | Operatorship |
| TransformerWinding | Ownership |
| TransmissionPath | ServicePoint |
| TransmissionPath | ServicePoint |
| VLSBusBarMonitored | MonitoredGroup |
| VoltageLevel | Substation |
| VoltageLevel | Operatorship |
| VoltageLevel | Ownership |
| VoltageMonitored | MonitoredGroup |
| WindGeneratingUnit | Operatorship |
| WindGeneratingUnit | Ownership |

# Appendix C - Validation Rules – COMPLEX rules

This appendix lists all of the validation rules that are more complex than required fields and range checks. These include validation rules that are conditional based upon certain conditions, involve associations with other attributes, and those that describe specific data relationships. The validation rule is explained descriptively and not in a formal language.

| Rule No. | Validation Rule |
| --- | --- |
| R1 | The abstract classes GeneratingUnit, Switch, EnergyConsumer,EnergyCosumerResource should not be used. Only the classes representing the actual classes should be used. For ex: Only instances of ThermalGeneratingUnit, NuclearGeneratingUnit, HydroGeneratingUnit or WindGeneratingUnit should be created instead of the generic GeneratingUnit Class |
| R2 | Each PowerTransformer and its associated TransformerWindings and TapChangers must be contained within one substation. |
| R3 | A PowerTransformer must be contained by a Substation. A TransformerWinding must be contained by a PowerTransformer. A TapChanger must be contained by a TransformerWinding( Check for associations between transformer, winding and tap. |
| R4 | A Measurement must be associated with a PowerSystemResource to convey containment information for the Measurement. |
| R5 | Transmission line measurements should be associated with an ACLineSegment or SeriesCompensator not with a Line. Transmission line measurements must be associated with a terminal. |
| R6 | Transformer measurements should be associated with a PowerTransformer. Transformer Windings should not have measurements. |
| R7 | A Measurement can be associated with at most one Terminal. |
| R8 | Combined Cycle configuration names should be unique for each Combined Cycle Plant. |
| R9 | ConnectivityNodes may only be placed within ConnectivityNodeGroup. |
| R10 | SynchronousMachine's minimumMVAr and maximumMVAr attributes and the minimum/maximum MVAr value specified in the associated MVArCapabilityCurve data should match. |
| R11 | Terminals connected to the same piece of Equipment can not be connected to the same connectivitynode |
| R12 | Voltage Levels can't be empty. There should always be classes associated to voltage levels. |
| R13 | The normal and neutral tap of the transformer must be within low and high steps |
| R14 | If there are 2 identical transformers in parallel with one marked Master and the other as Follower , the tap changer of the follower should always point towards the master tapchanger and not to itself. |
| R15 | Connectivity nodes must be associated to atleast 2 terminals. |
| R16 | Terminal associated to a any given equipment should have unique names. |
| R17 | ACLinesegment cannot go between different voltage levels. |
| R18 | Seriescompensator cannot go between different voltage levels and should be contained within one substation |
| R19 | The regulated terminal of a shuntcompensator must be in the same substation as the shuntcompensator's terminal (RegulatingCondEq->Terminal) |
| R20 | A shuntcompensator's SwitchedBy switch's terminal must be connected to shuntcompensator's terminal through a connectivitynode. |
| R21 | Transformer and Line ratings should follow these rules. NormalRating<=twohourrating<=15minrating |
| R22 | Sum of Ownership.ownershippercent should total 100% for SplitGenerationUnits(SGR). An SGR will have 1 record in one of the GeneratingUnit classes and "n" number of OwnerShareLimits that are associated to that GeneratingUnit. Each OwnerShareLimit will point to a OwnerShip record. The sum of all these ownership.ownershippercent should be equal to 100. |
| R23 | DCTie Psuedo Load breaker default value must be "Closed". |
| R24 | BLT (BlockLoadTransfer) must only group loads and only zero or one psuedo GeneratingUnit per BLT. The breaker for this psuedo gen if modeleld must have a default value of OPEN. |
| R25 | HubBus must have atleast one electrical bus. |
| R26 | The ConnectivityNodes in a ConnectivityNodeGroup must be in the SAME STATION i.e. ConnectivityNodes in a given ConnectivityNodeGroup cannot span multiple Stations. |
| R27 | If a HubBus is associated to more than 1 ConnectivityNodeGroup then ALL the associated ConnectivityNodeGroups must belong to the same station. |
| R28 | SynchronousMachine's 'ratedMVA' attribute should be greater than or equal to the 'baseMW' attribute of the GeneratingUnit it is associated to. |
| R29 | Check the baseVoltage (if not null) of each conducting equipment connected to a connectivityNode to be the same. |
| R30 | Only AnalogLimit instances that are children of an AnalogLimitSet instance with the LimitSet.forNetwork = False/Null should have the LimitAlarmCategory and AnalogLimitName associations populated. OR If the parent AnalogLimitSet instance’s the LimitSet.forNetwork = True of if the AnalogLimit instance’s parent is a Rating instance, the two associations do not need to be populated. |
| R31 | The energy consumer that is part of the DCTie must have ONE and ONLY one controllable load resource mapped to it. This energyconsumer can NOT be associated to a "non-controllable load resource". It has to be associated only to "controllable load resource". |
| R32 | Only AnalogLimit instances that are children of an AnalogLimitSet instance with the LimitSet.forNetwork = False/Null should have the lower and upper thresholds |
| R33 | Substation names should not exceed 8 chars. |
| R34 | The target voltage setting specified by the regulation schedules must be within 80% to 120% of the rated kV |
| R35 | The number of CurveData associated with the MVArCapabilityCurves and RampRateCurve should not exceed 10 |
| R36 | Two RampRateCurves (one with Emergency = True) should be associated with a ControllableLoadResource, a Configuration and a ThermalGeneratingUnit / HydroGeneratingUnit / NuclearGeneratingUnit / WindGeneratingUnit which has no association to a DCTie and a PrivateAreaNetwork (NetworkType: Non Modeled Generation, Mothballed, Retired) or a CombinedCyclePlant. |
| R37 | The FromConfig and ToConfig of a TransState shouldn't be same |
| R38 | FromConfig and ToConfig of a TransState must belong to the same CombinedCyclePlant |
| R39 | A Contingency can’t contain duplicate ContingencyElements |
| R40 | The controllable load resource must be associated with exactly two RampRateCurves, one for normal condition and the other for emergency condition |
| R41 | There is no duplicated CC configuration, i.e. there should not be 2 CC configurations that contain the same CCU combination with exactly same status of Primary/Alternate flag |
| R42 | Each CC plant must have at least one CC configuration to startup/shutdown |
| R45 | Each CustomerLoad instance should be associated with One instance of SettlementNOIELoadZone, Or One instance of DCTie, Or Its parent Substation should be associated with one instance of SettlementLoadZone |
| R46 | For any instance of MeasurementArgument with ReferenceFlag = True, the Calculation link on the associated MeasurementValue instance should not be same as the parent Calculation instance of the MeasurementArgument instance. |
| R48 | Every ElectricalBus should be in a LoadZone or a NOIE load zone |
| R49 | PsuedoTerminal shoud not be Associated to a connectivityNode |
| R50 | Psuedoterminal should not be associated to a RegulatingconductingEquipment |
| R51 | EnergyConsumerResource(LoadResource and ControllableLoadResource) should not have any association to ResourceNode |
| R52 | If PAN.networktype = retired or mothbolled, then there should be only one genunit associated to it. |
| R53 | x/r ratio for ACLineSegment should follow these rules. For 345kv x/r > 7, 138kv x/r> 1.5, 69kv x/r > 1 |
| R54 | A resourceNode that is associated to a PrivateUseNetwork(PUN), should not be associated to any Physical Generating Unit |
| R55 | Every GeneratingUnit (Thermal, Hydro, Nuclear, Wind) should have an association to a ResourceNode unless the GeneratingUnit is associated to a DCTIE, a Non-Modeledgeneration, a BlockLoadType or a retired unit. |
| R56 | If a Load is assigned to a NOIE load zone, then its electrical bus can ONLY have loads that are assigned to the same NOIE load zone, i.e. cannot have other loads at the same electrical bus assigned to different load zone In other words, all loads that connect to the same EB must belong to the same load zone. All those loads must either be associated to the same NOIE load zone, or none of them has this association. |
| R57 | DCTIE ElectricalBus can only connect to DCTIE load. The ElectricalBus connecting to terminal of DCTIE pseudo load (DCTIE attribute of CUSTOMERLOAD instance) cannot have other loads connect to it |
| R58 | Each CombinedCyclePlant Configuration instance should have at least one association to a ConfigurationMember instance |
| R59 | PricingVector's should have a unique name |
| R60 | MeasurementGroup and Calculation instances associated to a Zonal MeasurementLocation should have unique names. Similarly MeasurementGroup and Calculation instances associated to a Nodal MeasurementLocation should have unique names |
| R61 | Measurementargument and ConstantArgument instances associated to a Calculation should have unique names |
| R64 | At least one Ownersharelimit instance should be associated with every LoadResource, ControllableLoadResource, ThermalGeneratingUnit, HydroGeneratingUnit, WindGeneratingUnit, NuclearGeneratingUnit, |
| R65 | Every zonal AnalogLimitSet should be associated with a zonal Analog - Every Nodal AnalogLimitSet should be associated with Nodal Analog. |
| R66 | Every Zonal AnalogValue with NO association to a AnalogName should be associated with a zonal MeasurementValueQuality and MeasurementValueSource. Every Nodal AnalogValue with no association to a AnalogName should be associated with a Nonal MeasurementValueQuality and MeasurementValueSource |
| R67 | Every zonal AnalogValue with association to a AnalogName should be associated to atleast one zonal MeasurementGroup or one zonal Calculation - Every Nodal AnalogValue with association to a AnalogName should be associated should be associated to atleast one Nodal MeasurementGroup or one Nodal Calculation |
| R68 | Every zonal DiscreteValue with association to a DiscreteName should be associated to atleast one zonal MeasurementGroup or one zonal Calculation - Every Nodal discreteValue with association to a discreteName should be associated to atleast one Nodal MeasurementGroup or one Nodal Calculation |
| R69 | Every zonal Analog should be associated with a zonal AnalogValue - Every Nodal Analog should be associated with a Nodal AnalogValue |
| R70 | Every zonal analoglimit associated with analoglimitname should be associated with a zonal analoglimitset. Every nodal analoglimit associated with analoglimitname should be associated with a nodal analoglimitset |
| R71 | Every zonal MeasurementArgument and ConstantArgument should be associated with a zonal Calculation - Every Nodal MeasurementArgument and ConstantArgument should be associated with a Nodal Calculation |
| R73 | Every configuration should either be able to StartUp or Shutdown or transition into another configuration, else it is invalid. |
| R74 | Attributes, HightReasonabilityLimit, LowReasonabilityLimit and MaxWeeklyenergy should be populated for any ownersharelimits associated with a LoadResource, a ControllableLoadResource, and a ThermalGeneratingUnit / HydroGeneratingUnit / NuclearGeneratingUnit / WindGeneratingUnit which has no association to a DCTie and a PrivateAreaNetwork (NetworkType: Non Modeled Generation Retired, Mothballed, BlockLoadTransfer). |
| R75 | Attributes (Operational Resource Parameters), MinOnlineTime, minOfflineTime, hotstartTime, IntStartTime, ColdStartTime, Maxweeklystarts, maxonlinetime, maxdailystarts, maxweeklystarts, hotinttime, intcoldtime, syscondensercapable should be populated for any Configuration and any ThermalGeneratingUnit / HydroGeneratingUnit / NuclearGeneratingUnit / WindGeneratingUnit which has no association to a CombinedCyclePlant, a DCTie and a PrivateAreaNetwork (NetworkType: Non Modeled Generation, Retired, Mothballed, BlockLoadTransfer) . |
| R76 | Attributes (Resource Parameters), HighReasonabilityLimit, LowReasonabilityLimit, HighReasonabilityRampRateLimit, LowReasonabilityRampRateLimit, MaxSustainableRating, MinSustainableRating, MaxEmergencyRating, MinEmergencyRating should be populated for any Configuration and any ThermalGeneratingUnit / HydroGeneratingUnit / NuclearGeneratingUnit / WindGeneratingUnit which has no association to a DCTie and a PrivateAreaNetwork (NetworkType: Non Modeled Generation, Retired, Mothballed, BlockLoadTransfer). |
| R77 | Each Configuration must have at least one PRIMARY CCU (defined as CONFIGURATIONMEMBER with PRIMARY flag = ‘TRUE’ ) |
| R78 | Each CombinedCyclePlant must have at least one configuration that can start up (i.e. STARTUPFLAG = ‘TRUE’) |
| R79 | Each CombinedCyclePlant must have at least one configuration that can shut down (i.e. SHUTDOWNFLAG = ‘TRUE’) |
| R80 | Each Configuration must satisfy at least one of the two conditions a) have at least one in-transstate (i.e. transstate with that configuration as TOCONFIG_CONFIGURATION) or b) its STARTUPFLAG is set to ‘True’ |
| R81 | Each Configuration must have at least one of the two conditions a) have at least one out-transstate (i.e. transstate with that configuration as FROMCONFIG_CONFIGURATION) or b) its SHUTDNFLAG is set to ‘True’ |
| R82 | All Configurations must have path to transit from start-up configuration AND transit to shut-down figuration in some way. This can be direct transstate or through other configurations. This is to prevent CC Plant being trapped ONLINE or OFFLINE |
| R83 | Validate the UpTransition Attribute on a TransState: If UpTransition = True, count of primary members in the FromConfiguration < count of primary members in the ToConfiguration and if UpTransition = False, count of primary members in the FromConfiguration > count of primary members in the ToConfiguration. |
| R84 | Every Zonal DiscreteValue with no association to a DiscreteName should be associated with a zonal MeasurementValueQuality and a zonal MeasurementValueSource. Every Nodal DiscreteValue with no association to a DiscreteName should be associated with a Nodal MeasurementValueQuality and a nodal MeasurementValueSource. |
| R85 | All x_axisdata data points in a MVArCapabilityCurve should be unique |
| R86 | Only one y1_axisdata point in a MVArCapabilityCurve can be 0. |
| R87 | Only one y2_axisdata point in a MVArCapabilityCurve can be 0. |
| R88 | For every ICCPQualityConversion instance, a. Only One of the following attributes ICalculated, IManual, IEstimated, ITelemetered should be true, and b. Only One of the following attributes IValid, INotValid, ISuspect, IHeld should be true, and c. Only One of the following attributes OValid, ONotValid, OSuspect, OHeld should be true, and d. Only One of the following attributes OCalculated, OManual, OEstimated, ITelemetered should be true. |
| R89 | There should be atleast one swing bus in the model. i.e. atleast one connectivity node with SlackBusPriority = True |
| R90 | There should be no Pricingvector associated to a BusbarSection or a Endcap. |
| R91 | For an EnergyConsumer (CustomerLoad or StationSupply), if conformingLoadFlag = True, then the EnergyConsumer should be associated to a ConformLoadGroup |
| R92 | When a MeasurementLocation has more than one children (MeasurementGroup or Calculation), (All zonal analogvalues and discretevalues associated to the child MeasurementGroup) and (All zonal Analogvalues and discretevalues associated with measurementargument having referencefalg = False within the child calculation) should be associated to the same terminal. All Nodal analogvalues and discretevalues associated to the child MeasurementGroup) and (All Nodal Analogvalues and discretevalues associated with measurementargument having referencefalg = False within the child calculation) should be associated to the same terminal. For example 1. MeasLoc1 -> MeasGrp1 -> AnalogValue1 ->Analog1 ->Terminal1 2. MeasLoc1 -> MeasGrp1 -> AnalogValue2 ->Analog2->Terminal1 3. MeasLoc1 -> Calc1 -> MeasArg1 (referenceflag = false) -> AnalogValue3 ->Analog3 ->Terminal1 4. MeasLoc1 -> Calc1 -> MeasArg1 (referenceflag = false) -> AnalogValue4 ->Analog4->Terminal1 |
| R93 | A TriggerCondition may have multiple Gates associated with it. One of them must be its resulting Gate, (i.e. the Gate determing the trigger condition). This resulting Gate must be of type: or/and/nand/nor |
| R94 | If a Gate is of the following types: gt/ge/ lt/le/eq/ne, then its input must be exactly One PinFlow or PinBranchGroup or PinVoltage. If input is PinFlow then PinFlow.InputIsFlow must be TRUE, |
| R95 | If a Gate is of the following types: or/and/nand/nor, then its input must be one or more PinGate or PinSwitch. or PinFlow. If input is PinFlow then PinFlow.InputIsFlow must be FALSE |
| R96 | If a Gate is of the following types: not, then its input must be exactly one PinGate or PinSwitch. |
| R97 | MRID and TEIDs in the entire model should be unique. |
| R98 | Any Company with CompanyType = QSE or ERCOT can Own and Operate Zero Or One Substation with ForNetwork = False and ForSCADA = True. |
| R99 | For any GeneratingUnit, LoadResource and ControllableLoadResource each QSE operator of the GeneratinUnit needs to Own a Substation with ForNetwork = False and ForSCADA = True. Ex. GU->OSL->Operatorship->Company->Ownership ->Substation (forNetwork = False and ForSCADA = True) |
| R100 | The owner of a GeneratingUnit, LoadResource and ControllableLoadResource should always be an RE or ERCOT. Operator should be a QSE or ERCOT. |
| R101 | For every generating unit that’s not associated to a combined cycle plant, maximumOperatingMW = HRL and minimumOperatingMW = LRL |
| R102 | All instances of the following classes should have a unique name, Contingencies ContingencyGroups RemedialActionSchemes SharedProtectiveActions VoltageLimitSets , ResourceNode, HubBus |
| R103 | The total number of CalculationArguments (MeasurementArgument and/or ConstantArgument) associated to a Calculation must be equal to or greater than the total number of FunctionArguments the associated Function |
| R104 | In a Calculation every associated CalculationArgument (MeasurementArgument and/or ConstantArgument) should be associated to a unique FunctionArgument in the function associated to the Calculation |
| R106 | All conformLoads should have conformingloadflag = True and all nonconformloads should have conformingloadflag = False |
| R107 | A BLT-load, DCTie-load and a PUN-load should be of the type NonConformLoad |
| R108 | Name Length Limitations 2 AclineSegment. 4 TapChanger ,ConnectivityNode,ContingencyGroup Configuration,MeasurementGroup,Calculation VoltageLimitSet,VoltageLevel,CurveData,PowerTransformer Gate,PinBranchGroup,PinFlow,PinGate,PinSwitch PinTriggerCondition,PinVoltgae,Stage,StageTrigger AnalogName,Analog,AnalogLimitName DiscreteName,Discrete,MeasurementArgument,ConstantArgument ConstantValue 6 Company.(IO.Localname), FlowgateGroup 8 Substation,LoadbasedRegulationCurve MVArCapabilityCurve,PhaseShifterImpedanceCurve RampRateCurve,StationSupplyWRCurve,RemedialActionScheme TriggerCondition,Function,Site 12 IccpQualityConversionSet,IccpQualityConversion 14 Breaker,Disconnector,TransformerWinding,CutomerLoad LoadResource,Line,ShuntCompensator,StaticVarCompensator ResourceController,Company.(IO.AliasName),TieLine TieCorridor,ThermalGeneratingUnit,HydroGeneratingUnit NuclearGeneratingUnit,WindGeneratingUnit,SynchronousMachine SubLoadArea,LogicalConfiguration,PrivateUseNetwork |
| R109 | Every PowerSystemResource can have only one MeasurementLocation of a Particular Devicetype, i.e. Given a condition Device1 ->MeasLoc1 (RDFID: ABCD) DeviceTypeName: LD, Device1 ->MeasLoc1 (RDFID: FGHD) DeviceTypeName: LD : Invalid Device1 ->MeasLoc1 (RDFID: ABCD) DeviceTypeName: LDRES : Valid. |
| R110 | Measurement Argument or Constant argument under a Calculation should not be mapped to same Measurement Value or Constant Value. |
| R111 | An electrical bus must be associated with a connectivity node when: * a load is attached to the node. * Three or more switches are attached to the node and the node has a voltage reading |
| R112 | The RID for EPSmeter must be unique |
| R113 | customerLoad and Load instances cannot have association to PrivateAreaNetwork of type ERCOTPANTYPE.PrivateUseNetwork or SelfServe or BLT_Normally_out |
| R114 | Number of CurveScheduleData under PhaseShifterImpedanceCurve and TransformerImpedanceCurve are the same as Number of TapChanger step within PowerTransformer where the curve is asscociated to |
| R115 | FlowgateElement must associate with terminal of line/transformer/series (not allow association to other type of equipment) |
| R116 | OwnerShareLimit.name should be unique for Split generation resource . |
| R117 | A HubBus associates with 1..n ConnectivityNodeGroups. If a HubBus is associated to more than 1 ConnectivityNodeGroups, then ALL the associated ConnectivityNodeGroups must belong to the same Substation |
| R118 | Each DCTIE must associate with ONE and ONLY ONE ThermalGeneratingUnit |
| R119 | If a breaker or disconnector is modeled under a Bay instead of a VoltageLevel, then the association between Breaker/Disconnector to VoltageLevel should be populated. |
| R120 | If the Transformer is a Phase Shifting Transformer, a Phase Shifter Impedance Curve should be associated through the “Has A (PhaseShifterImpedanceCurve)” linkage. |
| R121 | If the Transformer is equipped with a Tap Ratio Curve, a Tap Ratio Curve should be associated through the “Has A (TapRatioCurve)” linkage. |
| R122 | A ConnectivityNodeGroup must have a unique PSSEBusNumber |
| R123 | Endcaps should not be connected to nodes with multiple equipment connection. |
| R124 | Each LoadSchedule should be connected to a load |
| R125 | Devices with 2 terminal must have one terminal with Near = True. Exception PowerTransformers should be considered as the "device" instead of TransformerWinding, PowerTransformer should not have the terminals connect to same connectivity node |
| R126 | Every Measurement (Analog/Discrete) should always have only one SCADA MeasurementValue (AnalogValue/DiscreteValue with association to AnalogName/DiscreteName) . |
| R127 | OwnerShareRating associated to Ratings of ratingtype = "Dynamic", should be associated to a single DynamicElement. |
| R128 | OwnerShareRating associated to Ratings of ratingtype = "Dynamic", should be associated to a weatherStation and/or a weatherstationalt. |
| R129 | Verify Equipment that needs an Electrical bus has one when connectivity changes. |
| R130 | For an instance of ICCP AnalogValue ( Alias name of anlog value not null ) only one of these 4 attributes must be set to TRUE . Remote Site Normally Calculated ,Remote Site Normally Estimated, Remote Site Normally Manually Entered, Remote Site Normally Telemetered |
| R131 | Every OwnerShareRating with an association to dynamicelement should have 1 Rating with ratingtype = Static, and 20 ratings with (ratingtype = Dynamic and unique temperature value) |
| R132 | Under the same aclinesegment, a company (duns) can own only one OwnerShareRating using the association OwnerShareRatingRatedByOwner. |
| R133 | Every Measurement of type MW, MVAR, should have 1/2 ICCP AnalogValue associated with it. |
| R134 | An equipment (Tranformer/Line) having MVAr and MW measurments needs to have a MVA Measurement as well. |
| R135 | Every MVA measurement associated to a Line or a Transformer should have an AnalogLimitSet with fornetwork = false. Deleted with MGRR0018 |
| R136 | Every KV, MVA, MVAr, MW, ST measurement should have Measurement.Unit and Measurement.MeasurementType association populated. |
| R137 | Winding's associated basevoltage must be equal to connectivitynodes base voltage |
| R138 | If ThermalGenUnit.CombinedCyclePlant is non null, ThermalGenUnit.CCP = CfgMem > Cfg > LogicalCfg > CCP. |
| ID 3 | A ConnectivityNodeGroup cannot span multiple VoltageLevels |
| ID 4 | A ConnectivityNodeGroup cannot span multiple Substations |
| ID 5 | A ConnectivityNodeGroup must have a unique PSSEBusNumber |
| ID 10 | Devices with 2 terminal must have one terminal with Near = True. Exception PowerTransformers should be considered as the "device" instead of TransformerWinding, PowerTransformer should not have the terminals connect to same connectivity node |
| ID 11 | Every Measurement (Analog/Discrete) should always have only one SCADA MeasurementValue (AnalogValue/DiscreteValue with association to AnalogName/DiscreteName) and one/two ICCP MeasurmentValues (AnalogValue/DiscreteValue with association to MeasurementValueSource) |
| ID 13 | OwenrShareRating associated to Ratings of ratingtype = "Dynamic", should be associated to a single DynamicElement. |
| ID 14 | OwnerShareRating associated to DynamicElement, should be associated to a weatherStation and/or a weatherstationalt. |
| ID 18 | Disallow branch equipment from crossing across voltage levels E.g. the terminals of an ACLineSegment cannot be in different voltage levels. SeriesCompensators are excluded from this list. |
| ID 19 | Every OwnerShareRating with an association to dynamicelement should have 1 Rating with ratingtype = Static, and 20 ratings with (ratingtype = Dynamic and unique temperature value) |
| ID 20 | Under the same equipment, a company (duns) can own only one OwnerShareRating using the association OwnerShareRatingRatedByOwner. |
| ID 21 | Every Measurement of type MW, MVAR, should have 1/2 ICCP AnalogValue associated with it. |
| ID 22 | An equipment (Tranformer/Line) having MVAr and MW measurments needs to have a MVA Measurement as well. |
| ID 23 | Every MVA measurement associated to a Line or a Transformer should have an AnalogLimitSet with fornetwork = false. |
| ID 27 | For every ownersharerating with association to dynamicelement, all children Ratings of ratingtype =Dynamic, should have unique activatevalue. |
| ID 28 | For every ownersharerating with association to dynamicelement, all children for every Ratings of ratingtype =Dynamic, the attribute activatevalue can have only 20, 25, 30, 35…115. |
| ID 30 | Tapchangers with attribute TCulControlMode <> off, should have TapChangerRegulatesTerminal and TapchagnerHasARegulationSchedule associations populated. |
| ID 31 | Tapchangers with attribute TCulControlMode = off, should not have TapChangerRegulatesTerminal and TapchagnerHasARegulationSchedule associations populated. And should have automaticvoltageregulation =false and loadbasedregulation = false |
| ID 32 | Measurement Location and Bus barsection name length 14 limit |
| ID 33 | Spaces are not allowed in names of equipment |
| ID 34 | Check if these associations for a generating unit are linked: GeneratingUnitHasAGenerationType, GeneratingUnitMemeberofSubLoadArea is required for all non DCTie-GenUnits. |
| ID 35 | Substation.HostControlArea is a required association |
| ID 37 | For ShuntCompensators, SVCs, synchronousmachines and tapchagners, if automaticvoltageregulation = True, Regulationsschedule, and regulatingterminal should be present. |
| ID 38 | For ShuntCompensators, SVCs, synchronousmachines and tapchagners, if loadbasedregulation = True, loadbasedregulationschedule, and regulatingterminal should be present. |
| ID 39 | For ShuntCompensators, SVCs, synchronousmachines and tapchagners, if automaticvoltageregulation = false, Regulationsschedule, and regulatingterminal should not be present. |
| ID 40 | For ShuntCompensators, SVCs, synchronousmachines and tapchagners, if loadbasedregulation = false, loadbasedregulationschedule, and regulatingterminal should not be present. |
| ID 41 | Discrete/Analog values associated to MeasurementValueSource must have unique names |
| ID 42 | Series compensator folder can only have series compensators |
| ID 43 | Don’t consider Bus Bus as an equipement. When looking for endcaps |
| ID 44 | ACLineSgments should not have both ends in the same substation. |
| ID 45 | Two or more BusbarSections cannot be connected to the same ConnectivityNode. |
| ID 46 | AnalogValue.AnalogAlarmCategory,is conditionally required association on all MeasurmentValues associated to AnalogName/Discretename. Refer Appendix E in modeling guidelines v1.0 for an additional validation check. DiscreteValue.DiscretAlarmCategory is a required association exclude anything other than MVAR, MW, MVA, KV |
| ID 47 | All PowerSystemResource except ACLineSegments should be associated to zero or one MeasurementLocation. ACLineSegments can be associated to zero, one or two MeasurementLocations. PowerTransformers should not be associated to any MeasurementLocations |
| ID 48 | MeasurementLocation should always have a child (either MeasurementGroup or Calculation) associated with it. |
| ID 49 | MeasurementArgument.referenceFlag = True, if for the associated MeasurementValue, MeasurementValue.MeasurementGroup is not null or MeasurementValue.Calculation <> parent of the MeasurementArgument. |
| ID 50 | Calculation should always have atleast one child of type MeasurementArgument or ConstantArgument. |
| ID 51 | A TransformerWinding when connected to a TapChanger must have TransformerWinding.ratedKV / BaseVoltage.nominalKV (traced using TransformerWinding.BaseVoltage) equal to 1. A TransformerWinding when not connected to a TapChanger must have TransformerWinding.ratedKV / BaseVoltage.nominalKV (traced using TransformerWinding.BaseVoltage between 0.8 and 1.2. |
| ID 52 | Every SynchronousMachine should be connected to a GeneratingUnit and Every GeneratingUnit should be connected to a SynchronousMachine. |
| ID 53 | GeneratingUnit.maximumcapacitylimit, Generatingunit.minimumCapacityLimit are required for all non-pun, non-dctie units. |
| ID 55 | In case of ACLineSegment & SeriesCompensator instances, every OwnerShareRating associated to a dynamicelement should be associated to a Analog whose child AnalogValue.AnalogName = ‘SSId’. |
| ID 56 | In case of dynamic ratings, as temperature increases, rating should decrease. For example NormalRating at 25 degrees <= Normalrating at 20 degrees. This check should be performed for all three required rating types. |
| ID 57 | MeasurementValues associated with a measurementValueSource should have a unique 32 char long name. |
| ID 58 | Deleted. |
| ID 59 | Node names should not get duplicated within a substation across all kVs. |
| ID 60 | Attribute LTC Control Mode on Tap Changer cannot be Null |
| ID 61 | Every ElectricalBus name should be unique throughout the entire model. |
| ID 62 | An Electrical Bus name should be 12 characters or fewer. |
| ID 64 | AnalogValue when associated with AnalogName (IO.Name = SSId), its parent’s Analog.PSR association should always be OSR. |
| ID 65 | In case of ACLineSegment & SeriesCompensator instances, the total number of AnalogValue(IO.Name= SSID) instances should be equal to the total number of OwnerShareRating instances with association to DynamicElement. |
| ID 66 | For every analog Analog.PSR = Analog’s Grandparent, except when a. the analog.psr type is PowerTransformer, Analog.PSR = Analog’s greatgrandparent b. the analog.PSR type is OwnerShareRating, Analog.PSR’s parent = Analog’s grandparent c. the analog.PSR type is ControllableLoadResource or LoadResource, Analog.PSR’s parent = Analog’s grandparent d. If grandparent of analog is of type ownersharelimit then Anloag.PSR should be of type SynchMachine and Synchmachine.GU should be analogs Greatgrandparent |
| ID 67 | Every Unit needs association to EPS meter unless: a)The unit's has a link to PrivateArea Network & PAN Type is BLT, Non Modeled, Retired, or Mothbolled b) the unit is Block Load Transfer. |
| ID 68 | Every PowerTransformer should have 2 TransformerWinding at its children. |
| ID 69 | For all instances of type NonConformLoad, conformingLoadFlag boolean = False. |
| ID 70 | DUNS number should be unique across all companies. |
| ID 71 ID 72 | All Analog/Discrete Measurements connected to the same PowerSystemResource except Lines (ACLineSegements only) should have a unique association thru AnalogValue/DiscreteValue to AnalogName. In case of Lines (ACLineSegements only), all Analog/Discrete Measurements connected to the same terminal should have a unique association thru AnalogValue/DiscreteValue to AnalogName. Add ProtectionEquipment to list of not allowed classes as well. |
| ID 73 | a. ConductingEquipment like, ACLineSegement, BusbarSection, EndCap, CustomerLoad, Load, NonConformLoad, InductionMotorLoad, StationSupply, ShuntCompensator, StaticVarCompensator, SynchronousMachine, SeriesCompensator, Disconnector, Breaker, TransformerWinding should always be connected to a Terminal. b. COmbinedCyclePlant, GenericEquipment should always be connected to a PseudoTerminal. C. OwnerShareLimits associated to JOUs should always be connected to a PseudoTerminal. |
| ID 74 | For AnalogValue/DiscreteValue associated with AnalogName/DiscreteName, only one amongst the booleans, FromRemote, FromCalculation, FromExternalProgram must be True. |
| ID 76 | For AnalogValue/DiscreteValue associated with AnalogName/DiscreteName and fromCalculation = True, a. should be connected to a MeasurementArgument whose FunctionArgument.writeFlag = True. B. Its parent measurement can be connected to 0 AnalogValue/discreteValue with MeasurementValueSource from non-ERCOT company and atmost 2 AnalogValue/discreteValue with MeasurementValueSource sourced from ERCOT. |
| ID 77 | For AnalogValue/DiscreteValue associated with AnalogName/DiscreteName and FromExternalProgram = True, a. should not be connected to any MeasurementArgument whose FunctionArgument.writeflag = True. b. Its parent measurement can be connected to 0 AnalogValue/DiscreteValue with MeasurementValueSource from non-ERCOT company and atmost 2 ICCP AnalogValue/DiscreteValue with MeasurementValueSource from ERCOT. |
| ID 78 | For AnalogValue/DiscreteValue associated with AnalogName/DiscreteName and FromRemote = True, a. should not be connected to any MeasurementArgument whose FunctionArgument.writeflag = True. b. If AnalogName.name = (MW, MW2, MW3, MVAR, MVR1) and parent measurement.PSR type = (ACLineSegment, SeriesCompensator, PowerTransformer) then its parent measurement can be connected to 1 AnalogValue/DiscreteValue with MeasurementValueSource from non-ERCOT company and atmost 2 AnalogValue/discreteValue with MeasurementValueSource sourced from ERCOT. c. If AnalogName.name <> (MW, MW2, MW3, MVAR, MVR1) and parent measurement.PSR type <> (ACLineSegment, SeriesCompensator, PowerTransformer) then its parent measurement can be connected to 0, 1 AnalogValue/DiscreteValue with MeasurementValueSource from non-ERCOT company and atmost 2 AnalogValue/discreteValue with MeasurementValueSource sourced from ERCOT. |
| ID 79 | Non zero, X values should be defined at each PowerTransformer. |
| ID 80 | For RegulatingCondEq (ShuntCompensator, SVC, Synchronousmachine) and Tachangers with nonnull RegulatingTerminal and RegulationSchedule, Target Voltage on the Regulation schedule should be within 80% to 120% of the regulating node voltage 0.8 <= (RegularTimePoint.value1) / (RegulatingTerminal_ConnectivityNode_BaseVoltage_VoltageLevel_nominalVoltage) <= 1.2 |
| ID 81 | For TapChangers, Neutral KV value should be within 80% to 120% of its base voltage 0.8 <= (TapChanger.neutralKV) / (Transformer.BaseVoltage) <= 1.2 |
| ID 82 | LoadBasedRegulatingCurves should have unique xaxisdata in their associated CurveData instances. |
| ID 83 | TransformerWindings, ACLineSegments, SeriesCompensators, VoltageLevels should always be connected to a BaseVoltage. |
| ID 84 | MVARCapabilityCurve, StationSupplyWRCurve, LoadbasedRegulationCurve, PhaseShifterImpedanceCurve, TransformerImpedanceCurve, TapRatioCurve should all have unqiue 8 char long alias names. |
| ID 85 | Modify name length requirements for Lines to be 14 when defined with a single segment and 11 characters when defined with multiple segments. |
| ID 86 | In case of MVARCapabilityCurves, Curvedata.y1axisdata < CurveData.y2axisdata. |
| ID 87 | Tapchangers with tculcontrolmode <> "MW" then stepvoltageincrement should be non-null, and stepphaseincrement should be zero or null. |
| ID 88 | Tapchangers with tculcontrolmode = "MW" then stepphaseincrement should be non-null, and stepvoltageincrement should be zero or null. |
| ID 90 | Every ConformLoadSchedule and NonConformLoadSchedule should be connected to 24 regulartimepoints with non-null value1, value2. |
| ID 91 | Every ConformLoadGroup and NonConformLoadGroup should be connected to 7 COnformLoadSchedule and NonConformLoadSchedule respectively. |
| ID 93 | a. For all instances of type InductionMotorLoad, conformingLoadFlag boolean = False. b. For all instances of type Load, CustomerLoad, conformingLoadFlag boolean = True. |
| ID 94 | SCADA Validation for Generating Units based on type. Drop ‘REQ’ Analog requirement from OwnerShareLimits |
| ID 104 | ThermalGenUnit.CombinedCyclePlant should be non null for a TGU linked to ConfigurationMember |
| ID 105 | If ThermalGenUnit.CombinedCyclePlant is non null, ThermalGenUnit.CCP = CfgMem > Cfg > LogicalCfg > CCP. |
| ID 106 | If ThermGenUnit.CCP is non null, the ThermalGenUnit should be non-retired, non-mothballed, non-nonmodeledgeneration, non-dctie, non-blt. or ConfigurationMember.ThermalGenUnit should be non-retired, non-mothballed, non-nonmodeledgeneration, non-dctie, non-blt |
| ID 109 ID 110 | Pseudo QSE Substations viz. Substations in WZ_SCADA_Only owned by QSE, § Should have 3 GenericEquipment with the names REGD, REGU, RR. DSRL is Optional. § Each of the above equipment when present, should be linked with a measurement whose, Measurment_MeasurementValue_MeasurementName.Name = GenericEquipment.Name Line names and LineName + SegmentName should be unique across all voltage levels. |
| ID 114 | SynchMach.Terminal is required association |
| ID 115 | Ownersharelimit.PseudoTerminal is required association for Jointly owned units |
| ID 116 | Every GeneratingUnit (Thermal, Hydro, Nuclear, Wind) that is associated to a DCTIE, a BlockLoadType or a retired unit. Should not have an association to ResourceNode |
| ID 117 | We need to have a new validation rule for shunt PSSE ID’s in production. As per PTI requirements, shunts PSSE ID’s should be populated with numeric value only and it should be between 1and 8. If a TSP submits an alphanumeric PSSEID or PSSEID above 8 then he should get an error. All the PSSE ID’s for a particular station should be consecutive and TSP’s cannot skip any number in between. Also, there is a PTI requirement that if there are 2 shunts on a CNG; one is a reactor and one is a capacitor then the reactor should be assigned PSSE ID 1 and the capacitor should be assigned PSSE ID 2. Always the reactor should have lower PSSE ID than the capacitor. Also, if there are 2 or more shunts on the same CNG then they cannot have same PSSE ID’s if their sizes are different or if 1 is a reactor and the other is a capacitor. For example if we have 3 reactors on one CNG and if all three have different sizes then they cannot have same PSSE ID or if we have 1 capacitor and 1 reactor on the same CNG and both are of same size then also they cannot have same PSSE ID’s. And above all shunt PSSEID is a mandatory field with all the above rules in place. If this field is not populated then it won’t come across TP. The following is the requirement from PTI. “The shunt compensators will be added to the switched shunt in ascending order of psseid. The psseid should be populated with numerical values only ranging between 1 and 8. Numbers may not be skipped or omitted. Shunt compensators with unique psseid’s will be placed in a group by themselves in the switched shunt record. In order for shunt compensators to be congregated into the same group, they must be the same size.” |
| ID 123 | A TAPS, TAP, TAP1 measurement when present should be on the same winding as TapChanger./If there exists a TAPS, TAP or TAP1 measurementvalue, then a Tapchanger must be associated to that winding |
| ID 124 | Tapchangers associated to Power Transformers are not allowed to link to an Analog with AnalogValue.[AnalogName.name] = TAPS.TransformerWindings associated with TapChanger tculcontrolmode <> 'MW' cannot be associated with a Analog with AnalogValue.[AnalogName.name] = TAPS. |
| ID 125 | Tapchangers associated to Phase Shifters are not allowed to link to an Analog with AnalogValue.[AnalogName.name] = TAP or TAP1.TransformerWindings associated with TapChanger tculcontrolmode = 'MW' cannot be associated with a Analog with AnalogValue.[AnalogName.name] = TAP or TAP1. |
| ID 126 | PrivateAreaNetwork.netowrktype is a required attribute. |
| ID 128 | TapChangers with TCulControlMode <> (off, MW) 1. If avrenabled = True, association TapChangerRegulatesTerminal should be non null. 2. If avrenabled = True, either association TapChangerHasARegulationSchedule or TapChangerRegulatedByLoadBasedRegulationCurve should be populated. 3. AwrEnabled cannot be True. 4. If avrenabled = True and TapChangerRegulatedByLoadBasedRegulationCurve is non null, loadbasedRegulationenabled = True 5. If avrenabled = True, both associations TapChangerHasARegulationSchedule and TapChangerRegulatedByLoadBasedRegulationCurve cannot be non null at the same time. |
| ID 129 | TapChangers with TCulControlMode = (MW) 1. If awrenabled = True, association TapChangerRegulatesTerminal should be non null. 2. If awrenabled = True, either association TapChangerHasARegulationSchedule or TapChangerRegulatedByLoadBasedRegulationCurve should be populated. 3. AvrEnabled cannot be True. 4. If awrenabled = True and TapChangerRegulatedByLoadBasedRegulationCurve is non null, loadbasedRegulationenabled = True 5. If awrenabled = True, both associations TapChangerHasARegulationSchedule and TapChangerRegulatedByLoadBasedRegulationCurve cannot be non null at the same time. |
| ID 130 | TapChangers with TCulControlMode = (off) 1. AvrEnabled and AwrEnabled cannot be True. |
| ID 131 | ShuntCompensators, SynchronousMachine, StaticVarCompensator 1. If avrenabled = True, association RegulatingCondEqRegulatesTerminal should be non null. 2. If avrenabled = True, either association RegulatingCondEqHasARegulationSchedule or RegulatingCondEqRegulatedByLoadBasedRegulationCurve should be populated. 3. If avrenabled = True and RegulatingCondEqRegulatedByLoadBasedRegulationCurve is non null, loadbasedRegulationenabled = True 4. If avrenabled = True, both associations RegulatingCondEqHasARegulationSchedule and RegulatingCondEqRegulatedByLoadBasedRegulationCurve cannot be non null at the same time. |
| ID 135 | CNG.name must be the same as its PSSEBusNumber |
| ID 136 | No duplicate CNGs in the Model |
| ID 137 | Electrical Bus names should always be uppercase letters |
| ID 138 | PSSE Bus Number Attribute and CNG Name Cannot be greater Than 999996 PSSE Bus Number Attribute and CNG Name Cannot be between 96000 – 699999 |
| ID 139 ID 141 ID 142 ID 143 ID 144 | PSSE Bus Name can be Alpha Numeric with first character of PSSE Bus Name Attribute must not be a minus sign Tranformer winding and Aclinesegment must have a parent child association with an instance of type OwnerShareRating. Analog.a_for_network must be same as AnalogLimitSet.a_fornetwork Display an error if multiple AnalogLimits with same Limit Type are present under the AnalogLimitSet and also if count of Analoglimits under ALS is not 3 and under Ratings (static rating) is not 4 Network/Scada/OSR ratings cannot have null A_value /a_upperthreshold/a_lowerthreshold values |
| ID 145 | All the Ratings of same type must be same under a transformer netmom=scadamom=OSR for single owned trnsformers |
| ID 146 | All the Ratings of same type must be same under a line.netmom=scadamom=OSR for single owned lines and NRML<=2HR<=15MN |
| ID 147 | deleted |
| ID 148 | Normal Open and Initial Open to match on a switch |
| ID 149 | Validation to include Cond.Rating .Conductor Rating >= 2 Hour Rating on a Line |
| ID 150 | Validation to include Cond.Rating .Conductor Rating >= 2 Hour Rating on a Transformer |
| ID 151 | As per PTI requirements, shunts PSSE ID’s should be populated with numeric value only and it should be between 1and 8. All the PSSE ID’s for a particular station should be consecutive and TSP’s cannot skip any number in between. Also, there is a PTI requirement that if there are 2 shunts on a CNG; one is a reactor and one is a capacitor then the reactor should be assigned PSSE ID 1 and the capacitor should be assigned PSSE ID 2. Always the reactor should have lower PSSE ID than the capacitor. Also, if there are 2 or more shunts on the same CNG then they cannot have same PSSE ID’s if their sizes are different or if 1 is a reactor and the other is a capacitor. For example if we have 3 reactors on one CNG and if all three have different sizes then they cannot have same PSSE ID or if we have 1 capacitor and 1 reactor on the same CNG and both are of same size then also they cannot have same PSSE ID’s. And above all shunt PSSEID is a mandatory field |
| ID 152 ID 153 ID 154 ID 155 ID 156 ID 157 ID 158 ID 159 ID 160 | Customerload PSS/E id should be alphanumeric and 2 char long NonConformLoad PSS/E id should be alphanumeric and 2 char long HydroGeneratingUnit should be alphanumeric and 2 char long ThermalGeneratingUnit PSS/E id should be alphanumeric and 2 char long NuclearGeneratingUnit PSS/E id should be alphanumeric and 2 char long WindGeneratingUnit PSS/E id should be alphanumeric and 2 char long PowerTransformer PSS/E id should be alphanumeric and 2 char long TransformerKludge PSS/E id should be alphanumeric and 2 char long TransformerKludge PSS/E name should be alphanumeric and 2 char long ACLineSegmentPSS/E id should be alphanumeric and 2 char long CustomerLoad must be linked to PlanningArea, Planning Zone NonConformLoad must be linked to PlanningArea, Planning Zone SeriesCompensator PSS/E id should be alphanumeric and 2 char long StaticVarCompensator --Can Be alpha Numeric and 2 Character limitation Length Attribute on an ACLinesegment is required field. For an instance of type Configuration all the following attributes are required highReasonabilityLimit, lowReasonabilityLimit, highReasonabilityRampRateLimit, lowReasonabilityRampRateLimit, seasonalMaxSustainableRating, seasonalMinSustainableRating, seasonalMinEmergencyRating, minONTime, minOFFTime, hotStartTime, intStartTime, coldStartTime, maxWeeklyStarts, maxONTime, maxDailyStarts, maxWeeklyEnergy, hotintTime, intColdTime Every SynchronousMachine must be either connected to a RegulationSchedule or a LoadbasedRegulationCurve If more than one AClineSegment/Series Compensator is connected between the same set of ConnectivityNodeGroups (Buses) then the PSSEids on the aclinesegments/SeriesCompensators should be unique If more than one 2 winding PowerTransformer is connected between the same set of ConnectivityNodeGroups (Buses) then the PSSEids on the PowerTransfomers should be unique PSSEID is a required attribute on instances of type ACLinesegment, SeriesCompensator and PowerTransformer If a new ConnectivityNodeGroup is added under a VL that already has a CNG that is associated to a HUBBus then the new CNG must also be associated to the same Hubbus. All Configurations must be associated to the same EPSMeters as the ThermalGeneratingUnits contained within the configuration. ID 161 WindingType should be unique for all TransformerWindings in a PowerTransformer. ID 162 Deleted ID 163 Series devices must be connected to 2 different ConnectivityNodeGroups (Two PTI numbers). ID 164 All primary transformer windings must have unique names within a station. ID 165 All DeviceTypeName.name linked to a single PowerTransformer via MeasurementLocation.DeviceTypeName must be unique. ID 166 Resource node name must be unique and limited to 12 chars. ID 167 Required association Resource Node must have ownership with Owner ERCOT_Resources/ResourceNode_Owner. ID 168 1KV ConnectivityNode, when connected three 1KV TransformerWindings, must have all of the associated PowerTransformers connected to a ThreeWindingKludge. ID 169 Every Line via its terminal can be linked to 0 or 1 TieLine. ID 170 An instance of Disconnector must point to at least 1 Operationship instance. ID 171 a. ACLineSegment's Terminals should be connected to ConnectivityNodes with the same BaseVoltage but lying in two different stations. b. Terminals of a PowerTransformer should be connected to ConnectivityNodes within the same substation. c. All other equipment with more than one Terminal should be connected to ConnectivityNodes within the same VoltageLevel. ID 172 If a Load (CustomerLoad, NonConformLoad) is associated with a DCTie or a Load (CustomerLoad, NonConformLoad) is associated with a SettlementNOIELoadZone, then Substation this load resides-in must be associated to a SettlementLoadZone. ID 173 For Ratings with ratingType = Dynamic perform nested limit violation test i.e. FifteenMin>= TwoHr >= NRML ID 174 For every TieCorridor, when TieCorridorConnectsToSubLoadArea is not null then the ToSubLoadArea (TieCorridorConnectsToSubLoadArea) <> FromSubLoadArea (TieCorridorConnectsFromSubLoadArea). ID 175 1. If TieCorridorConnectsToSubLoadArea is non null, TieCorridorConnectsToHostControlArea must be populated. 2. If TieCorridorConnectsToHostControlArea is ERCOT, TieCorridorConnectsToSubLoadArea must be populated. 3. If TieCorridorConnectsToHostControlArea is EXTERN, TieCorridorConnectsToSubLoadArea must be null. ID 176 EquipmentMemberOfEquipmentContainer association for a PowerTransformer must always point to a Substation. ID 177 Electrical buses are needed at the connectivity nodes of ACLine terminals for all sites with units, resource nodes, and/or EPS meters. ID 178 Every OwnerShareRating instance must be associated with at least one Rating instance. ID 179 Every Rating instance must be associated with at least three AnalogLimit instances. ID 180 Every OwnerShareRating instance must be associated with only one Rating instance with attribute ratingType = 'Static Rating'. ID 181 At least one OwnerShareRating instance must be present for every SeriesCompensator instance. ID 182 Attribute psseid is required to be populated for all instances of type Company, CustomerLoad, HydroGeneratingUnit, InductionMotorLoad, Load, NonConformLoad, NuclearGeneratingUnit, PlanningArea, PlanningZone, SettlementLoadZone, SettlementNOIELoadZone, ShuntCompensator, StaticVarCompensator, StationSupply, SynchronousMachine, ThermalGeneratingUnit, WindGeneratingUnit. ID 183 PSSEID for Breaker, Disconnector, InductionMotorLoad, Load, StationSupply and SynchronousMachine should be alphanumeric & 2 characters long. ID 184 With GeneratingUnits (GU), linked OwnerShareLimits (OSL) and OSL.oWnership (via OSLLimitsByOwnership) (OW) OSL.HRL = GU.hrl * (OW.ownPercent / 100) +/- 5% OSL.LRL = GU.lrl * (OW.ownPercent / 100) +/- 5% OSL.maxweeklyenergy = GU.maxweeklyenergy * (OW.ownPercent / 100) +/- 5% ID 185 Description Field on a Substation is a required attribute ID 186 Magnetizing branch susceptance and magnetizing susceptance in saturation region for a TransformerWinding must be equal to or less than 0. ID 187 Every Transformer Kluge should be associated to three two winding transformers with the neutral being at 1KV. ID 188 ShuntCompensatorALt instances with controlmode like 'Switched%' or a_controlmod like '%_Voltage_%', must have non-null maximumkV & minimumkV. ID 189 ShuntCompensatorAlt instancs must have be connected to a ConnectivityNode via the association ShuntCompensatorAltConnectedToConnectivityNode . ID 190 ShuntCompensator & ShuntCompensatorAlt instances should have non-null maxsections, normsections, MVArperSections and pcReactivePowerTransfer. ID 191 Load instances (CustomerLoad, NonConformLoad) when connected to a PrivateAreaNetwork instance with networkType like 'SelfServe%' must have psseid like 'S%' ID 192 Load instances (CustomerLoad, NonConformLoad) having psseid starting with S% must be connected to a PrivateAreaNetwork instance with networkType like 'SelfServing' or ‘BLT_Normally_out’ or ‘PrivateUseNetwork’. ID 193 For every PrivateAreaNetwork with networkType <> 'PrivateUseNetwork', the association PANcontainsConductingEquip must be null. ID 194 Every ShuntCompenstorAlt (SCA) instance's maxkV must not be less than minKV. ID 195 The regulating Terminal of an equipment (ShuntCompensator, TapChanger, StaticVarCompensator, Synchronous Machine) must be in the same station as the equipment. ID 196 Equipment within a bay must connect to nodes in a VoltageLevel same as the Bay itself. ID 197 Substation.Name should be unique in the model. ID 198 For every ShuntCompenstorAlt (SCA) instance with controlmode in (discAdj_voltage_control, contadj_voltage_control) the ratio (regulation target voltage)/(regulated bus voltage) must be within 0.8 to 1.1. regulation target voltage: (SCA.maxKV - (SCA.maxkV - SCA.minkV)/2) regulated bus voltage : use ShuntCompensatorAltControlToConnectivityNode -> ConnectivityNode -> VoltageLevel ->BaseVoltage.nominalVoltage. If ShuntCompensatorAltControlToConnectivityNode is null, then use, ShuntCompensatorAltConnectedToConnectivityNode -> ConnectivityNode -> VoltageLevel ->BaseVoltage.nominalVoltage ID 199 Measurements with forNetwork=True are not allowed to be modeled at Terminals associated with TransformerWinding, ACLineSegment and SeriesCompensator instances. ID 200 AnalogLimitSets are not allowed to be modeled at MVA measurements associated with TransformerWinding, ACLineSegment and SeriesCompensator instances. ID 201 Fixed Shunt Compensator PSSEID should be 2 char alphanumeric for Control mode. ID 202 NonConformLoad name is going to have a limit of 14 characters. ID 203 Instance Name check ID 204 Required Link - cardinality ID 205 Checking Genreating unit operating MW against the REASONABILITYLIMIT ID 206 Operational Resource Parameters should be populated for Generating Unit ID 207 Resource Parameters should be populated for Generating Unit ID 208 Check if there are only 2 Rampratecurves associated to a SolarGeneratingUnit one of each type Emergency and Normal ID 209 Checks if the sum of the ownerships for a Solar Generating Unit for is not 100 ID 210 SolarGeneratingUnit has measurement location at most one of certain device type. ID 211 Throws an error if SubloadArea is not linked to SU unless its a DCTie ID 212 This procedure checks for any spaces in the name of the an instance ID 213 Ensure that for a Resource Node that is associated to a PUN the resource node is also not associated to a SolarGeneratingUnit ID 214 Ensure that for a Resource Node that is associated to a PUN the resource node is also not associated to a SolarGeneratingUnit ID 215 GeneratingUnit.maximumcapacitylimit, Generatingunit.minimumCapacityLimit are required for all non-pun, non-dctie units. ID 216 Checks for the required Measurement Values for GU ID 217 Checks for the required Measurement Values for GU ID 218 Checks for the required Measurement Values for GU and OSLs ID 219 Checks for the required Measurement Values for GU and OSLs ID 220 Displays an error message if a Solar Generating Unit that is associated to a Resource Node is also associated to either a DCTie or BLT or Retired type resource ID 221 CheckAV_UniqueCompositeKey unique ID 222 CheckNameRangLength ID 223 ConnectivityNodes, linked to ACLineSegments and contained in a Substation that has a ResourceNode,SynchronousMachine, or EPSMeter, must have an associated ElectricalBus.. ID 224 GeneratingUnits, linked OwnerShareLimits and OSL.oWnership (OW) OSL.HRL = GU.hrl * (OW.ownPercent / 100) +/- 5%,OSL.LRL = GU.lrl * (OW.ownPercent / 100) +/- 5%, OSL.maxweeklyenergy = GU.maxweeklyenergy * (OW.ownPercent / 100) +/- 5% ID 225 Required Link (enforce minimum cardinality) ID 226 Range Check Attribute Generating Unit::highReasonabilityLimit ID 227 Range Check Attribute Generating Unit::hotStartTime ID 228 Range Check Attribute Generating Unit::lowReasonabilityLimit ID 229 Range Check Attribute Generating Unit::maxWeeklyStarts ID 230 Range Check Attribute Generating Unit::minONTime ID 231 Range Check Attribute Generating Unit::seasonalMaxSustainableRating ID 232 Range Check Attribute Generating Unit::highReasonabilityRampRateLimit ID 233 Required attribute Generating Unit::ControlPulseHigh ID 234 Required attribute Generating Unit::ControlPulseLow ID 235 Required attribute Generating Unit::controlResponseRate ID 236 Required attribute Generating Unit::Efficiency ID 237 Range Check Attribute Generating Unit::Efficiency ID 238 Required attribute Generating Unit::GovernorMPL ID 239 Required attribute Generating Unit::GovernorSCD ID 240 Range Check Attribute Generating Unit::MaximumEconomicMW ID 241 Required attribute Generating Unit::MaximumOperatingMW ID 242 Range Check Attribute Generating Unit::MinimumEconomicMW ID 243 Required attribute Generating Unit::MinimumOperatingMW ID 244 Required attribute Generating Unit::modelDetail ID 245 Required attribute Generating Unit::OperatingMode ID 246 Required attribute Generating Unit::PenaltyFactor ID 247 Required attribute Generating Unit::StepChange ID 248 Required attribute Generating Unit::freqBias ID 249 Required attribute Generating Unit::freqDevDeadband ID 250 Required attribute Generating Unit::maxONTime ID 251 Required attribute Generating Unit::maxWeeklyEnergy ID 252 Required attribute Generating Unit::minOFFTime ID 253 Required attribute Generating Unit::minONTime ID 254 Required attribute Generating Unit::qualificationStatus ID 255 Range Check Attribute PowerSystemResource::TEID ID 256 Required Link (enforce minimum cardinality) ID 257 Required Link (enforce minimum cardinality) ID 258 Required attribute. ID 259 The owner of a Generating Unit should always be an RE. Operator should be a QSE. |

# Appendix D – Classes Not Allowed

Classes that are marked as “Not Allowed” cannot have data instances within the ERCOT CIM XML data file. The importers would ignore this data, but references between a "NOT_ALLOWED" class and a "USED" class could produce an invalid model/solution, especially if topology related. A list of classes and their compatibility with ERCOT applications will be published, and the classes marked as “Not Allowed” must NOT be populated via NOMCRs or they will be rejected in the NMMS validation step.

In the future, data for some of the classes currently “Not Allowed” may be allowed, but only after the impact has been evaluated and  the changes tested by all affected ERCOT applications. Newly created classes could also be allowed after being tested by affected ERCOT applications.

| BASICINTERVALSCHEDULE | NOT_ALLOWED - ABSTRACT |
| --- | --- |
| COMPOSITESWITCH | NOT_ALLOWED - TOPOLOGY |
| CONDUCTINGEQUIPMENT | NOT_ALLOWED - ABSTRACT |
| CONDUCTOR | NOT_ALLOWED - ABSTRACT |
| CONFORMLOAD | NOT_ALLOWED - ABSTRACT |
| CONNECTOR | NOT_ALLOWED - TOPOLOGY |
| CURVE | NOT_ALLOWED - ABSTRACT |
| DCLINESEGMENT | NOT_ALLOWED - TOPOLOGY |
| ENERGYAREA | NOT_ALLOWED - ABSTRACT |
| ENERGYCONSUMER | NOT_ALLOWED - ABSTRACT |
| ENERGYCONSUMERRESOURCE | NOT_ALLOWED - ABSTRACT |
| EQUIPMENT | NOT_ALLOWED - ABSTRACT |
| EQUIPMENTCONTAINER | NOT_ALLOWED - ABSTRACT |
| EQUIVALENTSOURCE | NOT_ALLOWED - TOPOLOGY |
| FEEDER | NOT_ALLOWED - TOPOLOGY |
| FREQUENCYCONVERTER | NOT_ALLOWED - TOPOLOGY |
| FUSE | NOT_ALLOWED - TOPOLOGY |
| GATEINPUTPIN | NOT_ALLOWED - ABSTRACT |
| GENERATINGUNIT | NOT_ALLOWED - ABSTRACT |
| GROUND | NOT_ALLOWED - TOPOLOGY |
| GROUNDDISCONNECTOR | NOT_ALLOWED - TOPOLOGY |
| JUMPER | NOT_ALLOWED - TOPOLOGY |
| JUNCTION | NOT_ALLOWED - TOPOLOGY |
| LIMIT | NOT_ALLOWED - ABSTRACT |
| LIMITSET | NOT_ALLOWED - ABSTRACT |
| LOADBREAKSWITCH | NOT_ALLOWED - TOPOLOGY |
| LOADGROUP | NOT_ALLOWED - ABSTRACT |
| MEASUREMENT | NOT_ALLOWED - ABSTRACT |
| POWERSYSTEMRESOURCE | NOT_ALLOWED - ABSTRACT |
| PROTECTEDSWITCH | NOT_ALLOWED - ABSTRACT |
| RECTIFIERINVERTER | NOT_ALLOWED - TOPOLOGY |
| REGULARINTERVALSCHEDULE | NOT_ALLOWED - ABSTRACT |
| REGULATINGCONDEQ | NOT_ALLOWED - ABSTRACT |
| SWITCH | NOT_ALLOWED - ABSTRACT |

# Appendix E – Data Types Values

AccuracyClass

| NAME | Description |
| --- | --- |
| KV | Default Accuracy class assigned to all Voltage Analog Values . Used by the State Estimator to specify the expected error in the Input Data |
| LD | Default Accuracy class assigned to Loads |
| LDHR | Accuarcy Class assigned to load MVARs which are expected to be less erroneous |
| LDHW | Accuarcy Class assigned to load MWs which are expected to be less erroneous |
| LNHK | Accuarcy Class assigned to line MWs, MVARs and MVAs which are expected to be less erroneous |
| TAP | Default Accuracy class assigned to all Tap Analog Values . Used by the State Estimator to specify the expected error in the Input Data |
| UN | Default Accuracy class assigned to Units |
| UNHR | Accuarcy Class assigned to Unit MVARs which are expected to be less erroneous |
| UNHW | Accuarcy Class assigned to Unit MWs which are expected to be less erroneous |
| UNLW | Accuarcy Class assigned to Unit MWs with expectancy of error is on High level |
| UNMW | Accuarcy Class assigned to Unit MWs with expectancy of error is on medium level |
| XFHK | Accuarcy Class assigned to Transfomer MWs and MVARs which are expected to be less erroneous |

AnalogNames

| NAME | DESCRIPTION |
| --- | --- |
| AMP | Current Measurement |
| AMP2 | Current Measurement |
| AMP3 | Current Measurement |
| AMP4 | Current Measurement |
| AMP5 | Current Measurement |
| BP | Base Point communicated to Market Participants (from SCED/Emergency BP) |
| C1 | Count of valid samples |
| C2 | Count of valid samples |
| CCC | Combined Cycle Configuration for a Combined Cycle Plant |
| CT05 | Count of valid samples within a 5-minute window |
| CT15 | Count of valid samples within a 15-minute window |
| CT60 | Count of valid samples within a 60-minute window |
| DA15 | 15-Min Dynamic Rating (in AMP) |
| DAEM | Emergency Dynamic Rating (in AMP) |
| DANR | Normal Dynamic Rating (in AMP) |
| DCIP | DC Tie Import |
| DCXP | DC Tie Export |
| DEG | Angle measurement for a Wind Generation Resource |
| DGAV | NOT VALID FOR NODAL |
| DM15 | 15-min Dynamic Rating |
| DMEM | Emergency Dynamic Rating |
| DMNR | Normal Dynamic Rating |
| DO1 | NOT VALID FOR NODAL |
| DO2 | NOT VALID FOR NODAL |
| DO3 | NOT VALID FOR NODAL |
| DR1 | NOT VALID FOR NODAL |
| DR2 | NOT VALID FOR NODAL |
| DR3 | NOT VALID FOR NODAL |
| DSRL | QSE DSR Load |
| DSRS | DSR Schedule |
| DTMP | Dynamic Rating Temperature |
| DYNS | NOT VALID FOR NODAL |
| DYOA | NOT VALID FOR NODAL |
| DYRA | NOT VALID FOR NODAL |
| EMRR | Emergency Ramp Rate for a Generation Resource |
| FB | NOT VALID FOR NODAL |
| FTGT | NOT VALID FOR NODAL |
| GI1 | NOT A VALID ANALOG NAME |
| GI2 | NOT A VALID ANALOG NAME |
| GMV | Gross MVAR Measurement |
| GMW | Gross MW Measurement |
| HASL | High Ancillary Service Limit for a Generation Resource |
| HDL | High Dispatch Limit for a Generation Resource |
| HEL | High Emergency Limit for a Generation Resource |
| HSL | High Sustained Limit for a Generation Resource |
| HZ | Frequency Measurement |
| HZ1 | Frequency Measurement |
| JRMW | NOT VALID FOR NODAL |
| KFAC | NOT VALID FOR NODAL |
| KV | Bus kV Measurement |
| LASL | Low Ancillary Service Limit for a Generation Resource |
| LD | NOT VALID FOR NODAL |
| LDL | Low Dispatch Limit for a Generation Resource |
| LEL | Low Emergency Limit for a Generation Resource |
| LM | Limit on Current Measurement |
| LM2 | Limit on Current Measurement |
| LM3 | Limit on Current Measurement |
| LM4 | Limit on Current Measurement |
| LM5 | Limit on Current Measurement |
| LMP | Locational Marginal Price for a Generator Bus |
| LOAD | NOT VALID FOR NODAL |
| LPC | Low Power Consumption for a Load Resource |
| LSL | Low Sustained Limit for a Generation Resource |
| MPC | Maximum Power Consumption for a Load Resource |
| MPH | Wind Generation Resource Speed |
| MVA | Calculated MVA |
| MVAR | MVAR Measurement |
| MVR1 | MVAR Measurement |
| MVR2 | MVAR Measurement |
| MW | MW Measurement |
| MW05 | 5-min average of Load Area Load |
| MW1 | MW Measurement |
| MW15 | NOT VALID FOR NODAL |
| MW2 | MW Measurement |
| MW3 | MW Measurement |
| MW4 | MW Measurement |
| MW60 | 60-min average of Load Area Load |
| MWH | NOT VALID FOR NODAL |
| MWHI | NOT VALID FOR NODAL |
| MWHO | NOT VALID FOR NODAL |
| MWL | NOT VALID FOR NODAL |
| NMRR | Normal Ramp Rate for a Generation Resource |
| NPF | Net Power Flow |
| NSA | NOT VALID FOR NODAL |
| NSD | NOT VALID FOR NODAL |
| NSP | NOT VALID FOR NODAL |
| NSRS | Non-Spin Responsibility for a Generation/Load Resource |
| NSSC | Non-Spin Schedule for a Generation/Load Resource |
| PRES | Wind Generation Resource Temperature |
| QDCO | NOT VALID FOR NODAL |
| QGOV | NOT VALID FOR NODAL |
| QHZ | NOT VALID FOR NODAL |
| QL10 | NOT VALID FOR NODAL |
| QLD | NOT VALID FOR NODAL |
| QPF | NOT VALID FOR NODAL |
| QSCE | NOT VALID FOR NODAL |
| QSEG | NOT VALID FOR NODAL |
| QSEL | NOT VALID FOR NODAL |
| QSES | NOT VALID FOR NODAL |
| RDPF | Regulation Down Participation Factor for a Generation/Controllable Load Resource |
| RDRS | Regulation Down Responsibility for a Generation/Controllable Load Resource |
| REGD | Regulation Down Request for a given QSE |
| REGU | Regulation Up Request for a given QSE |
| REQ | NOT VALID FOR NODAL |
| RR | Responsive Reserve Request for a given QSE |
| RRA | NOT VALID FOR NODAL |
| RRAG | NOT VALID FOR NODAL |
| RRAL | NOT VALID FOR NODAL |
| RRAT | NOT VALID FOR NODAL |
| RRAU | NOT VALID FOR NODAL |
| RRC | NOT VALID FOR NODAL |
| RRRS | Responsive Reserve Responsibility for a Generation/Load Resource |
| RRSC | Responsive Reserve Schedule for a Generation/Load Resource |
| RST | Resource Status for a Generation/Load Resource |
| RUPF | Regulation Up Participation Factor for a Generation/Controllable Load Resource |
| RURS | Regulation Up Responsibility for a Generation/Controllable Load Resource |
| SCBP | SCED Base Point written by RLC |
| SDRM | SCED Down Ramp Rate (calculated by RLC) |
| SPC | Sceheduled Power Consumption for a Load Resource |
| SSId | NOT A VALID ANALOG NAME |
| SURM | SCED Up Ramp Rate (calculated by RLC) |
| TAP | Transformer Tap Position |
| TAPS | Phase Shifter Tap |
| TEMP | Wind Generation Resource Temperature |
| TMP | Temporary Variable |
| UDBP | Updated Desired Base Point for a Generation Resource |
| XMW | Average Load Area Load |

Analog Alarm Category

| Name | Description |
| --- | --- |
| AL | Analog Alarm Category used for Analog Values of type MVA, MW, MVAR for EMS system |
| BB | Analog Alarm Category used for Analog Values of type KV for EMS system |

AnalogLimitName

| Name | Description |
| --- | --- |
| 15MN | Analog Limit Name Associated to a 15MN MVA Limit. Used for EMS system to Identify the Analog Limt as 15 Minute Limit |
| EMGY | Analog Limit Name Associated to a EMGY MVA Limit. Used for EMS system to Identify the Analog Limt as Emergency ( 2 HR) Limit |
| NRML | Analog Limit Name Associated to a NRML MVA Limit. Used for EMS system to Identify the Analog Limt as Normal Limit |
| WARN | Analog Limit Name Associated to a MW Limit . Used for EMS system to identify the Analog Limit as MW limit |

Calculation Trigger Times

| Name | Description |
| --- | --- |
| AA | Timer to Trigger the Calculation every 3600 secs |
| R1 | Timer to Trigger the Calculation every 10 secs |
| X4 | Timer to Trigger the Calculation every 4 secs |
| XX | Timer to Trigger the Calculation every 300 secs |

Conversion Table

| Name | Description |
| --- | --- |
| OAG | Conversion Table to covert ICCP Status Inputs to values , that are readable by SCADA |

Discrete Alarm Categories

| Name | Description |
| --- | --- |
| AL | Alarm Category used on Discrete Values for Capacitors and Reactors . Used by the EMS system |
| AV | Alarm Category used on Discrete Value AVR on Synchronous Machines . Used by the EMS system |
| B1 | Alarm Category used on Discrete Values for any 345kV Devices . Used by the EMS system |
| B2 | Alarm Category used on Discrete Values for any 138kV Devices . Used by the EMS system |
| B3 | Alarm Category used on Discrete Values for any Generators . Used by the EMS system |
| B4 | Alarm Category used on Discrete Values for any 69kV Devices . Used by the EMS system |
| BB | Alarm Category used on OAG Data Links |
| SS | Alarm Category used on Discrete Values for SPSs . Used by the EMS system |

DiscreteNames

| NAME | DESCRIPTION |
| --- | --- |
| ASTS | OAG Link status |
| AVR | Automatic Voltage Regulator status |
| EOCV | Energy Offer Curve Exists flag for a Generation Resource |
| HSUF | High Set Under Frequency Relay status |
| LBST | Lower Block status for a Generation/Controllable Load Resource |
| LRCB | Load Resource Relay CB status |
| NDPL | Non-Spin Deployed flag from MMS for a Generation/Controllable/Non-Controllable Load Resource |
| RBST | Raise Block status for a Generation/Controllable Load Resource |
| RDPL | Responsive Reserve Deployed flag from MMS for a Non-Controllable Load Resource |
| RSTS | OAG Remote status |
| SCM | Synchronous Condenser Mode status (NOT Valid in Nodal) |
| ST | Device status |
| ST2 | Device status (used to distinguish another component device status within a SPS (Special Protection Scheme)) |
| ST3 | Device status (used to distinguish another component device status within a SPS (Special Protection Scheme)) |
| ST4 | Device status (used to distinguish another component device status within a SPS (Special Protection Scheme)) |
| ST5 | Device status (used to distinguish another component device status within a SPS (Special Protection Scheme)) |
| ST6 | Device status (used to distinguish another component device status within a SPS (Special Protection Scheme)) |

Discrete Types

| Name | Description |
| --- | --- |
| OAGS | Discrete Type for OAG link status |
| ON_F | Discrete Type for ON/OFF STATUS MANUAL POINT |
| O_C | Discrete Type defined for a Switch Statuses |

Functions

| NAME | Description |
| --- | --- |
| ADD | Function to Add 2 Analog Values |
| ADD3 | Function to Add 3 Analog Values |
| AVG1 | Average of an Analog Value without considering the Data Quality |
| AVG2 | Function to calculate Average of 2 Analog Values |
| BEST | Function to calculate the Best within 2 Analog Values using the quality code |
| CAV1 | Average of an Analog Value with GOOD data quality |
| DIV | Function to divide 2 Analog Values |
| DYNA | ONLY FOR QSE THAT HAS AT LEAST ONE RESOURCE AND ONE LOAD: ARG1-NUMBER OF OBLIGATION, ARG2-NUMBER OF RESOURCE, ARG3-EACH OBLIGATION ZONE, ARG4-EACH RESOURCE ZONE, ARG5-NEW RESOURCE ZONE - THIS CUST CALC CALCULATIONS NEW RESOURCE ZONES. |
| GE | ARG1 GREATER THAN ARG2 THEN SET ARG3 ELSE RESET ARG3 |
| LAAR | LAAR MW: USES BRKR STATUS AND BREAKER MW TO CALC LAAR MW ARG1: NO. OF BRKRS, ARG2: BREAKER STATUS, ARG3:BREAKER MW, ARG4:LAAR MW |
| MAX | Function calculate the Maximium of 2 Values |
| MULT | Function to multiply 2 Values |
| MVA1 | Function to read MW and MVAR value and calculates MVA value |
| MWHS | SUMMING PART OF MWH |
| NET | NET GEN: USES BRKR STATUS, NET INJECTION, AND GROSS INDIVIDUAL GEN TO CALC NET GEN FOR EACH UNIT IN A PRIV NETW ARG1: NUMBER OF UNITS ARG2: BRKR STATUS FOLLOWED BY GROSS GEN [OPEN-ENDED] |
| OES | Function to Add Multiple Analog Values |
| OESB | Function to Subtract multiple Analog Values |
| OR | Function to do an OR on Discrete Value |
| SUB | Function to Subtract 2 Analog Values |
| TIE | IF A DC TIE MW IS POSITIVE, IT WILL DEPOSIT THE VALUE IN THE GEN ANALOG AND ZERO OUT THE LOAD ANALOG. IF THE DC TIE MW IS NEGATIVE, IT WILL DEPOSIT THE NEGATIVE VALUE IN THE LOAD ANALOG AND 0 GEN MW |

Generation Type

| NAME | Description |
| --- | --- |
| COAL | Coal Plant |
| COGN | Cogeneration Plant |
| FOSS | Fossil Plant |
| GT | Gas Turbine Plant |
| HYDR | Hydro Plant |
| NUCL | Nuclear Plant |
| STM | Steam Plant |
| WIND | Wind Plant |

Limit Alarm Categories

| Name | Description |
| --- | --- |
| T1 | Alarm Category defined for any Normal Limit . This is used by EMS System to identify the type of Alarm |
| T2 | Alarm Category defined for any Emergency Limit . This is used by EMS System to identify the type of Alarm |
| T3 | Alarm Category defined for any 15 Minute Limit . This is used by EMS System to identify the type of Alarm |

MonitoredGroup

| Name | Description |
| --- | --- |
| ISO | Default Monitored Group for Modeling . This field is used by the State Estimator , to group elements based on certain Category. |

PermissionAreas

| Name | Description |
| --- | --- |
| ERCOT | valid area of responsibility for SCADA measurements and its always set to ERCOT. |

Site

| NAME | Description |
| --- | --- |
| DE | Site Defined to identify a calcualtion |
| QSE1 | Link 1 from QSE ICCP Database to EMS System |
| QSE2 | Link 2 from QSE ICCP Database to EMS System |
| QSE3 | Link 3 from QSE ICCP Database to EMS System |
| QSE5 | Link 5 from QSE ICCP Database to EMS System |
| QSE6 | Link 6 from QSE ICCP Database to EMS System |
| QSE7 | Link 7 from QSE ICCP Database to EMS System |
| SI | Intial assignment of the site |
| TSP1 | Link 1 from TSP ICCP Database to EMS System |
| TSP2 | Link 2 from TSP ICCP Database to EMS System |
| TSP3 | Link 3 from TSP ICCP Database to EMS System |
| TSP5 | Link 5 from TSP ICCP Database to EMS System |
| TSP6 | Link 6 from TSP ICCP Database to EMS System |
| TSP7 | Link 7 from TSP ICCP Database to EMS System |

Types

| NAME | Description |
| --- | --- |
| LineCurrent | MeasurementType used for Line Current. This information is used by the EMS System |
| LineToLineVoltage | MeasurementType used for Line To Line Voltage. This information is used by the EMS System |
| NoType | Generic Measurement Type for Instances with No real measurement ( ex: Network Line limits) |
| SwitchPosition | MeasurementType used for Switch Position. This information is used by the EMS System |
| TapPosition | MeasurementType used for Tap Position. This information is used by the EMS System |
| ThreePhaseActivePower | MeasurementType used for MW Value. This information is used by the EMS System |
| ThreePhasePower | MeasurementType used for MVA Value. This information is used by the EMS System |
| ThreePhaseReactivePower | MeasurementType used for MVAR. This information is used by the EMS System |

Units

| NAME | Description |
| --- | --- |
| Amperes | Units for Measurement of type LineCurrent |
| Dummy | Units for Measurement of type Dummy |
| HZ | Units for Measurement on a Frequency Relay |
| MVA | Units for Measurement of type ThreePhasePower |
| MVAr | Units for Measurement of type ThreePhaseReactivePower |
| MW | Units for Measurement of type ThreePhaseActivePower |
| NoUnit | Generic Unit Type for Instances with No measurement ( ex: Network Line limits) |
| PerCent | Units for Measurement on a SynchrocheckRelay |
| SwitchPosition | Units for Measurement of type SwitchPosition ( ON/OFF) |
| TapPosition | Units for Measurement of type TapPosition |
| kV | Units for Measurement of type LinetoLineVoltage |

# Text boxes

SCADA Discrete

SCADA Discrete Value

Terminal

Terminal

Breaker

ICCP

SCADA Discrete Value

VoltageLevel

ShuntCompensator

SeriesCompensator

OwnerShareRating

Line

Terminal

VoltageLevel

GeographicalRegion

Line

VoltageLevel

SubGeographicalRegion

GeographicalRegion

SeriesCompensator

VoltageLevel

GeographicalRegion

SubGeographicalRegion

VoltageLevel

Line

Substation

GeographicalRegion

SysOrphan

SubGeographicalRegion

Bay

VoltageLevel

Substation

MeasurementArgument

MeasurementArgument

Calculation

MeasurementGroup

Substation

MeasurementLocation

CustomerLoad

VoltageLevel

AnalogValue

MeasurementValueQuality

AnalogValue

Analog

Terminal

MeasurementLocation

Customer Load

DiscreteValue

MeasurementValueQuality

DiscreteValue

Discrete

Terminal

Disconnetor

Voltage Level

Substation

AnalogLimit

AnalogLimit

AnalogLimitSet

Analog

Terminal

VoltageLevel

Substation

Terminal

OwnerShareRating

TapChanger

TransformerWinding

PowerTransformer

Transformer Kluge

Customer Load

Voltage Level

Substation

NonConformLoad

VoltageLevel

Substation

ConformLoadGroup

Sub Load Area

Load Area

NonConformLoadGroup

Sub Load Area

Load Area

CurveData

RampRateCurve

Hydro/Nuclear/Thermal/Wind Unit

Resource Controller

Substation

Substation

RampRateCurve

Resource Controller

Hydro/Nuclear/Thermal/Wind Unit

CurveData

RegularTimePoint

ConformLoadSchedule

ConformLoadGroup

SubLoadArea

LoadArea

Terminal

Disconnector

VoltageLevel

Substation

ConnectivityNode

ConnectivityNodeGroup

VoltageLevel

Substation

ElectricalBus

ConnectivityNode

ConnectivityNodeGroup

VoltageLevel

Substation

ConnectivityNodeGroup

VoltageLevel

Substation

OwnerShareRating

BusbarSection

VoltageLevel

Substation

DynamicElement

HUBBus

SettlementHUB

PricingVector

ElectricalBus

ResourceNode

ElectricalBus

SettlementLoadZone

SettlementNOIELoadZone

Terminal

MVArCapabilityCurve

SynchronousMachine

VoltageLevel

SeasonalLimitSet

MeasurementLocation

SeasonalLimitSet

NormalRampRateCurve

EmergencyRampRateCurve

OwnerShareLimits

Hydro/Nuclear/Thermal/WindGenerationUnit

ResourceController

Substation

Hydro/Nuclear/Thermal/Wind Generation Unit

Logical Configuration

TransState

Seasonal Limit Set

Configuration Member

Configuration Member

NormalRampRateCurve

EmergencyRampRateCurve

Configuration

Logical Configuration

PseudoTerminal

MeasurementLocation

CombinedCyclePlant

ResourceController

Hydro/Nuclear/Thermal/Wind Generation Unit

Logical Configuration

Logical Configuration

Logical Configuration

Logical Configuration

Logical Configuration

Pseudo Terminal

Measurement Location

Combined Cycle Plant

Resource Controller

Configuration

Logical Configuration

Pseudo Terminal

Combined Cycle Plant

TransState

Seasonal Limit Set

Configuration Member

Configuration Member

NormalRampRateCurve

EmergencyRampRateCurve

Configuration

Logical Configuration

TransState

Configuration

Configuration Member

Configuration Member

OwnerShareLimit

NormalRampRateCurve

EmergencyRampRateCurve

ControllableLoadResource

Terminal

CustomerLoad

VoltageLevel

Substation

OwnerShareLimit

LoadResource

CustomerLoad

VoltageLevel

Substation

OwnerShareLimits

GeneratingUnit

Contingency

ContingencyElement

ContingencyGroupMember

ContingencyGroup

ProActSwitch

StageTrigger

PrivateProtectiveAction

Stage

PinFlow

PinGate

Gate

TriggerCondition

RemedialActionScheme

VoltageLimit

VoltageLimit

VoltageMonitored