## Slide 1
Review of UFLS Draft NOGRR from UFLS Workshops
Matt Mereness
Director of Compliance
November 17, 2017

## Slide 2: UFLS Discussion outline
Recap of key issues to date on clarifying ERCOT UFLS Program
ERS Proposed changes
Review current draft NOGRR
Appendix
  2016 and 2017 UFLS Survey results
  NERC requirement excerpt
  Potential Load Resource data to provide
  Overarming and ERS questions

## Slide 3: Recap- Summary of UFLS workshops
Key discussions to date
  Problem statement- 2016 OWG issue over OpGuide 2.6.1 on inclusion and exclusion of Load
    “At least 25% of the ERCOT System Load that is not equipped with high-set under-frequency relays shall be equipped at all times with provisions for automatic under-frequency load shedding. The under-frequency relays shall be set to provide Load relief as follows:”… 5%, 10%, 10% of ERCOT System Load
  Recognize there are at least two scenarios of UFLS being activated
    Sudden event: normal day but then significant loss of generation (starting point of 60Hz and no LR deployed)
    Slow-burn event: system is in emergency operations (EEA2), LR deployed, and then loss of generation
    ERCOT conclusion that in both cases, need for 25% of armed UFLS to arrest frequency
  ERCOT view that as frequency drops from 60 to 59.7 to 59.3, that the measurement of 25% response is tied to what the Load was when crossing 59.3 and initiating UFLS levels.
  Agreement that annual Compliance survey measurement should align as closely as possible with expected Operations compliance (post event reports and analysis).
  ERCOT was requested to create initial NOGRR draft reflecting operational expectations
  ERCOT was requested to provide inventory of LRs in DSP footprint
    ERCOT noted this is in network model but can also be provided
  ERCOT asked about providing historical LR trends/deployments
    ERCOT offered to provide annually if market can agree how to summarize (min, max, avg, annual, etc)
  ERCOT asked about providing Load Resource telemetry to TO/DSPs
  ERCOT asked about ERS information for TDSPs to understand location and impacts
  Is DSP or TO the appropriate role/definition for compliance in the NOGRR?

## Slide 4: Action Items from Aug/Sept OWG on ERS
Can ERCOT provide more ERS data for improved transparency?

## Slide 5: Current ERS TDSP Report
Site-level information
  Qsename
  Resource Name
  Esiid, Site name, Street, City, Zip code
  TDSP interconnection agreement year (Generator Only)
  ERS Obligation per time period (YES or leave BLANK)
  ERS Service type
    Weather-Sensitive ERS-10
    Non-Weather-Sensitive ERS-10
    Weather-Sensitive ERS-30
    Non-Weather-Sensitive ERS-30
  Resource type (Load or Generator)
Notes: Site level information

## Slide 6: Proposed Additional Tab(s) to current TDSP Report per OWG’s discussion
Additional tab(s)
  To TDSP’s in competitive areas
    Report Aggregated ERS MW Obligation by station code
      By the following ERS resource types: Weather-Sensitive Load, Non-Weather-Sensitive Load, Generator
  To NOIEs
    Report Aggregated ERS MW Obligation by zip code
      By the following ERS resource types: Weather-Sensitive Load, Non-Weather-Sensitive Load, Generator
  NPRR will be required to include the additional information as part of ERS routine reporting process.
    ERCOT recommends replacing current report with report proposed herein
Notes: Site level information

## Slide 7: Proposed Additional Tab(s) per OWG’s discussion
ERS Obligation by Station code and/or Zip code
  TDSP Name
  ERS resource type
  Station Code/Zip code
  ERS_MW_TP1…. ERS_MW_TP6
  Aggregated ERS obligation for each time period (MW)
Notes: Site level information

## Slide 8: Proposed ERS TDSP Report
Methodology
Step 1 Disaggregation
Step 2 Aggregation
Load
Generator
The assigned portion of an ERS Generator obligation will be based on each generator’s name plate rating
Assign an equal portion of an ERS Resources Obligation to each site in the resource
Sum the assigned portion to each site by station code (if in competitive area), zip code (if in NOIE area) as well as service type (NON-WS Load, WS Load and Generator)
NON-WS LOAD
WS LOAD
GENERATOR
Step 3 By Time Period
Perform Step 1 & 2 for each ERS Time Period

## Slide 9: Review current NOGRR version
Summary of changes
  Purposeful in separating (1) and (2) between actual event and survey
    In actual event, compliance with system Load measured at 59.3 Hz (2.6.1(1)).
    In annual survey, compliance with system Load at survey time (2.6.1(2)).
  ERCOT agreeable to allowing totals to roll into next tier
    Moved STEC’s language on deployment amounts into survey section (2).
    Inserted ability for ERCOT to request redistribution if any reliability issues identified in survey
  NOGRR adds ERCOT requirement to annually provide registered Load Resources and capacity in TO/DSP footprint
  Question of proper alignment of DSP and TO responsibilities
  Does not currently include 2 concepts discussed in workshops
      Provision of trends of Load Resource status in TO/DSP footprint (eg, min, max, avg responsibility) – could be added with no project impacts to add
      Provision of telemetry of LR status to TO/DSP – project impacts
      NPRR would be needed for ERS reporting changes discussed today

## Slide 10
APPENDIX:
2016 and 2017 UFLS Survey results
NERC requirement excerpt
Potential Load Resource data to provide
Overarming and ERS questions

## Slide 11: Appendix- 2016 & 2017 UFLS Survey Results
ERCOT Compliance coordinates and conducts an annual survey with the TSPs and DSPs to ensure that the required automatic under-frequency load shed circuits are configured to provide the appropriate load relief in an under-frequency event as required by table below from Operating Guides 2.6.1(1) Requirements for Under-Frequency Load Shedding:
2016 results were 7.2% / 12.2% / 12.6% for total of 31.9%
2017 results were 7.8% / 13.2% / 13.2% for total of 34.1%

## Slide 12: Appendix- NERC Requirement
NERC standard PRC-006-2 — Automatic Underfrequency Load Shedding:
Requirement 3. Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s).
Requirement 9. Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. [VRF: High][Time Horizon: Long-term Planning]
Measurement 9. Each UFLS Entity shall have dated evidence such as spreadsheets summarizing feeder load armed with UFLS relays, spreadsheets with UFLS relay settings, or other dated documentation that it provided automatic tripping of load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, per Requirement R9.

## Slide 13: Appendix- Potential Load Resource data to be provided
TDSP shown on Registration Form
  TDSP Duns
From the Load Resource Asset Registration Form
  Dispatch Asset Code
  ESIID (Load Resources for NOIEs will have a non-settlement ESIID)
  Station the Load Resource is mapped to in the Network Operations Model
  PTI Number
  Transmission Transformer Load Name
  Maximum Registered Interruptible Load
Historical Data (more analysis needed)
  Average hourly RRS Responsibility for LR during a predefined date range
  Maximum RRS Responsibility during the same time period

## Slide 14: Overarming and ERS (Responses from Sept OWG)
Is there any risk of overarming and overshooting on UFLS?
  ERCOT does perform planning studies that include dynamic simulations using DWG model that includes equipped UFLS circuits and Load Resources.
  The dynamic study is performed on different models, including High Wind, Low-Load and to date ERCOT has not observed any over-shoot issues related to this study.
  Current ERCOT surveys do reflect a certain amount of overshoot at the different levels (2-3%), and with the current proposed changes allowing movement across tiers, the overshoot may be reduced overall.
Has ERCOT studied the impacts of ERS deployments?
  ERCOT has not studied ERS deployments in current dynamic models
    Current ERS procurement is approximately 800MW
    When compared to the current excess 2-3% UFLS capacity at each tier this is not a significant number
      For 30,000MW load, 600-900MW per tier represent the 2-3% at each tier