| RRGRR Number | 016 | RRGRR Title | Additional Guidance for Solar Data |
| --- | --- | --- | --- |
| Date Posted |  | December XX, 2017 |  |
| Requested Resolution |  | Normal |  |
| Resource Registration Glossary Sections Requiring Revision |  | Section 2, Resource Registration Glossary |  |
| Related Documents Requiring Revision/Related Revision Requests |  | None |  |
| Revision Description |  | This Resource Registration Glossary Revision Request (RRGRR) clarifies Glossary definitions and detailed descriptions of data fields in order to provide more direction to Market Participants for the successful submission of their Resource Asset Registration Forms (RARFs). |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  |  |  |

| Sponsor |  |
| --- | --- |
| Name | John Palen on behalf of the Resource Data Working Group (RDWG) |
| E-mail Address | John.Palen@nrg.com |
| Company | NRG Energy Inc. |
| Phone Number | 713-537-3706 |
| Cell Number | 713-545-3415 |
| Market Segment | Not Applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brittney Albracht |
| E-mail Address | Brittney.Albracht@ercot.com |
| Phone Number | 512-225-7027 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None |  |

Market Rules Notes

None

Proposed Guide Language Revision

| SECTION 2: RESOURCE REGISTRATION GLOSSARY – Effective July 1, 2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| RARF Tab | Wind | Solar Photovoltaic (PV) | Conventional Generation (Gen) | Combined Cycle (CC) | Load Resources | Distributed Generation | Notes | Field Name | Definition / Detailed Description | Screening Study (SS) (R, C, O, A) | Full Interconnect Study (FIS) (R, C, O, A) | Planning Model (R, C, O, A) | Full Registration (R, C, O, A) | Effective Date |
| Panel Details |  | X |  |  |  |  | All Caps | Site Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  |  | A |  |
| Panel Details |  | X |  |  |  |  | List | Panel Configuration Identifier | Unique name of a given Panel Model used more than once |  |  |  | R |  |
| Panel Details |  | X |  |  |  |  | List | Tracking Type | What type of tracking system does this plant use? (None, Azimuth only, Tilt only, Azimuth and Tilt) (Single AxisTilt Tracking Only, Azimuth Tracking Only, Double Axis, Fixed/None) |  |  |  | R |  |
| Panel Details |  | X |  |  |  |  | degrees | Plane of Array - Azimuth | For a Tracking Type of Fixed/None, or Single Axis – For panels with a non-zero tilt, enter the degrees of rotation of the panel face using true north as a reference, 180 degrees means that the panel is facing south. Tracking Type Single Axis – Enter the degrees of rotation of the axis from north-south: North-South=0, East-West=90, all others are between 0 and 90). For panels with a fixed tilt of zero degrees, As a default, enter “0” (zero) degrees if panel is facing directly up (vertical). For a Tracking Type of Double axis – enter “0” (zero). Tracking Type of Fixed/None or Tilt Tracking Only - Enter the orientation of the panel in degrees, using true north (0 degrees), as a reference point. Tracking type of Azimuth Tracking Only, or Double Axis - Enter the maximum potential range of Azimuth trancking in degrees, using true north (0 degrees) as the starting point. For example, if the panel is capable of reaching due West, enter 270. if the panel is capable of a complete arc, enter 360. |  |  |  | R |  |
| anel Details |  | X |  |  |  |  | degrees | Plane of Array - Tilt | Used for Solar Generation Forecasting (Tracking Type =Fixed or Azimuth-only) Tracking type of Fixed/None or Single Axis - Enter the angle in degrees of the panel face from horizontal. Tracking Type of Double Axis - Enter "0" (zero). For tracking type of Single Axis and Double Axis – The maximum tilt possible during tracking, in degrees of the panel face from horizontal (e.g., 90 means the panel is capable of standing up vertically) For Tracking Type Fixed/None or Azimuth Tracking Only - Enter the degrees of tilt, using horizontal (0 degrees) as a reference. For Tracking Type Tilt Tacking Only, or Double Axis - Enter the maximum possible tilt, using horizontal (0 degrees), as a reference. |  |  |  | R |  |
| Panel Details |  | X |  |  |  |  | All Caps | Panel Manufacturer | From name-plate or manufacturer data sheet |  |  |  | R |  |
| Panel Details |  | X |  |  |  |  | All Caps | Panel Model | From name-plate or manufacturer data sheet |  |  |  | R |  |
| Panel Details |  | X |  |  |  |  | meters squared | Panel Area | From name-plate or manufacturer data sheet |  |  |  | R |  |
| Panel Details |  | X |  |  |  |  | % | Panel Efficiency | From name-plate or manufacturer data sheet |  |  |  | R |  |
| Panel Details |  | X |  |  |  |  | % / degrees C | Panel temperature Coefficient of power | From name-plate or manufacturer data sheet |  |  |  | R |  |
| Panel Details |  | X |  |  |  |  | Degrees C | Nominal Operating Cell Temperature | From name-plate or manufacturer data sheet |  |  |  | R |  |
| Panel Details |  | X |  |  |  |  | MW kW | MW kW Rating for this Model of Panel | From name-plate or manufacturer data sheet |  | R |  | R |  |