## Slide 1: Transformer Reactive Power Losses Due to GIC

## Slide 2
Transformer Saturation and Reactive Power Losses
The DC offset can cause transformer saturation which links to dramatic increase in the transformer excitation current.
Excitation current lags system voltage by 90 degree and therefore associated with reactive power losses

## Slide 3
Transformer Core Types

## Slide 4
5-Lagged Core
Transformer Core Types
7-Lagged Shell

## Slide 5
 | Default K Factor Values | 
 | PSSE | Powerworld
Three Phase Shell | 0.33 | 0.80
Three Phase Core | N/A | 0.50
Single Phase (Three separate cores) | 1.18 | 1.70
Three Phase, 3-legged , Core | 0.29 | 0.80
Three Phase, 5-legged , Core | 0.66 | 0.80
Three Phase, 7-legged , Core | 0.66 | 0.80
Unknown core, <=200kV | 0.60 | 0.80
Unknown core, >200kV and <= 400kV | 0.60 | 0.80
Unknown core, >400kV | 1.10 | 1.70
Default K Factor Values

## Slide 6
Linear or Multi-Segment

## Slide 7
ABB’s Assessment Model

## Slide 8
ABB’s Assessment Model
333 MVA, 500 / 230 kV, Single phase Transformer

## Slide 9
Approaches for Obtaining k Factor Values
Default values
Request from manufactures
Transformer modeling and simulation (using topologically correct core model)