## Slide 1
Freeport Area Master Plan Project -
ERCOT Independent Review
TAC
November 30, 2017

## Slide 2: Background
CenterPoint Energy submitted the Freeport Master Plan RPG Project to solve identified reliability criteria violations due to new committed industrial loads in the Freeport area
$246.7 Million
Tier 1 project
ERCOT studied 2019, 2020, and 2022 cases and found multiple reliability criteria violations in 2020 and 2022
  No reliability criteria violations found for 2019

## Slide 3: 2020 Needs - Bridge The Gap Upgrades
To resolve the base case violations CNP’s ‘Bridge The Gap Upgrades’ are recommended.
The list of these upgrades include ->
  Loop 345 kV South Texas Project (STP) – Dow-Velasco circuit 27 into the Jones Creek Substation (approximately 0.9 mile)
  Install 7-ohm in-line reactors at the Jones Creek Substation on 345 kV STP – Jones Creek circuits 18 and 27
  Install 3rd 345/138 kV 800/1000 MVA Autotransformer at the Jones Creek Substation
  Install 4th 138 kV Capacitor Bank (120 MVAr) at Jones Creek Substation
  Install 1st 138 kV Automatically Switchable Capacitor Bank (140 MVAr) at Jones Creek Substation
  Install 2nd 138 kV Automatically Switchable Capacitor Bank (140 MVAr) at Jones Creek Substation
Total cost estimate for all these upgrades is $32.3M.

## Slide 4: 2022 Needs – Project Options
Reliability criteria violations in 2022 after the CNP’s ‘Bridge The Gap Upgrades’:
  NERC P3 (G-1+N-1)
  Maintenance Outage conditions (N-1-1)
Project Options considered:
  Four options - each with new 345 kV line (on new ROW)
  One option included existing 345 kV system upgrades
Project Options evaluation:
  Steady State and Dynamic Stability
  Voltage Stability Transfer limit
  Extreme Event contingency limitations
  High Load Sensitivity with 657 MW (uncommitted load) added to the Freeport Area

## Slide 5: 2022 Project Options – Summary of Results
Option # | Option 1 | Option 2 | Option 3 | Option 4 | Option 5
Description | STP-JC | HILLJE-JC | BAILEY-JC | PHR-JC | Only line upgrades
Extreme Event Contingency Limitation | Yes | No | No | Yes | Yes
Voltage Stability Transfer Limit (MW) | 2240 | 2160 | 2080 | 1560 | 360
Dynamic Stability Criteria Violations? | Not studied | No | No | Not studied | Not studied
Projected Load for 2022 Criteria Violations? | No | No | No | No | No
Projected Load for 2022 + High Load Sensitivity | None | P6 | P3/P6 | Not studied | Not studied
New ROW Distance (miles) | 50.4 | 62.4 | 48 | 60 | 0
Estimated Cost (Million) | $223.2 | $272.5 | $214.4 | $220.0 | $281.8

## Slide 6: Final Recommendation - Description
‘Bridge the Gap Upgrades’ are required to meet the near-term reliability needs, have a cost estimate: $32,340,000 and are described as follows:
  Loop 345 kV South Texas Project (STP) – Dow-Velasco circuit 27 into the Jones Creek Substation (approximately 0.9 mile)
  Install 7-ohm in-line reactors at the Jones Creek Substation on 345 kV STP – Jones Creek circuits 18 and 27
  Install 3rd 345/138 kV 800/1000 MVA Autotransformer at the Jones Creek Substation
  Install 4th 138 kV Capacitor Bank (120 MVAr) at Jones Creek Substation
  Install 1st 138 kV Automatically Switchable Capacitor Bank (140 MVAr) at Jones Creek Substation
  Install 2nd 138 kV Automatically Switchable Capacitor Bank (140 MVAr) at Jones Creek Substation
Option 3 meets the long-term reliability criteria needs in the most cost effective manner. Option 3 has a cost estimate of $214,400,000 and is described as follows:
  Construct a new approximately 48 mile 345 kV double circuit transmission line from Bailey Substation to Jones Creek Substation (2988 MVA emergency rating)
  Upgrade 345 kV Dow-Velasco to Jones Creek circuits 18 and 27 which is approximately 3 miles (minimum 1700 MVA emergency rating)

## Slide 7: Conclusion
The estimated capital cost of the recommended upgrades is $246.7 million. Based on this estimate the project is classified as a Tier 1 project per Protocol Section 3.11.4.7.
Pursuant to Protocol Section 3.11.4.9(2) ERCOT will present the project to the Board for endorsement.
ERCOT requests that TAC recommends the Board endorse the project.
Questions?

## Slide 8: Appendix: Past RPG Presentations on Freeport Master Plan Project
  ERCOT presented the study scope in June 2017 RPG
    http://www.ercot.com/content/wcm/key_documents_lists/108872/CNP_Freeport_Masterplan_Study_Scope_-_RPG.pdf
  ERCOT presented a status update during August 2017 RPG http://www.ercot.com/calendar/2017/8/22/108879-RPG
  ERCOT presented last status updates during October 2017 RPG http://www.ercot.com/content/wcm/key_documents_lists/108888/CNPFP_EIR_StatusUpdate_RPG_10192017.pdf
  ERCOT presented final update to RPG during November 2017 RPG http://www.ercot.com/content/wcm/key_documents_lists/108892/CNP_Freeport_Master_RPG_11_04_2017_.pdf