## Slide 1
Transmission Loss Factors
December 4, 2017
CMWG

## Slide 2: INTRODUCTION
Late 2016: 2017 Transmission Loss Factors (TLFs) Posted for period from March 1, 2017 – February 28, 2018
March 2017: New tag created to track actual TLF so comparison data exists for April-August
  TLFs changed significantly prompting questions from market participants
2016/17 TLFs |  | 
Season | SONLF | SOFFLF
Spring | 2.0925% | 1.7968%
Summer | 1.9901% | 1.4773%
Fall | 1.8153% | 1.5960%
Winter | 2.3877% | 1.7965%
2016/17 TLFs |  | 
Season | SONLF | SOFFLF
Spring | 2.1639% | 1.9870%
Summer | 2.0514% | 1.8735%
Fall | 2.3955% | 2.5085%
Winter | 2.3522% | 2.4581%

## Slide 3: CURRENT TLF PROCEDURES
Transmission Loss Factors (TLFs) are posted for each season annually
Actual transmission losses not directly accounted for in settlement, ERCOT uses Deemed Actual TLFs
Procedures for developing TLFs relatively unchanged since Zonal market open in 2001
Relevant Documentation
Protocols Section 13 prescribes the method to develop forecasted Transmission Loss Factors (TLFs) and their use in settlement
Generator dispatch for each of the eight cases is determined pursuant to Section 4.3.3 of the SSWG Procedure Manual*
*http://www.ercot.com/content/wcm/key_documents_lists/27292/SSWG_Procedure_Manual.Approved_by_ROS_20160203.docx

## Slide 4: TRANSMISSION LOSSES AND UFE
Net Generation for Settlement Interval
Profiled Energy Usage Non-Metered Accounts
Interval Data Energy Usage
Losses (Transmission and Distribution)
UFE
Unaccounted for Energy (UFE) = Generation – (Load + Losses)
GAP
Sources of UFE include:
Generation Measurement Errors
DC Tie Inadvertent Energy
Load
  Missing/Erroneous Usage Data
  Backcast Profile Error
  Load Profile ID Assignment Error
  Theft
Losses - Model Error
  Loss Calculation Error
  Loss Code Assignment Error

## Slide 5: HISTORICAL UFE VALUES
 | MWH | COST | % of LOAD | AVG PRICE
2003 | 1,672,727 | $156,733,428 | 0.40% | $41.31
2004 | 1,344,289 | $102,693,690 | 0.40% | $42.00
2005 | 1,082,561 | $174,154,088 | 0.30% | $65.91
2006 | 2,304,458 | $187,975,534 | 0.70% | $51.26
2007 | 2,914,297 | $206,949,832 | 0.90% | $52.77
2008 | 1,541,086 | $134,692,211 | 0.40% | $68.04
2009 | 1,351,187 | $44,857,873 | 0.40% | $30.89
2010 | 1,756,344 | $85,406,714 | 0.55% | $35.74
2011 | 1,453,256 | $31,666,952 | 0.43% | $43.30
2012 | 1,002,761 | $25,945,816 | 0.31% | $26.60
2013 | -395,393 | -$17,061,127 | -0.12% | $31.71
2014 | 298,578 | $2,286,431 | 0.09% | $38.02
2015 | 240,091 | $1,441,929 | 0.07% | $24.80
2016 | 644,293 | $11,037,155 | 0.18% | $22.60

## Slide 6: ACTUAL AND DEEMED ACTUAL TLF
Deemed Actual TLF
Forecasted TLFs determined based on seasonal SSWG cases
  On-peak case for each season
  Off-peak case is the minimum load on the same day as season on-peak case
  Linear approximation for each season
True-up SSWG linear transmission loss function to ERCOT operational load for settlement
Actual TLF
Measured based on an EMS calculation of the losses on all TSP owned equipment
If Actual transmission losses are greater (less) than the Deemed Actual, the difference will contribute to an increase (decrease) in Unaccounted for Energy (UFE)

## Slide 7: EFFECT OF DC TIE FLOW VARIANCE FROM SCHEDULE
Large differences between scheduled and actual DC tie flow strongly impact UFE, so
for this analysis any interval with a difference greater than 10 is discarded
Chart: 3 June 2017
Interchange (MW)
UFE (MWh)
Hour Ending
The high difference between scheduled and actual DC tie flow was due to East DC-Tie testing
Notes: 2663 settlement intervals (15min intervals) thrown out with DC tie cut-off

## Slide 8: CORRELATION OF TL DIFFERENCE AND UFE
Month | Correlation with UFE
April | 0.80
May | 0.81
June | 0.70
July | 0.55
Aug | 0.39
Overall | 0.68
Overall there is a moderately strong correlation between Transmission Loss Difference and UFE, with a strong correlation for Spring
A correlation between TL Difference and UFE is expected in the absence of other large drivers of UFE
UFE and Transmission Losses are allocated differently to market participants

## Slide 9: DIFFERENCES IN ACTUAL AND DEEMED ACTUAL TL
Chart: TL Difference
Transmission Loss (TL) Difference = Measured Actual TL – Deemed Actual TL
(April – August)
Average Load: 44,941 MW
Average Actual Losses: 962 MW