| NPRR Number | 849 | NPRR Title | Clarification of the Range of Voltage Set Points at a Generation Resource’s POI |
| --- | --- | --- | --- |
| Date |  | December 4, 2017 |  |
| Submitter’s Information |  |  |  |
| Name |  | Stephen Solis |  |
| E-mail Address |  | Stephen.solis@ercot.com |  |
| Company |  | ERCOT |  |
| Phone Number |  | 512-248-6772 |  |
| Cell Number |  | 512-426-4721 |  |
| Market Segment |  | Not applicable |  |

Comments

ERCOT is submitting these comments in response to the 10/5/17 NRG comments, in addition to incorporating some feedback provided by Market Participants at the 11/14/17 Voltage Profile Working Group (VPWG) meeting and the 11/17/17 Operations Working Group (OWG) meeting.

ERCOT maintains that the range of potential Voltage Set Points within which the 0.95 leading and lagging capability at the Point of Interconnection (POI) must be provided should be wider than the range proposed by NRG.  Voltage Set Points have historically been provided by the seasonal Voltage Profile process and instructed in Real-Time between the 0.98 and 1.04 per unit range.  This represents an operational range where dynamic reactive capability provided by Generation Resources required to provide Voltage Support Service (VSS) ensures the necessary reliability function by maintaining system voltages in response to system disturbances.

While ERCOT understands NRG’s comments on factors that impact reactive capability between a generator’s terminals and the POI, the Protocols have always required generators to meet their VSS obligations at the POI to ensure the transfer of real power and response to system disturbances.  While grid voltages and reactive power flows do alter the voltages at the POI, Generation Resources are only required to maintain the Voltage Set Point to the extent that doing so does not cause the Resource to exceed its Unit Reactive Limit (URL), except where ERCOT has issued a Verbal Dispatch Instruction to exceed the URL, in which case the Resource is obligated to maintain the Voltage Set Point only to the extent the Resource is physically capable of doing so.  If a Generation Resource has exhausted its Reactive Power capability in attempting to maintain the Voltage Set Point (+/- 2% with its Automatic Voltage Regulator (AVR) in service and in voltage control mode), ERCOT or the Transmission Operator (TO) should be utilizing static reactive devices on the transmission system to restore the Generation Resource dynamic Reactive Power capability in accordance with paragraph (1)(b)(4) of Operating Guide Section 2.7.2, Maintaining Voltage Profiles, paragraph (1)(i) of Operating Guide Section 2.7.3.1, Operational Guidelines, and paragraph (3) of Operating Guide Section 2.7.3.3, TO/TSP Responsibilities.

NRG cites to a NERC white paper which states that “a generator should not be required to provide full reactive power consumption when low voltage conditions are occurring at the POI.” However, the white paper also recognizes that such a requirement would be appropriate when “the Transmission Provider has established different requirements that apply to all similarly situated generators in the control area on a comparable basis.”  Additionally, a Voltage Set Point instruction at 0.98 per unit does not constitute a “low voltage condition,” as that term is used in the white paper, and a Voltage Set Point instruction at 1.04 does not constitute a “high voltage condition.”  Rather, these are the normal operating voltages and within voltage limits where dynamic Reactive Power capability would be utilized to respond to disturbances.  Finally, while the white paper may provide a technical basis for understanding fundamentals related to the topic, it does not set any precedent or ruling that is applicable to the ERCOT Region.

NRG also questions whether it is realistic to assume that Voltage Set Points would be instructed at 0.98 or at 1.04 per unit.  There are operational conditions where Voltage Set Points are set such that post-contingency system voltages will remain within emergency system voltage limits (determined by the TOs, but typically 0.9 and 1.1 per unit).  During heavily loaded conditions where perhaps there are limited dynamic reactive Resources in an area, it may be desirable to have pre-contingency voltages near the normal high limits to allow for the post-contingency voltage drop to remain above the emergency low limits, where actions can then be taken post- contingency to utilize additional static reactive devices to recover voltages within normal limits and relieve reactive loading on the dynamic reactive Resources after the disturbance has occurred.  Additionally this operational practice of setting pre-contingency voltages high or near the normal high limits can allow additional transfer capability by boosting voltages and flattening out the “knee” of the curve for Generic Transmission Limits (GTLs) based on voltage stability import limits.

Conversely, during lightly loaded conditions, high voltages may be an issue where setting pre-contingency Voltage Set Points lower than nominal but within limits (e.g., 0.98 per unit) allows post-contingency voltages to remain within emergency limits (e.g., 1.1 per unit).  Once again, if a Generation Resource is instructed to maintain a 0.98 per unit Voltage Set Point (+/- 2%) and has exhausted all of its required Reactive Power capability in attempting to maintain the Voltage Set Point, ERCOT and the TOs have requirements to utilize static reactive resources (e.g. reactors in this example) to preserve the dynamic reactive capability.

These examples are real scenarios that ERCOT and the TOs encounter in attempting maintain voltages within pre- and post-contingency system voltage limits.  ERCOT has recognized that it would be rare to instruct Voltage Set Points outside of voltages between 0.98 and 1.04 per unit and is seeking to clarify the current requirement to provide 0.95 leading and lagging at any potential POI Voltage Set Point—including any Voltage Set Point between 0.95 and 1.05.  Contrary to some comments raised at OWG, this NPRR actually narrows the Generation Resource’s responsibility compared to the current Protocol language.  ERCOT also believes it may introduce confusion to utilize “proportional” language recommended by NRG.  ERCOT prefers identifying clear and discrete ranges and has proposed the same ranges but has modified “voltages” to “Voltage Set Points” as suggested at VPWG.

Finally, ERCOT agrees with NRG’s comments on paragraph (3)(e) of Section 3.15, and has revised this language in an attempt to clarify and simplify (3)(e) to convey the intent that each Generation Resource still has an obligation to provide what Reactive Power capability it has when instructed outside of the Voltage Set Point ranges identified in (3)(a) and (3)(b), albeit at potentially less than 0.95 power factor. ERCOT has, at this time, chosen not to cross-reference other provisions that prohibit removing high reactive loading during abnormal conditions without permission (e.g., paragraph (11) of Section 3.15) and voltage ride-through requirements (e.g., paragraph (2) of Section 3.15.3, Generation Resource Requirements Related to Voltage Support) as this would be duplicative.  The possibility of doing so was discussed at VPWG.

OWG had also discussed the potential addition of including “be designed to” in the beginning of paragraph (3) of Section 3.15 (e.g. “…VSS shall be designed to comply…”). However, ERCOT believes this is already implied because it is reasonable to presume that a Generation Resource has been designed to comply with the requirements if it is capable of operating in compliance with the requirements, and because it is the Generation Resource’s operation, and not necessarily its design, that is ERCOT’s primary concern.  ERCOT declines to suggest that additional language on this basis.

Revised Cover Page Language

None

Revised Proposed Protocol Language

- 3.15	Voltage Support

(1)	ERCOT, in coordination with the Transmission Service Providers (TSPs), shall establish and update, as necessary, the ERCOT System Voltage Profile and shall post it on the Market Information System (MIS) Secure Area.  ERCOT, the interconnecting TSP, or that TSP’s agent, may modify the Voltage Set Point described in the Voltage Profile based on current system conditions.

(2)	All Generation Resources (including self-serve generating units) that have a gross generating unit rating greater than 20 MVA or those units connected at the same Point of Interconnection (POI) that have gross generating unit ratings aggregating to greater than 20 MVA, that supply power to the ERCOT Transmission Grid, shall provide Voltage Support Service (VSS).

(3)	Each Generation Resource required to provide VSS shall comply with the following Reactive Power Requirements:

(a)	An over-excited (lagging or producing) power factor capability of 0.95 or less determined at the generating unit's maximum net power to be supplied to the ERCOT Transmission Grid and at any Voltage Set Point from 0.95 per unit to 1.04 per unit, as measured at the POI;

(b)	An under-excited (leading or absorbing) power factor capability of 0.95 or less, determined at the generating unit's maximum net power to be supplied to the ERCOT Transmission Grid and at any Voltage Set Point from 0.98 per unit to 1.05 per unit, as measured at the POI;

(c)	Reactive Power capability shall be available at all MW output levels and may be met through a combination of the Generation Resource’s Unit Reactive Limit (URL), which is the generating unit’s dynamic leading and lagging operating capability, and/or dynamic VAr capable devices.  This Reactive Power profile is depicted graphically as a rectangle.  For Intermittent Renewable Resources (IRRs), the Reactive Power requirements shall be available at all MW output levels at or above 10% of the IRR’s nameplate capacity.  When an IRR is operating below 10% of its nameplate capacity and is unable to support voltage at the POI, ERCOT may require an IRR to disconnect from the ERCOT System for purposes of maintaining reliability;

(d)	As part of the technical Resource testing requirements prior to the Resource Commissioning Date, all Generation Resources must conduct an engineering study, or demonstrate through performance testing, compliance with the Reactive Power capability requirements of this section.  Any study or testing results must be accepted by ERCOT prior to the Resource Commissioning Date; and

(e)  	Notwithstanding paragraphs (a) and (b) above, the Generation Resource shall provide any available Reactive Power capability to comply with any instructed Voltage Set Points outside of the ranges identified in paragraphs (a) and (b) above.

(4)	Wind-powered Generation Resources (WGRs) that commenced operation on or after February 17, 2004, and have a signed Standard Generation Interconnection Agreement (SGIA) on or before December 1, 2009 (“Existing Non-Exempt WGRs”), must be capable of producing a defined quantity of Reactive Power to maintain a set point in the Voltage Profile established by ERCOT in accordance with the Reactive Power requirements established in paragraph (3) above, except in the circumstances described in paragraph (a) below.

(a)	Existing Non-Exempt WGRs whose current design does not allow them to meet the Reactive Power requirements established in paragraph (3) above must conduct an engineering study using the Summer/Fall 2010 on-peak/off-peak Voltage Profiles, or conduct performance testing to determine their actual Reactive Power capability.  Any study or testing results must be accepted by ERCOT.  The Reactive Power requirements applicable to these Existing Non-Exempt WGRs will be the greater of: the leading and lagging Reactive Power capabilities established by the Existing Non-Exempt WGR’s engineering study or testing results; or Reactive Power proportional to the real power output of the Existing Non-Exempt WGR (this Reactive Power profile is depicted graphically as a triangle) sufficient to provide an over-excited (lagging) power factor capability of 0.95 or less and an under-excited (leading) power factor capability of 0.95 or less, both determined at the WGR’s set point in the Voltage Profile established by ERCOT, and both measured at the POI.

(i)	Existing Non-Exempt WGRs shall submit the engineering study results or testing results to ERCOT no later than five Business Days after its completion.

(ii)	Existing Non-Exempt WGRs shall update any and all Resource Registration data regarding their Reactive Power capability documented by the engineering study results or testing results.

(iii)	If the Existing Non-Exempt WGR’s engineering study results or testing results indicate that the WGR is not able to provide Reactive Power capability that meets the triangle profile described in paragraph (4)(a) above, then the Existing Non-Exempt WGR will take steps necessary to meet that Reactive Power requirement depicted graphically as a triangle by a date mutually agreed upon by the Existing Non-Exempt WGR and ERCOT.  The Existing Non-Exempt WGR may meet the Reactive Power requirement through a combination of the WGR’s URL and/or automatically switchable static VAr capable devices and/or dynamic VAr capable devices.  No later than five Business Days after completion of the steps to meet that Reactive Power requirement, the Existing Non-Exempt WGR will update any and all Resource Registration data regarding its Reactive Power and provide written notice to ERCOT that it has completed the steps necessary to meet its Reactive Power requirement.

(iv)	For purposes of measuring future compliance with Reactive Power requirements for Existing Non-Exempt WGRs, results from performance testing or the Summer/Fall 2010 on-peak/off-peak Voltage Profiles utilized in the Existing Non-Exempt WGR’s engineering study shall be the basis for measuring compliance, even if the Voltage Profiles provided to the Existing Non-Exempt WGR are revised for other purposes.

(b)	Existing Non-Exempt WGRs whose current design allows them to meet the Reactive Power requirements established in paragraph (3) above (depicted graphically as a rectangle) shall continue to comply with that requirement.  ERCOT, with cause, may request that these Existing Non-Exempt WGRs provide further evidence, including an engineering study, or performance testing, to confirm accuracy of Resource Registration data supporting their Reactive Power capability.

(5)	Qualified Renewable Generation Resources (as described in Section 14, State of Texas Renewable Energy Credit Trading Program) in operation before February 17, 2004, required to provide VSS and all other Generation Resources required to provide VSS that were in operation prior to September 1, 1999, whose current design does not allow them to meet the Reactive Power requirements established in paragraph (3) above, will be required to maintain a Reactive Power requirement as defined by the Generation Resource’s URL that was submitted to ERCOT and established per the criteria in the ERCOT Operating Guides.

(6)	New generating units connected before May 17, 2005, whose owners demonstrate to ERCOT’s satisfaction that design and/or equipment procurement decisions were made prior to February 17, 2004, based upon previous standards, whose design does not allow them to meet the Reactive Power requirements established in paragraph (3) above, will be required to maintain a Reactive Power requirement as defined by the Generation Resource’s URL that was submitted to ERCOT and established per the criteria in the Operating Guides.

(7)	For purposes of meeting the Reactive Power requirements in paragraphs (3) through (6) above, multiple generation units including IRRs shall, at a Generation Entity’s option, be treated as a single Generation Resource if the units are connected to the same transmission bus.

(8)	Generation Entities may submit to ERCOT specific proposals to meet the Reactive Power requirements established in paragraph (3) above by employing a combination of the URL and added VAr capability, provided that the added VAr capability shall be automatically switchable static and/or dynamic VAr devices.  A Generation Resource and TSP may enter into an agreement in which the proposed static VAr devices can be switchable using Supervisory Control and Data Acquisition (SCADA).  ERCOT may, at its sole discretion, either approve or deny a specific proposal, provided that in either case, ERCOT shall provide the submitter an explanation of its decision.

(9)	A Generation Resource and TSP may enter into an agreement in which the Generation Resource compensates the TSP to provide VSS to meet the Reactive Power requirements of paragraph (3) above in part or in whole.  The TSP shall certify to ERCOT that the agreement complies with the Reactive Power requirements of paragraph (3).

(10)	Unless specifically approved by ERCOT, no unit equipment replacement or modification at a Generation Resource shall reduce the capability of the unit below the Reactive Power requirements that applied prior to the replacement or modification.

(11)	Generation Resources shall not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT unless equipment damage is imminent.

(12)	All WGRs must provide a Real-Time SCADA point that communicates to ERCOT the number of wind turbines that are available for real power and/or Reactive Power injection into the ERCOT Transmission Grid.  WGRs must also provide two other Real-Time SCADA points that communicate to ERCOT the following:

(a)	The number of wind turbines that are not able to communicate and whose status is unknown; and

(b)	The number of wind turbines out of service and not available for operation.

(13)	All PhotoVoltaic Generation Resources (PVGRs) must provide a Real-Time SCADA point that communicates to ERCOT the capacity of PhotoVoltaic (PV) equipment that is available for real power and/or Reactive Power injection into the ERCOT Transmission Grid.  PVGRs must also provide two other Real-Time SCADA points that communicate to ERCOT the following:

(a)	The capacity of PV equipment that is not able to communicate and whose status is unknown; and

(b)	The capacity of PV equipment that is out of service and not available for operation.

(14)	For the purpose of complying with the Reactive Power requirements under this Section 3.15, Reactive Power losses that occur on privately-owned transmission lines behind the POI may be compensated by automatically switchable static VAr capable devices.