## Slide 1
Generation Resource Energy and Regulation Deployment Performance Report for November 2017

## Slide 2: Non-IRR GREDP < 85% – November 2017
Unit | Total Intervals Passed | Total Intervals Scored | Std. Dev. (ATG - Exp MW) | GREDP Monthly Score
Unit 262 | 29 | 38 | 0.99 | 76.32
Unit 267 | 19 | 29 | 1.71 | 65.52
Unit 273 | 8 | 10 | 0.83 | 80.00
Unit 275 | 0 | 1 | 1.37 | 0.00

## Slide 3: IRR Summary – November 2017
IRR | Fleet | < 95% | > 100 INT, < 95%
GREDP Average (%) | 82.86 | 68.57 | 73.48
GREDP Median (%) | 94.00 | 77.54 | 79.81
Average MW Error | 3.27 | 3.34 | 3.49
Median MW Error | 2.96 | 3.30 | 3.51
Total Intervals Scored | 20,744 | 9,664 | 8,296
100+ Intervals Scored | 51 | 126 | 26
Total Intervals Scored Average | 113.98 | 161.07 | 319.08

## Slide 4: IRR < 95%, ≥ 100 Scored Intervals – November 2017
Unit | Total Intervals Passed | Total Intervals Scored | Std Dev (ATG - Exp MW) | GREDP Monthly Score
Unit 4 | 1122 | 1424 | 12.35 | 78.79
Unit 5 | 832 | 938 | 4.01 | 88.69
Unit 6 | 475 | 561 | 4.62 | 84.67
Unit 9 | 449 | 480 | 1.48 | 93.54
Unit 10 | 319 | 476 | 4.63 | 67.02
Unit 11 | 325 | 414 | 0.83 | 78.50
Unit 12 | 346 | 400 | 3.63 | 86.50
Unit 14 | 151 | 320 | 4.91 | 47.19
Unit 15 | 228 | 295 | 0.40 | 77.29
Unit 18 | 246 | 265 | 1.14 | 92.83
Unit 19 | 230 | 263 | 3.40 | 87.45

## Slide 5: IRR < 95%, ≥ 100 Scored Intervals – November 2017
Unit | Total Intervals Passed | Total Intervals Scored | Std Dev (ATG - Exp MW) | GREDP Monthly Score
Unit 20 | 88 | 259 | 1.44 | 33.98
Unit 22 | 210 | 227 | 5.47 | 92.50
Unit 23 | 183 | 220 | 4.55 | 83.18
Unit 25 | 187 | 208 | 6.18 | 89.90
Unit 26 | 131 | 193 | 3.27 | 67.88
Unit 30 | 120 | 182 | 5.63 | 65.93
Unit 33 | 105 | 167 | 1.24 | 62.87
Unit 34 | 150 | 166 | 1.23 | 90.36
Unit 35 | 154 | 163 | 0.95 | 94.48
Unit 37 | 19 | 124 | 5.97 | 15.32
Unit 39 | 97 | 120 | 2.14 | 80.83

## Slide 6: IRR < 95%, ≥ 100 Scored Intervals – November 2017
Unit | Total Intervals Passed | Total Intervals Scored | Std Dev (ATG - Exp MW) | GREDP Monthly Score
Unit 40 | 97 | 118 | 1.88 | 82.20
Unit 46 | 64 | 109 | 3.95 | 58.71
Unit 50 | 80 | 102 | 4.01 | 78.43

## Slide 7: IRR ≥ 95%, Scored Intervals ≥ 100 – November 2017
Unit | Total Intervals Passed | Total Intervals Scored | Std Dev (ATG - Exp MW) | GREDP Monthly Score
Unit 1 | 2445 | 2511 | 4.48 | 97.37
Unit 2 | 2038 | 2115 | 2.90 | 96.30
Unit 3 | 1420 | 1494 | 3.29 | 95.04
Unit 7 | 557 | 559 | 2.92 | 99.60
Unit 8 | 483 | 503 | 2.21 | 96.02
Unit 13 | 305 | 327 | 4.50 | 99.00
Unit 16 | 289 | 293 | 2.92 | 98.63
Unit 17 | 265 | 275 | 2.88 | 96.30
Unit 21 | 237 | 241 | 4.89 | 98.34
Unit 24 | 209 | 220 | 1.17 | 95.10
Unit 27 | 182 | 189 | 4.47 | 96.30

## Slide 8: IRR ≥ 95%, Scored Intervals ≥ 100 – November 2017
Unit | Total Intervals Passed | Total Intervals Scored | Std Dev (ATG - Exp MW) | GREDP Monthly Score
Unit 28 | 174 | 184 | 1.76 | 96.00
Unit 29 | 177 | 183 | 2.87 | 96.72
Unit 31 | 169 | 169 | 2.41 | 100.00
Unit 32 | 165 | 167 | 2.50 | 98.80
Unit 36 | 144 | 146 | 2.84 | 98.63
Unit 38 | 121 | 122 | 3.15 | 99.18
Unit 41 | 114 | 114 | 2.90 | 100.00
Unit 42 | 113 | 113 | 3.11 | 100.00
Unit 43 | 109 | 112 | 3.05 | 97.32
Unit 44 | 110 | 111 | 2.86 | 99.10
Unit 45 | 107 | 110 | 1.54 | 97.27

## Slide 9: IRR ≥ 95%, Scored Intervals ≥ 100 – November 2017
Unit | Total Intervals Passed | Total Intervals Scored | Std Dev (ATG - Exp MW) | GREDP Monthly Score
Unit 47 | 105 | 108 | 1.62 | 97.22
Unit 48 | 106 | 108 | 3.05 | 98.15
Unit 49 | 102 | 105 | 3.08 | 97.14