## Introduction
TLF = Transmission Loss Factor
SIEL = Settlement Interval ERCOT system Load
SSC = Seasonal Slope Coefficient = (SONLF - SOFFLF)/(SONL - SOFFL)
SIC = Seasonal Intercept Coefficient = [(SOFFLF * SONL) - (SONLF * SOFFL)]/(SONL - SOFFL)
SONLF = Seasonal on-peak percent loss factor
SOFFLF = Seasonal off-peak percent loss factor
SONL = Seasonal on-peak Load value
SOFFL = Seasonal off-peak Load value

## 2018_Transmission_Losses
TRANSMISSION LOSS FACTORS for 2018 as of 11/06/17
Data from Seasonal SSWG Base Cases Updated with updates received by 11/06/17
Transmission Loss is from 60 kV or higher reporting only
NOIE INTERNAL refers to generation, load and losses behind NOIE meters
|  | ERCOT TOTAL |  |  |  | AEN (9) NOIE INTERNAL TOTAL |  |  |  |  | CPS (5) NOIE INTERNAL TOTAL |  |  |  |  | COG (20) NOIE INTERNAL TOTAL |  |  |  |  | GEUS (21) NOIE INTERNAL TOTAL |  |  |  |  | COD (19) NOIE INTERNAL TOTAL |  |  |  |  | BPUB (15) NOIE INTERNAL TOTAL |  |  |  |  | BTU (22) NOIE INTERNAL TOTAL |  |  |  |  | COCS (23) NOIE INTERNAL TOTAL
Case Type | Base Case Name | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV | Total Base Case Loss MW | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen)
Spring On Peak | 2018_SPG1 | 67652.9 | 66257.5 | 1276.29 | 1383.37 | 1670.9 | 2439.7 | 37.41 | 40 | 808.8 | 2541.2 | 3951 | 23.66 | 27.6 | 1437.4 | 228.2 | 427 | 4.51 | 4.5 | 203.3 | 41 | 75.7 | 0.32 | 0.3 | 35 | 0 | 304.4 | 0.68 | 0.7 | 305.1 | 95 | 294.6 | 0.7 | 0.8 | 200.4 | 151.2 | 335.4 | 2.83 | 3.2 | 187.4 | 0 | 160.9 | 0.15 | 0.2 | 161.1
Spring Off Peak | 2018_SPG2 | 41818.3 | 41022.3 | 725.67 | 781.76 | 1372 | 1340.6 | 19.38 | 21.1 | -10.3 | 961 | 2094 | 7.88 | 8.5 | 1141.5 | 109.6 | 204.7 | 0.85 | 0.8 | 95.9 | 32 | 50.7 | 0.15 | 0.1 | 18.8 | 0 | 208.9 | 0.35 | 0.3 | 209.2 | 38 | 144.6 | 0.22 | 0.3 | 106.9 | 38.4 | 167.8 | 1.46 | 1.5 | 130.9 | 0 | 75 | 0.02 | 0 | 75
Summer On Peak | 2018_SUM1 | 83518.3 | 81808.5 | 1559.77 | 1686.01 | 1604.9 | 2876 | 51.2 | 53.6 | 1324.7 | 4688.1 | 5207 | 37.93 | 44.8 | 563.7 | 310 | 580.1 | 7.32 | 7.3 | 277.4 | 89 | 115.1 | 0.88 | 1 | 27.1 | 0 | 328.6 | 1.08 | 1.1 | 329.7 | 104 | 306.8 | 0.69 | 0.8 | 203.6 | 260 | 447.2 | 4.95 | 5.9 | 193.1 | 0 | 220 | 0.25 | 0.3 | 220.3
Summer Off Peak | 2018_SUM2 | 51896 | 51112.2 | 704.68 | 771.77 | 1238.1 | 1583.8 | 20.45 | 21.7 | 367.4 | 2640.8 | 2916 | 18.84 | 22.1 | 297.3 | 112.8 | 211 | 1.59 | 1.6 | 99.8 | 89 | 71 | 0.43 | 0.4 | -17.6 | 0 | 167.5 | 0.44 | 0.4 | 167.9 | 46 | 161.6 | 0.23 | 0.3 | 115.9 | 149.1 | 254 | 1.6 | 2 | 106.9 | 0 | 106.2 | 0.09 | 0.1 | 106.3
Fall On Peak | 2018_FAL1 | 69140.9 | 67830.1 | 1196.36 | 1298.99 | 1654.7 | 2337 | 33.64 | 36.2 | 718.5 | 2055.4 | 4173 | 25.49 | 28.4 | 2146 | 206.8 | 387.2 | 3.42 | 3.4 | 183.8 | 49 | 90.1 | 0.46 | 0.5 | 41.6 | 0 | 265.4 | 0.98 | 1 | 266.4 | 104 | 291.9 | 0.61 | 0.8 | 188.7 | 126.6 | 416 | 3.87 | 4.1 | 293.5 | 0 | 163.5 | 0.28 | 0.3 | 163.8
Fall Off Peak | 2018_FAL2 | 43087.7 | 42190.5 | 824.52 | 882.63 | 971.1 | 1403 | 14.99 | 15.8 | 447.7 | 961.4 | 2253 | 8.67 | 9.3 | 1300.9 | 105.3 | 196.8 | 0.68 | 0.7 | 92.2 | 24 | 55.2 | 0.16 | 0.2 | 31.4 | 0 | 111.5 | 0.65 | 0.7 | 112.2 | 42 | 136.7 | 0.23 | 0.3 | 95 | 38.4 | 208 | 1.97 | 2 | 171.6 | 0 | 73.6 | 0.03 | 0 | 73.6
Winter On Peak | 2019_WIN1 | 67349.9 | 66070.9 | 1162.75 | 1267.13 | 1680.3 | 2076 | 35.39 | 38 | 433.7 | 4260 | 3776 | 25.9 | 31.6 | -452.4 | 260.8 | 488.1 | 3.24 | 3.2 | 230.5 | 0 | 78.1 | 0.25 | 0.2 | 78.3 | 0 | 206.5 | 0.65 | 0.7 | 207.2 | 68 | 265.3 | 0.66 | 0.8 | 198.1 | 49.7 | 311.4 | 2.73 | 2.8 | 264.5 | 0 | 142.3 | 0.24 | 0.2 | 142.5
Winter Off Peak | 2019_WIN2 | 49819.1 | 48957.8 | 775.13 | 848.69 | 1187.2 | 1560.3 | 16.69 | 18.2 | 391.3 | 963 | 2454 | 12.18 | 12.8 | 1503.8 | 127.2 | 238.1 | 1.3 | 1.3 | 112.2 | 0 | 63.4 | 0.17 | 0.2 | 63.6 | 0 | 105.4 | 0.62 | 0.6 | 106 | 28 | 189.7 | 0.41 | 0.5 | 162.2 | 38.5 | 226.4 | 1.33 | 1.3 | 189.2 | 0 | 79 | 0.08 | 0.1 | 79.1
Self Serve Load Modeled in Base Cases that does not contribute to transmission losses. | [8 empty] | NOIE TOTALS
Case Type | Base Case Name | CNP Self Serve MW | AEP Self Serve MW | TNMP Self Serve MW | BTU Self Serve MW | ONCOR Self Serve MW | AEP DC Ties Model MW | TOTAL |  | NOIE LOAD MW | NOIE External Resources MW | NOIE Load Served from Internal Resources MW | NOIE TOTAL Loss Above 60 kV | Base Case Name
Spring On Peak | 2018_SPG1 | 2597 | 1002.3 | 587.1 | 42.92 | 112.1 | 0 | 4341.42 |  | 7988.7 | 3338.5 | 4650.2 | 70.26 | 2018_SPG1
Spring Off Peak | 2018_SPG2 | 2597 | 973.2 | 513.72 | 26.4 | 112.1 | 0 | 4222.42 |  | 4286.3 | 1767.9 | 2518.4 | 30.31 | 2018_SPG2
Summer On Peak | 2018_SUM1 | 2597 | 1265.28 | 587.1 | 42.99 | 112.1 | 0 | 4604.47 |  | 10080.8 | 3139.6 | 6941.2 | 104.3 | 2018_SUM1
Summer Off Peak | 2018_SUM2 | 2597 | 976.46 | 528.4 | 45.76 | 112.1 | 0 | 4259.72 |  | 5471.1 | 1243.9 | 4227.2 | 43.67 | 2018_SUM2
Fall On Peak | 2018_FAL1 | 2597 | 973.2 | 587.1 | 31.9 | 112.1 | 0 | 4301.3 |  | 8124.1 | 4002.3 | 4121.8 | 68.75 | 2018_FAL1
Fall Off Peak | 2018_FAL2 | 2597 | 973.2 | 484.37 | 26.41 | 112.1 | 0 | 4193.08 |  | 4437.8 | 2324.6 | 2113.2 | 27.38 | 2018_FAL2
Winter On Peak | 2019_WIN1 | 2644 | 1022.15 | 587.1 | 0 | 112.1 | 0 | 4365.35 |  | 7343.7 | 1102.4 | 6241.3 | 69.06 | 2019_WIN1
Winter Off Peak | 2019_WIN2 | 2644 | 944.96 | 499.04 | 26.43 | 112.1 | 0 | 4226.53 |  | 4916.3 | 2607.4 | 2308.9 | 32.78 | 2019_WIN2
SEASON | ERCOT WITH SELF SERVE LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL
| SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF
SPRING | 63311.48 | 37595.88 | 2.016% | 1.93% |  | 2439.7 | 1340.6 | 1.51% | 1.425% |  | 3951 | 2094 | 0.5953% | 0.3749% |  | 427 | 204.7 | 1.045% | 0.4135% |  | 75.7 | 50.7 | 0.4209% | 0.295% |  | 304.4 | 208.9 | 0.2229% | 0.1673% |  | 294.6 | 144.6 | 0.237% | 0.1519% |  | 335.4 | 167.8 | 0.8367% | 0.8626% |  | 160.9 | 75 | 0.09314% | 0.02666%
SUMMER | 78913.83 | 47636.28 | 1.977% | 1.479% |  | 2876 | 1583.8 | 1.749% | 1.275% |  | 5207 | 2916 | 0.7232% | 0.6419% |  | 580.1 | 211 | 1.246% | 0.7479% |  | 115.1 | 71 | 0.7588% | 0.602% |  | 328.6 | 167.5 | 0.3276% | 0.262% |  | 306.8 | 161.6 | 0.2244% | 0.1421% |  | 447.2 | 254 | 1.095% | 0.626% |  | 220 | 106.2 | 0.1135% | 0.08467%
FALL | 64839.6 | 38894.62 | 1.845% | 2.12% |  | 2337 | 1403 | 1.419% | 1.057% |  | 4173 | 2253 | 0.6071% | 0.3833% |  | 387.2 | 196.8 | 0.8755% | 0.3443% |  | 90.1 | 55.2 | 0.508% | 0.289% |  | 265.4 | 111.5 | 0.3679% | 0.5796% |  | 291.9 | 136.7 | 0.2085% | 0.168% |  | 416 | 208 | 0.9217% | 0.9382% |  | 163.5 | 73.6 | 0.171% | 0.04074%
WINTER | 62984.55 | 45592.57 | 1.846% | 1.7% |  | 2076 | 1560.3 | 1.676% | 1.058% |  | 3776 | 2454 | 0.6812% | 0.4939% |  | 488.1 | 238.1 | 0.6594% | 0.543% |  | 78.1 | 63.4 | 0.3191% | 0.2674% |  | 206.5 | 105.4 | 0.3138% | 0.5848% |  | 265.3 | 189.7 | 0.2482% | 0.2157% |  | 311.4 | 226.4 | 0.8691% | 0.584% |  | 142.3 | 79 | 0.1684% | 0.1012%
TRANSMISSION LOSS FACTORS FOR INSTALLATION IN ERCOT SYSTEMS IN RED BOXES
SEASON | ERCOT WITH SELF SERVE, MODEL & NOIE INTERNAL LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL
| SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC
SPRING | 3.3328e-06 | 1.8049 |  |  |  | 7.7524e-05 | 1.3211 |  |  |  | 0.00011867 | 0.12641 |  |  |  | 0.0028414 | -0.16811 |  |  |  | 0.0050383 | 0.039545 |  |  |  | 0.0005825 | 0.045581 |  |  |  | 0.00056756 | 0.069843 |  |  |  | -0.00015435 | 0.88848 |  |  |  | 0.00077391 | -0.031384
SUMMER | 1.5898e-05 | 0.72196 |  |  |  | 0.0003671 | 0.69332 |  |  |  | 3.5457e-05 | 0.53855 |  |  |  | 0.0013498 | 0.46311 |  |  |  | 0.0035547 | 0.3496 |  |  |  | 0.00040715 | 0.1938 |  |  |  | 0.00056662 | 0.050559 |  |  |  | 0.0024265 | 0.0096582 |  |  |  | 0.00025337 | 0.057766
FALL | -1.0591e-05 | 2.5318 |  |  |  | 0.00038747 | 0.51351 |  |  |  | 0.00011655 | 0.12076 |  |  |  | 0.0027899 | -0.20471 |  |  |  | 0.0062732 | -0.057261 |  |  |  | -0.0013755 | 0.73295 |  |  |  | 0.00026141 | 0.13223 |  |  |  | -7.9401e-05 | 0.95474 |  |  |  | 0.0014485 | -0.065863
WINTER | 8.3926e-06 | 1.3175 |  |  |  | 0.001198 | -0.81087 |  |  |  | 0.00014172 | 0.14609 |  |  |  | 0.00046559 | 0.43217 |  |  |  | 0.0035142 | 0.044619 |  |  |  | -0.0026806 | 0.86734 |  |  |  | 0.0004298 | 0.13413 |  |  |  | 0.0033534 | -0.17519 |  |  |  | 0.0010618 | 0.017283
EFFECTIVE DATES | SEASON
03/01/2018 - 05/31/2018 | SPRING
06/01/2018 - 09/30/2018 | SUMMER
10/01/2018 - 11/30/2018 | FALL
12/01/2018 - 02/28/2019 | WINTER