| NOGRR Number | 169 | NOGRR Title | Disturbance Monitoring Requirements Update to Align with NERC Reliability Standard PRC-002-2 |
| --- | --- | --- | --- |
| Date of Decision |  | November 17, 2017 |  |
| Action |  | Recommended Approval |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | February 1, 2018 |  |
| Priority and Rank Assigned |  | Not applicable |  |
| Nodal Operating Guide Sections Requiring Revision |  | 6.1.1, Introduction 6.1.2, Fault Recording Equipment 6.1.2.1, Triggering Requirements 6.1.2.2, Location Requirements 6.1.2.3, Data Recording Requirements 6.1.2.4, Data Retention and Reporting Requirements 6.1.2.5, Maintenance and Testing Requirements (delete) 6.1.3, Phasor Measurement Recording Equipment 6.1.3.1, Recording Requirements 6.1.3.2 Location Requirements 6.1.3.3 Data Recording and Redundancy Requirements 6.1.3.4 Data Retention and Reporting Requirements 6.1.4, Maintenance and Testing Requirements (new) 6.1.4, Equipment Reporting Requirements 6.1.5, Review Process 8, Attachment M, Selecting Buses for Capturing Sequence of Events Recording and Fault Recording Data (new) |  |
| Related Documents Requiring Revision/Related Revision Requests |  | None |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) aligns language in Section 6.1, Disturbance Monitoring Requirements, with North American Electric Reliability Corporation (NERC) Reliability Standard PRC-002-2, Define Regional Disturbance Monitoring and Reporting Requirements. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | The current Nodal Operating Guide utilizes an entirely different approach to determining required locations for disturbance monitoring equipment than that required by NERC Reliability Standard PRC-002-2. This request relieves the burden on Facility owners of having to adhere to two vastly different requirements for the same purpose. |  |
| OWG Decision |  | On 4/20/17, the Operations Working Group (OWG) was in consensus to table NOGRR169. On 8/17/17, OWG was in consensus to recommend approval of NOGRR169 as amended by the 5/23/17 ERCOT comments. On 9/21/17, OWG was in consensus to table NOGRR169. On 11/17/17, OWG was in consensus to endorse and forward to ROS the 9/21/17 OWG Report and Impact Analysis for NOGRR169. |  |
| Summary of OWG Discussion |  | On 4/20/17, participants discussed the differences between NERC Reliability Standard PRC-002-2 and the Nodal Operating Guide language pertaining to disturbance monitoring equipment, and requested tabling of NOGRR169 for additional review. On 8/17/17, participants reviewed the 5/23/17 ERCOT comments. On 9/21/17, participants reviewed the 9/19/17 ERCOT comments and tabled NOGRR169 to allow ERCOT additional time to complete the Impact Analysis. On 11/17/17, there was no discussion. |  |

| Sponsor |  |
| --- | --- |
| Name | Bret Burford (2016 Chair) on behalf of the System Protection Working Group (SPWG) |
| E-mail Address | bgburford@aep.com |
| Company | American Electric Power (AEP) |
| Phone Number | 361-881-5866 |
| Cell Number | 361-816-0637 |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Cory Phillips |
| E-Mail Address | cory.phillips@ercot.com |
| Phone Number | 512-248-6464 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ERCOT 052317 | Proposed several clarifying edits and introduced a new Section 8, Attachment M, describing the methodology for selecting buses for sequence of events recording and fault recording data |
| ERCOT 091917 | Requested additional time for development of the Impact Analysis for NOGRR169 |

Market Rules Notes

None

Proposed Guide Language Revision

6.1.1	Introduction

(1)	Disturbance monitoring is necessary to:

(a)	Determine performance of the ERCOT System;

(b)	Determine effectiveness of protective relaying systems;

(c)	Verify ERCOT System models;

(d)	Determine causes of ERCOT System disturbances (trips, faults, and protective relay system actions); and

(e)	Meet the requirements of North American Reliability Corporation (NERC) Reliability Standards.

(2)	To ensure that adequate data is available for these activities, the disturbance monitoring requirements and procedures discussed in these Operating Guides have been established by ERCOT for fault recording, sequence of events recording, and dynamic disturbance recording equipment owners in the ERCOT System.

6.1.2	Fault Recording and Sequence of Events Recording Equipment

(1)	Fault recording equipment includes digital fault recorders, certain protective relays and/or meters with fault recording capability, and dynamic disturbance recorders that meets the associated requirements in this Section.

(2)	Sequence of events recording equipment includes any device capable of recording circuit breaker position (open/close) that meets the associated requirements in this Section.

(3)	Required fault recording and sequence of events recording equipment shall have a clock source that is synchronized to within +/- 2 milliseconds of Coordinated Universal Time (UTC), with or without a local time offset for Central Prevailing Time (CPT).

6.1.2.1	Fault Recording Requirements

(1)	Fault recording equipment shall meet the following requirements:

(a)	Triggering for at least the following:

(i)	Neutral (residual) overcurrent; and

(ii)	Phase under-voltage or overcurrent;

(b)	Minimum recording rate of 16 samples per cycle; and

(c)	A single record or multiple records that include:

(i)	A pre-trigger record length of at least two cycles and a total record length of at least 30 cycles for the same trigger point; or

(ii)	At least two cycles of the pre-trigger data, the first three cycles of post-trigger data, and the final cycle of the fault as seen by the fault recorder.

6.1.2.2	Fault Recording and Sequence of Events Recording Equipment Location Requirements

(1)	The location criteria listed below applies to Transmission Facilities operated at or above 100 kV.  The Facility owner(s), whether a Transmission Facility owner or Generation Resource owner, shall install fault recording and sequence of events recording equipment at the following Facilities, at a minimum:

(a)	Locations identified by the Transmission Facility owner utilizing the methodology in Section 8, Attachment M, Selecting Buses for Capturing Sequence of Events Recording and Fault Recording Data;

(b)	Additional locations selected at the Transmission Facility owner’s discretion, utilizing the methodology in Section 8, Attachment M;

(c)	ERCOT mandatory fault recording and sequence of events recording locations operating at or above 100kV, as defined below.

(i)	Interconnections with non-ERCOT Control Areas (i.e., outside ERCOT Region);

(ii)	Substations where electrical transfers of equipment can be made between the ERCOT Control Area and non-ERCOT Control Area;

(iii)	At all generating station switchyards connected to the ERCOT System with an aggregated generating capacity above 100 MVA or at the remote line terminals of each generating station switchyard.

(2)	Facility owners shall install the fault recording and sequence of events recording equipment identified in paragraphs (1)(a) and (1)(b) above.  This installation shall occur such that half of the identified facilities have the associated equipment installed by July 1, 2020, and all of the identified facilities by July 1, 2022.

(3)	Facility owners shall install the fault recording and sequence of events recording equipment identified in paragraph (1)(c) above by July 1, 2019.

6.1.2.3	Fault Recording and Sequence of Events Recording Data Requirements

(1)	Each Transmission Facility owner and Generation Resource owner shall have fault recording data to determine the following electrical quantities for each triggered fault recording for the Transmission Elements  operated at or above 100kV it owns connected to the Facilities operated at or above 100kV identified in these requirements::

(a)	Phase-to-neutral voltage for each phase of each specified bus.  Two sets of substation voltage measurements for breaker-and-a-half and ring bus substation configurations.  One set of substation voltage measurements for each bus in other substation configurations.

(b)	For all transmission lines, each phase current and the neutral (residual) current; and

(c)	For all transformers that have a low-side operating voltage of 100kV or above, each phase current and the neutral (residual) current.

(2)	Each Transmission Facility owner and Generation Resource owner shall have sequence of events recording data per the following requirements:

(a)	Circuit breaker position (open/close) for each circuit breaker that it owns connected directly to the transmission buses identified in paragraphs (1)(a) and (1)(b) of Section 6.1.2.2, Fault Recording and Sequence of Events Recording Equipment Location Requirements; and

(b)	The following data is required as either part of the sequence of events recording data or fault recording digital status data:

(i)	Circuit breaker position for each circuit breaker that it owns associated with monitored generator interconnects, transmission lines, and transformers;

(ii)	Carrier transmitter control status (i.e. start, stop, keying) for associated transmission lines; and

(iii)	Carrier signal receive status for associated transmission lines.

6.1.2.4	Fault Recording and Sequence of Events Recording Data Retention and Reporting Requirements

(1)	Each Transmission Facility owner and Generation Resource owner shall provide, upon request, fault recording and sequence of events recording data for the transmission buses or Transmission Elements identified in these requirements to the requesting Entity in accordance with the following:

(a)	Data will be retrievable for the period of ten calendar days, inclusive of the day the data was recorded;

(b)	Data subject to item (a) above will be provided within 30 calendar days of request unless an extension is granted by the requestor;

(c)	Sequence of events recording data will be provided in ASCII Comma Separated Value (CSV) format as follows:  Date, Time, Local Time Code, Substation, Device, State;

(d)	Fault recording data will be provided in electronic files that are formatted in conformance with Institute of Electrical and Electronic Engineers (IEEE) C37.111, IEEE Standard for Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later; and

(e)	Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later.

(2)	The Transmission Facility owner and Generation Resource owner providing the requested fault recording and sequence of events recording data to ERCOT, the NERC Regional Entity, or NERC shall store the requested data for at least a three year period.

6.1.3	Phasor Measurement Recording Equipment Including Dynamic Disturbance Recording Equipment

(1)	Phasor measurement recording equipment includes all dynamic disturbance recording equipment with phasor measurement recording capability that meet the requirements in Sections 6.1.3.1, Recording and Triggering Requirements, and 6.1.3.3, Data Recording and Redundancy Requirements.

(2)	Phasor measurement recording equipment required by these Operating Guides shall be time synchronized with a Global Positioning System-based clock, or ERCOT-approved alternative, with sub-cycle (<1 microsecond) timing accuracy and performance.

- 6.1.3.1	Recording and Triggering Requirements

(1)	Recorded electrical quantities shall be:

(a)	Provided in IEEE C37.118.1-2011, IEEE Standard for Synchrophasor format;

(b)	A minimum output recording rate of 30 times per second;

(c)	A minimum input sampling rate of 960 samples per second; and

(d)	Transmitted to an ERCOT phasor data concentrator via a communication link or stored locally per retention requirements in Section 6.1.3.4, Data Retention and Data Reporting Requirements.

- 6.1.3.2	Location Requirements

(1)	ERCOT shall identify Transmission Elements operated at or above 100kV for which dynamic disturbance recording data is required, including the following:.

(a)	Generation Resource(s) with:

(i)	Gross individual nameplate rating greater than or equal to 500 MVA; or

(ii)	Gross individual nameplate rating greater than or equal to 300 MVA where the gross plant/facility aggregate nameplate rating is greater than or equal to 1,000 MVA;

(b)	Any one Transmission Element that is part of a stability (angular or voltage) related system operating limit;

(c)	Each terminal of a high-voltage, direct current (HVDC) circuit with a nameplate rating greater than or equal to 300 MVA, on the alternating current portion of the converter;

(d)	One or more Transmission Elements that are part of an Interconnection Reliability Operating Limit (IROL); and

(e)	Any one Transmission Element within a major voltage sensitive area as defined by an area with an in-service Under-Voltage Load Shedding (UVLS) program.

(2)	ERCOT shall identify a minimum dynamic disturbance recording coverage, inclusive of those Transmission Elements identified above, of a least:

(a)	One Transmission Element; and

(b)	One Transmission Element per 3,000 MW of ERCOT’s historical simultaneous peak Demand.

(3)	Facility owners identified under paragraphs (1) or (2) above shall install dynamic disturbance recording equipment by July 1, 2019.

(4)	The Facility owner(s), whether a Transmission Facility owner or new Generation Resource owner, shall install phasor measurement recording equipment at the following Facilities.

(a)	Flexible AC transmission system devices configured to actively control steady-state voltage or power transfer capability, operated at or above 100kV, and energized after July 1, 2015;

(b)	Within 18 months after receiving written notice from ERCOT, a Transmission Facility identified by ERCOT associated with each published generic transmission constraint as deemed necessary by ERCOT; and

(c)	New generating Facilities over 20 MVA aggregated at a single site placed into service after January 1, 2017.

- 6.1.3.3	Data Recording and Redundancy Requirements

(1)	Recorded electrical quantities shall be sufficient to determine the following:

(a)	For Transmission Facility owner locations meeting paragraphs (1) or (2) of Section 6.1.3.2, Location Requirements:

(i)	Phase-to-neutral voltage magnitude/angle data for each phase from at least two distinct transmission level element measurements;

(ii)	Single phase current magnitude/angle data for each phase from at least two distinct transmission level lines; and

(iii)	Frequency and df/dt data for at least two transmission level element measurements.

(b)	For Generator Resource owner locations meeting paragraph (1) or (2) of Section 6.1.3.2:

(i)	Phase-to-neutral voltage, or phase-to-phase voltage magnitude/angle data for each phase from at least one generator-interconnected bus measurement;

(ii)	Single phase current magnitude/angle data for each phase from each interconnected generator over 20 MVA; and

(iii)	Frequency and df/dt data for at least one generator-interconnected bus measurement.

- 6.1.3.4	Data Retention and Data Reporting Requirements

(1)	The minimum recorded electrical quantities shall be retained per the following guidelines:

(a)	Rolling ten calendar day window for all data stored locally and not transmitted to an ERCOT phasor data concentrator;

(b)	Minimum three year data retention by the Generation Resource owner for event data utilized for model validation in accordance with NERC Reliability Standards; and

(c)	Minimum three year data retention by the Generation Resource owner or Transmission Facility owner for event data provided to ERCOT, the NERC Regional Entity, or NERC via written request that is recorded in the context of an ERCOT-, NERC Regional Entity-, or NERC-initiated disturbance analysis or event review.

(2)	Each Transmission Facility owner and Generation Resource owner shall provide, upon request, dynamic disturbance recording data for the buses or Transmission Elements identified in these requirements to the requesting entity, in accordance with the following:

(a)	Data will be retrievable for the period of ten calendar days, inclusive of the day the data was recorded;

(b)	Data subject to item (a) above will be provided within 30 calendar days of a request unless an extension is granted by the requestor;

(c)	Dynamic disturbance recording data will be provided in electronic files that are formatted in conformance with IEEE C37.111, revision C37.111-1999 or later;

(d)	Data files will be named in conformance with IEEE C37.232, revision C37.232-2011 or later.

6.1.4	Maintenance and Testing Requirements

(1)	Each Transmission Facility owner and Generation Resource owner with dynamic disturbance recording, fault recording, and/or sequence of events recording equipment identified by these requirements shall maintain and test their recording equipment as follows:

(a)	Calibration of the recording devices shall be performed at installation and when records from the equipment indicate a calibration problem.

6.1.5	Equipment Reporting Requirements

(1)	Disturbance monitoring equipment owners shall maintain a current database summarizing their disturbance monitoring equipment installations.

(2)	The database shall include installation location, type of equipment, make and model of equipment, operational status, a listing of the major equipment being monitored.  This database shall be submitted to ERCOT annually, by October 31.  Additionally, a complete list of all monitored points at each installation shall be maintained by disturbance monitoring equipment owners and provided, when requested specifically by ERCOT, the NERC Regional Entity, or NERC, within 30 days.

(3)	ERCOT shall maintain and update annually, a comprehensive database of all disturbance monitoring equipment owners’ disturbance monitoring equipment submittals.

6.1.6	Review Process

(1)	ERCOT shall review dynamic disturbance recording equipment locations for adequacy when significant changes are made to the ERCOT System or at least every five years.

(2)	Transmission Facility owners shall review fault recording and sequence of events recording equipment locations for compliance at least every five years.

(3)	Existing Facility Owners identified in the reviews shall have three years from the time of notification to install the equipment.

ERCOT Nodal Operating Guides

Section 8

Attachment M

Selecting Buses for Capturing Sequence of Events Recording and Fault Recording Data

XXX 1, 2017

This attachment provides the Transmission Facility owner the methodology to use for selecting bus locations for capturing sequence of events recording and fault recording data.

To identify monitored bulk electric system buses for sequence of events recording and fault recording data, each Transmission Facility owner shall follow sequentially, unless otherwise noted, the steps listed below:

Step 1. Determine a complete list of bulk electric system buses that it owns.

For the purposes of this attachment, a single bulk electric system bus includes physical buses with breakers connected at the same voltage level within the same physical location sharing a common ground grid. These buses may be modeled or represented by a single node in fault studies. For example, ring bus or breaker-and-a-half bus configurations are considered to be a single bus.

Step 2. Reduce the list to those bulk electric system buses that have a maximum available calculated three phase short circuit MVA of 1,500 MVA or greater. If there are no buses on the resulting list, proceed to Step 7.

Step 3. Determine the 11 bulk electric system buses on the list with the highest maximum available calculated three phase short circuit MVA level. If the list has 11 or fewer buses, proceed to Step 7.

Step 4. Calculate the median MVA level of the 11 bulk electric system buses determined in Step 3.

Step 5. Multiply the median MVA level determined in Step 4 by 20 percent.

Step 6. Reduce the bulk electric system buses on the list to only those that have a maximum available calculated three phase short circuit MVA higher than the greater of:

- 1,500 MVA or

- 20 percent of median MVA level determined in Step 5.

Step 7. If there are no bulk electric system buses on the list: the procedure is complete and no fault recording and sequence of events recording data will be required. Proceed to Step 9.

If the list has 1 or more but less than or equal to 11 bulk electric system buses: fault recording and sequence of events recording data is required at the bulk electric system bus with the highest maximum available calculated three phase short circuit MVA as determined in Step 3. Proceed to Step 9.

If the list has more than 11 bulk electric system buses: fault recording and sequence of events recording data is required on at least the 10 percent of the bulk electric system buses determined in Step 6 with the highest maximum available calculated three phase short circuit MVA. Proceed to Step 8.

Step 8. Fault recording and sequence of events recording data is required at additional bulk electric system buses on the list determined in Step 6. The aggregate of the number of bulk electric system buses determined in Step 7 and this Step will be at least 20 percent of the bulk electric system buses determined in Step 6. The additional bulk electric system buses are selected, at the Transmission Facility owner’s discretion, to provide maximum wide-area coverage for fault recording and sequence of events recording data. The following bulk electric system bus locations are recommended:

- Electrically distant buses or electrically distant from other DME devices.

- Voltage sensitive areas.

- Cohesive load and generation zones.

- Bulk electric system buses with a relatively high number of incident Transmission circuits.

- Bulk electric system buses with reactive power devices.

- Major Facilities interconnecting outside the Transmission Owner’s area.

Step 9. The list of monitored bulk electric system buses for fault recording and sequence of events recording data is the aggregate of the bulk electric system buses determined in Steps 7 and 8.