## Slide 1
Panhandle GTC Analysis
ERCOT Operations Planning

## Slide 2: Outline
Background
Framing the Problem & Examples
Panhandle Overloads Instances
Potential Solutions

## Slide 3: Background
ERCOT has an existing stability concern in the Panhandle region and consequentially ERCOT has defined Generic Transmission Constraint.
ERCOT has observed the real-time flow on the interface exceeding the calculated limit on numerous occasions.
This creates a reliability concern due to the potential loss of generation in the area
To mitigate this concern, ERCOT has to lower the limit at which the GTC is constrained in order to try and manage the flow to the true limit.

## Slide 4: Framing the Problem
By design, SCED does not have the ability to “look ahead” when it comes to wind resources.
Basepoints for wind, are set via persistence.
When Congestion occurs in the panhandle, typically some units are curtailed and others are not.
While curtailed units are under control and following basepoints, the un-curtailed units continue normal operations and often ramp.
  Primarily, the curtailed units follow basepoints well.
Ramps from un-curtailed units are unaccounted for in SCED, and lead to overloading the GTC.

## Slide 5: October 26th, 2017
Chart: 

## Slide 6: June 21st, 2017
Chart: 6.21.17

## Slide 7: Panhandle GTC > 100%
Chart: Count of Five Minute Intervals where Real-Time Flow Exceeds Limit
| January | February | March | April | May | June | July | August | September | October | November | December
2016 | 0 | 0 | 21 | 1 | 17 | 0 | 1 | 0 | 0 | 0 | 23 | 20
2017 | 0 | 0 | 1 | 0 | 4 | 16 | 2 | 0 | 23 | 12 | 4 | 4

## Slide 8: Count of Intervals over 95%
Chart: 
| January | February | March | April | May | June | July | August | September | October | November | December
2016 | 0 | 144 | 123 | 2 | 464 | 13 | 1 | 0 | 16 | 48 | 1424 | 703
2017 | 265 | 770 | 670 | 886 | 726 | 923 | 303 | 113 | 449 | 1512 | 1045 | 814

## Slide 9: Count of Intervals over 95% continued
Chart: 
| January | February | March | April | May | June | July | August | September | October | November | December
2016 | 0 | 144 | 123 | 2 | 464 | 13 | 1 | 0 | 16 | 48 | 1424 | 703
2017 | 265 | 770 | 670 | 886 | 726 | 923 | 303 | 113 | 449 | 1512 | 1045 | 814
 | 2016 - 95% | 2017 - 95% | 2016 - 100% | 2017 - 100%
January | 0 | 265 | 0 | 0
February | 144 | 770 | 0 | 0
March | 123 | 670 | 21 | 1
April | 2 | 886 | 1 | 0
May | 464 | 726 | 17 | 4
June | 13 | 923 | 0 | 16
July | 1 | 303 | 1 | 2
August | 0 | 113 | 0 | 0
September | 16 | 449 | 0 | 23
October | 48 | 1512 | 0 | 12
November | 1424 | 1045 | 23 | 4
December | 703 | 814 | 20 | 4
Total | 2938 | 7894 | 83 | 65
Instances over 95% nearly tripled, while instances over 100% declined.

## Slide 10: Discount Factor Statistics
Nov-Dec 2017 |  | Discount Factor |  |  |  |  |  |  | 
 |  | Statistics |  |  |  | Number of SCED intervals |  |  | 
 |  | Average | Max | Min | Median | 85%-89% | 90-94% | >95% | All
Loading Factor | All | 90.36 | 98 | 85 | 93 | 8738 | 287 | 8621 | 17,646
 | >=90 | 95.19 | 98 | 85 | 95 | 8 | 235 | 4661 | 4904
 | >=95 | 95.71 | 98 | 85 | 95 | 3 | 55 | 1216 | 1274
 | >=100 | 94.50 | 98 | 85 | 95 | 0 | 3 | 3 | 6
Nov-Dec 2016 |  | Discount Factor |  |  |  |  |  |  | 
 |  | Statistics |  |  |  | Number of SCED intervals |  |  | 
 |  | Average | Max | Min | Median | 85%-89% | 90-94% | >95% | All
Loading Factor | All | 91.75 | 98 | 85 | 95 | 6,266 | 1,432 | 9,927 | 17,625
 | >=90 | 95.34 | 98 | 85 | 95 | 4 | 772 | 3316 | 4092
 | >=95 | 95.93 | 98 | 90 | 95 | 0 | 89 | 1430 | 1519
 | >=100 | 94.94 | 97 | 91 | 95 | 0 | 3 | 30 | 33
*The discount factor is the percentage that a constraint is being bound to compared to the true limit.
*The loading factor is the loading compared to the true limit.

## Slide 11: Hours Active vs. Hours Binding
Chart: 
| January | February | March | April | May | June | July | August | September | October | November | December
2016 Binding | 0.42278 | 13.6625 | 77.5011 | 0.24917 | 60.485 | 1.2506 | 5.2558 | 0.084722 | 1.8339 | 6.3381 | 208.0711 | 69.6681
2017 Binding | 28.4217 | 68.2956 | 127.5364 | 184.02 | 115.9178 | 141.4133 | 48.8336 | 12.9444 | 100.8364 | 230.6044 | 212.3981 | 146.3286
2016 Active | 1.7489 | 40.7503 | 82.5867 | 74.9997 | 157.3267 | 22.8247 | 71.4947 | 5.1664 | 90.9933 | 193.9231 | 261.7467 | 254.9822
2017 Active | 172.5706 | 259.9394 | 306.6383 | 343.9089 | 288.2506 | 233.4969 | 115.2397 | 33.4161 | 197.3325 | 356.0169 | 302.8117 | 224.2439

## Slide 12: Solution 1 – Status Quo
Continue to have the Panhandle GTC be constrained to as low as 85% (with the possibility of going even lower.)
    Have to over-constrain.
Doesn’t require any rule or system changes.
May continue to see overloads depending on when we ERCOT choose to constrain.

## Slide 13: Solution 2 – Do not exceed limit
Give all wind units a “Do Not Exceed Limit”
    Value where all units have an additional value instruction that they cannot exceed, regardless of wind conditions.
Would need some sort of definition (New type of GTC, etc.)
    How would that be done?
Should offer better control, and ability to raise GTC constrained value percentage.

## Slide 14: Solution 3 – Incorporate 5 Min. Wind Forecast
Calculate wind unit basepoints based on 5 minute wind forecast.
    Must be incorporated into HSL used by SCED.
Potentially places more units in curtailed “bucket” and allow ERCOT to raise GTC constrained value percentage.
Will work well for predictable, sustained wind ramps.
During quick, unpredictable wind ramps, exceedance will depend on forecast accuracy.
    On track to receive regional 5-min forecast from AWS and Energy & Meteo. Would need individual forecasts.

## Slide 15: Solution 4
Combination of Solution 2 and 3.

## Slide 16: Solution 5 -???
???

## Slide 17: Questions?