| PGRR Number | 060 | PGRR Title | Clarification of Reliability Performance Criteria |
| --- | --- | --- | --- |
| Date Posted |  | February 14, 2018 |  |
| Requested Resolution |  | Normal |  |
| Planning Guide Sections Requiring Revision |  | 4.1.1.2, Reliability Performance Criteria |  |
| Related Documents Requiring Revision/Related Revision Requests |  | None |  |
| Revision Description |  | This Planning Guide Revision Request (PGRR) updates the reliability performance criteria by defining unavailability of a Direct Current Tie (DC Tie) as a new contingency. The PGRR also includes clarification of the voltage level of transformers referred to in the reliability performance criteria. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | DC Ties are currently modeled based on historic import/export patterns. However, flows over the DC Ties are driven by market forces beyond ERCOT’s control and it is possible that assumed imports may not materialize in future operation. Additionally, it is possible that a DC Tie experiences a momentary or extended Forced Outage. This PGRR allows planners to evaluate and plan for unavailability or Outage of DC Tie Resources or Load. |  |

| Sponsor |  |
| --- | --- |
| Name | Sandeep Borkar |
| E-mail Address | Sandeep.Borkar@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-6642 |
| Cell Number | 501-246-0147 |
| Market Segment | N/A |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brittney Albracht |
| E-Mail Address | Brittney.Albracht@ercot.com |
| Phone Number | 512-225-7027 |

Proposed Guide Language Revision

4.1.1.2	Reliability Performance Criteria

(1)	The following reliability performance criteria (summarized in Table 1, ERCOT-specific Reliability Performance Criteria, below) shall be applicable to planning analyses in the ERCOT Region:

(a)	With all Facilities in their normal state, following a common tower outage with or without a single line-to-ground fault, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.

(b)	With all Facilities in their normal state, following an outage of a DC Tie Resource or Load with or without a single line-to-ground fault, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.

(c)	With any single generating unit unavailable, followed by Manual System Adjustments, followed by a common tower outage or outage of a DC Tie Resource or Load with or without a single line-to-ground fault, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.

(d)	With any single transformer, with the primary and secondary terminal operated at  100 kV or above unavailable, followed by Manual System Adjustments, followed by a common tower outage, or the contingency loss of a single generating unit, transmission circuit, transformer, shunt device, FACTS device, or DC Tie Resource or Load with or without a single line-to-ground fault, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.  An operational solution may be planned on a permanent basis to resolve a performance deficiency under this condition.

(e)	With any single DC Tie Resource or Load unavailable, followed by Manual System Adjustments, followed by a common tower outage, or the contingency loss of a single generating unit, transmission circuit, transformer, shunt device, FACTS device, or DC Tie Resource or Load, with or without a single line-to-ground fault, all Facilities shall be within their applicable Ratings, the ERCOT System shall remain stable with no cascading or uncontrolled Islanding, and there shall be no non-consequential Load loss.  An operational solution may be planned on a permanent basis to resolve a performance deficiency under this condition.

| Initial Condition |  | Event | Facilities within Applicable Ratings and System Stable with No Cascading or Uncontrolled Outages | Non-consequential Load Loss Allowed |
| --- | --- | --- | --- | --- |
| 1 | Normal System | Common tower outage | Yes | No |
| 2 | Normal System | DC Tie Resource or Load outage | Yes | No |
| 3 | Unavailability of a generating unit, followed by Manual System Adjustments | Common tower outage or a DC Tie Resource or Load outage | Yes | No |
| 4 | Unavailability of a transformer with the primary and secondary terminal operated at 100 kV or above, followed by Manual System Adjustments | Common tower outage; or Contingency loss of one of the following: 1. Generating unit; 2. Transmission circuit; 3. Transformer; 4. Shunt device; 5. FACTS device; or 6. DC Tie Resource or Load | Yes | No |
| 5 | Unavailability of a DC Tie Resource or Load, followed by Manual System Adjustments | Common tower outage; or Contingency loss of one of the following: 1. Generating unit; 2. Transmission circuit; 3. Transformer; 4. Shunt device; 5. FACTS device; or 6. DC Tie Resource or Load | Yes | No |

Table 1: ERCOT-specific Reliability Performance Criteria

(2)	ERCOT and the TSPs shall endeavor to resolve any performance deficiencies as appropriate.  If a Transmission Facility improvement is required to meet the criteria in this Section 4.1.1.2, but the improvement cannot be implemented in time to resolve the performance deficiency, an interim solution may be used to resolve the deficiency until the improvement has been implemented.