## Slide 1
Southern Cross Transmission Directives
Ancillary Service Related
February 2018 OWG
ERCOT Staff

## Slide 2: Summary
Directives | Area | Working Group
Directive #9 - Ancillary Services | Issues related to MSSC and margin between min RRS procurement, Contingency Reserve requirements Issues related to study of frequency overshoot and LRs UFR setting to DWG | OWG (ROS)
 | Issues related to NSRS and Regulation Service | PDCWG (ROS)
 | Issues related to study of frequency overshoot and LRs UFR setting | DWG (ROS)

## Slide 3: Directive #9
ERCOT shall (a) evaluate what modifications to existing and additional ancillary services, if any, are necessary for the reliable interconnection of the Southern Cross DC tie, (b) implement any needed modifications to ancillary-services procurement, (c) recommend how the costs of such required ancillary services are to be allocated, and (d) certify to the Commission when it has completed these actions.
Issues & Corresponding Studies:
Most Severe Single Contingency (MSSC) OWG
  1375 MW or 2000 MW?
Non-Spin Reserve Service has a minimum floor based on MSSC from 6 am to 10 pm. OWG & PDCWG
  Reconcile the MSSC with existing Non-Spin floor for on-peak hours.
Margin between minimum Responsive Reserve Service (RRS) procurement (2300 MW) and minimum Contingency Reserve (MSSC based) requirement. OWG
  Examine if changing MSSC (i.e. min Contingency Reserve) will bring a corresponding need to change RRS floor.
October 11 PDCWG & November 17 OWG

## Slide 4: Background – Disturbance Control
NERC’s BAL-002 Standard requires ERCOT to determine ERCOT’s Most Severe Single Contingency (MSSC) and make preparations to have Contingency Reserve equal to, or greater than MSSC available for maintaining system reliability.
  BAL-002-2 beginning Jan 1, 2018 is now in effect.
  BAL-002-2 provides more clear guidance on definition of terms included in the standard. Hence this discussion will reference the terms as coined by BAL-002-2
MSSC is the Balancing Contingency Event that would result in the greatest loss of resource (MW) output.
Balancing Contingency Event is a single event that causes an unexpected change in ERCOT’s Frequency.
Notes: ,

## Slide 5: NERC Definitions - BAL-002-2
Most Severe Single Contingency (Effective 1/1/2018)
The Balancing Contingency Event, due to a single contingency identified using system models maintained within the Reserve Sharing Group (RSG) or a Balancing Authority’s area that is not part of a Reserve Sharing Group, that would result in the greatest loss (measured in MW) of resource output used by the RSG or a Balancing Authority that is not participating as a member of a RSG at the time of the event to meet Firm Demand and export obligation (excluding export obligation for which Contingency Reserve obligations are being met by the Sink Balancing Authority).
Balancing Contingency Event (Effective 1/1/2018)
Any single event described in Subsections (A), (B), or (C) below, or any series of such otherwise single events, with each separated from the next by one minute or less.
Sudden loss of generation:
  Due to
    unit tripping, or
    loss of generator Facility resulting in isolation of the generator from the Bulk Electric System or from the responsible entity’s System, or
    sudden unplanned outage of transmission Facility;
  And, that causes an unexpected change to the responsible entity’s ACE;
Sudden loss of an Import, due to forced outage of transmission equipment that causes an unexpected imbalance between generation and Demand on the Interconnection.
Sudden restoration of a Demand that was used as a resource that causes an unexpected change to the responsible entity’s ACE.

## Slide 6: Directive #9 – First Question
ERCOT’s current MSSC is 1375 MW.
To determine ERCOT’s MSSC, ERCOT seasonally reviews the Net Dependable Capability (NDC) for all Generation Resources (submitted in NDCRC) and NDC of all HVDC Tie imports.
Southern Cross is a bipole DC-Tie line that can import up-to 2000 MW. Will Southern Cross’ integration into ERCOT change ERCOT’s MSSC?

## Slide 7: Survey of Other ISOs
New England ISO
  MSSC is 2000MW
    Based on Quebec - New England HVDC, a bipole DC line, that can transfer up to 2000 MW.
California ISO
  MSSC is 2400 MW
    Based on Pacific DC Intertie, a bipole DC line, that can import up to 2400 MW into Cal-ISO’s grid.
Hydro Quebec
  MSSC is based on Hydro Unit ~1000 MW
    Methodology includes assessing import on DC Ties. DC Tie with IESO under special operational configuration can become HQ’s MSSC.

## Slide 8: Recommendation
Southern Cross DC Tie, a bipole DC line, can import up to 2000 MW into ERCOT.
ERCOT recommends that the loss of the bipole Southern Cross DC Tie is a credible contingency that qualifies as a single event for the purpose of defining a Balancing Contingency Event per the current BAL-002-2 standard.
Further, ERCOT recommends that upon Southern Cross DC Tie’s interconnection into the ERCOT grid, ERCOT’s MSSC be changed to 2000 MW.

## Slide 9: Appendix

## Slide 10: Directive #9 (cont’d)
ERCOT shall (a) evaluate what modifications to existing and additional ancillary services, if any, are necessary for the reliable interconnection of the Southern Cross DC tie, (b) implement any needed modifications to ancillary-services procurement, (c) recommend how the costs of such required ancillary services are to be allocated, and (d) certify to the Commission when it has completed these actions.
Issues & Corresponding Studies:
Impact on Regulation Service during DC-Tie ramps PDCWG
  Study the impact of DC-Tie ramps on Regulation, Non-Spin & RRS requirements
Study impact on Frequency due to forced outage of DC Tie while exporting, evaluate if new AS is needed to address the overshoot issue and review existing UFR settings on LRs. PDCWG, DWG & DSWG
  Study impact on system frequency of DC-Tie trip when exporting and evaluate if a new type of A/S product may be needed to arrest the resulting frequency overshoot.
  Evaluate the risk of & frequency of triggering Load Resources due to DC-Tie trips when importing. Examine if the under-frequency relay settings for Load Resources warrant a change.

## Slide 11: Reference Links
NERC Glossary
NERC BAL-002-1
NERC BAL-002-2
NERC FAC-011-3
ERCOT’s SOL Methodology
ERCOT’s Current Protocols

## Slide 12: BAL-002 Disturbance Control Standard
Requires ERCOT (the BA) to take actions (including deploying Contingency Reserve) to balance resources and demand and return the BA’s Area Control Error (ACE) to defined values within Contingency Event Recovery Period (15 minutes) following a Reportable Balancing Contingency Event.
Requires ERCOT to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than Most Severe Single Contingency available for maintaining system reliability.
Following a Reportable Balancing Contingency Event, requires ERCOT to restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period (up to 90 minutes).
Contingency Event Recovery Period (New) = Disturbance Recovery Period (Old)
Reportable Balancing Contingency Event (New) = Reportable Disturbance (Old)
Contingency Reserve Restoration Period (New, Old)
Notes: Contingency Event Recovery Period (New) = Disturbance Recovery Period (Old)
Reportable Balancing Contingency Event (New) = Reportable Disturbance (Old)
Contingency Reserve Restoration Period (New, Old)

## Slide 13: BAL-002 Disturbance Control Standard
Reportable Balancing Contingency Event (Effective 1/1/2018)
Any Balancing Contingency Event occurring within a one-minute interval of an initial sudden decline in ACE based on EMS scan rate data that results in a loss of MW output less than or equal to the Most Severe Single Contingency, and greater than or equal to the lesser amount of: (i) 80% of the Most Severe Single Contingency, or (ii) 800 MW (ERCOT). Prior to any given calendar quarter, the 80% threshold may be reduced by the responsible entity upon written notification to the Regional Entity.
Contingency Reserve (Effective 1/1/2018)
The provision of capacity that may be deployed by the Balancing Authority to respond to a Balancing Contingency Event and other contingency requirements (such as Energy Emergency Alerts as specified in the associated EOP standard). A Balancing Authority may include in its restoration of Contingency Reserve readiness to reduce Firm Demand and include it if, and only if, the Balancing Authority:
is experiencing a Reliability Coordinator declared Energy Emergency Alert level, and is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan.
is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan.

## Slide 14: Background – System Operating Limit
NERC’s FAC-011-3 requires ERCOT to have an System Operating Limits (SOL) Methodology that helps ERCOT determine SOLs that ensure transmission security both pre-contingency and following a single contingency.
  Transmission Security = transient, dynamic and voltage stability; all Facilities operate within their Facility Ratings and within their thermal, voltage and stability limits; and no cascading or uncontrolled separation will occur.
During Real Time Operations to assess for SOL exceedances, ERCOT conducts transmission security assessments for all modeled Credible Single Contingencies.
ERCOT’s Credible Single Contingency list include double-circuit i.e. multiple circuit contingencies.
Some of these multiple circuit contingencies may result in isolation of radially connected generation. These multiple circuit contingencies are solely for transmission security assessments and do not correlate to a list of single balancing events that are assessed as a part of ERCOT’s MSSC determination.
Notes: ,

## Slide 15: FAC-011-3 – Operating Limits Methodology
Operating Limits Methodology for the Operations Horizon
R2.2. Following the single Contingencies1 identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur.
  R2.2.1. Single line to ground or 3-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device.
  R2.2.2. Loss of any generator, line, transformer, or shunt device without a Fault.
  R2.2.3. Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system
  1The Contingencies identified in FAC-011 R2.2.1 through R2.2.3 are the minimum contingencies that must be studied but are not necessarily the only Contingencies that should be studied.
Notes: FAC-011-4 allows RC to define contingencies above & beyond the guidance as it currently stands.

## Slide 16: ERCOT Contingency Definition
Credible Single Contingency (NP Section 2)
The Forced Outage of any single Transmission Facility or, during a single fault, the Forced Outage of multiple Transmission Facilities (single fault multiple element);
The Forced Outage of a double-circuit transmission line in excess of 0.5 miles in length;
The Forced Outage of any single Generation Resource, and in the case of a Combined Cycle Train, the Forced Outage of the combustion turbine and the steam turbine if they cannot operate separately as provided in the Resource registration process; or
For transmission planning purposes, contingencies are defined in the Planning Guide.