## Slide 1
Far West Texas Dynamic Reactive Devices - ERCOT Independent Review
ERCOT Transmission Planning
Regional Planning Group
February 27, 2018

## Slide 2: Far West Texas Transmission Project in June Endorsed by ERCOT BOD in 2017
At the time, the endorsed project (“Option 2”) was found to be reliable for a 2022 projected Culberson Loop load of 596 MW.
The Odessa EHV-Riverton 345 kV line is expected to be in service in 2020.
Option 2 had several expansion alternatives that would allow it to meet a higher load demand.
Description | Option 2 | Option 3 (Option 2 + closing loop 345 kV circuit) | Option 4 (Option 3 + dynamic devices)
Culberson Loop Load Serving Capability | 717 | 917 | 1037

## Slide 3: Culberson Loop Load Forecast Since 2016
Confirmed load requests
Could be over 1,300 MW by 2022 with 300 MW potential additions
Chart: Culberson Loop Confirmed Load Requests
| 2018 | 2019 | 2020 | 2021 | 2022
Far West Texas Dynamic Reactives Project (December, 2017) | 484.3 | 647.4 | 733.5 | 761.6 | 789.7
Far West Texas Project 2 (February, 2018) | 580.2 | 775.4 | 893 | 964.4 | 1013.1
425
596
Projected in April, 2016
Projected in May, 2017

## Slide 4: Overview
Oncor submitted Far West Texas Dynamic Reactive Devices for Regional Planning Group review. This is a Tier 1 project that is estimated to cost $86 million.
  Proposed for 2019 timeframe
  Addresses load growth due to the oil and gas industry
  Reliability Issues
    Voltage Violation
    Voltage Collapse
  Provide Operational Flexibility

## Slide 5: Study Procedure
Voltage Stability and Dynamic Stability Analysis
  Study Case: 2017 DWG 2019 Summer Peak Flat Start
  Criteria: NERC TPL and ERCOT Planning Guides
Scenarios to be evaluated:
  Base Scenario for 2019, 2020, and 2021
  Zero Solar Scenario
    Same as study case but with 0 MW Solar dispatched in study region
  Sensitivities based on Planning Guide 3.1.3(4):
    Generator additions with Signed Interconnection Agreements but that DO NOT meet Planning Guide Section 6.9 criteria in study region at time of study will be added to the case

## Slide 6
?
Stakeholder Comments Also Welcomed Through:
rpg@ercot.com