## Slide 1: Far West Texas Project 2
Presentation to ERCOT Regional Planning Group
at Feb 27, 2018 Meeting
Austin, TX – MET Center
Brent Kawakami, PE
brent.kawakami@oncor.com
When any portion of this presentation is used as a reference, please include attribution to Oncor Electric Delivery Company LLC (Oncor) and include the date of the presentation.
Plans are subject to change due to factors including, but not limited to, load, generation, engineering, system protection and system topology.

## Slide 2: Far West Texas Projects History
Far West Texas Project
  Submitted to ERCOT RPG in Apr 2016
  Approved by ERCOT RPG in May 2017
  Approved by ERCOT Board of Directors in Jun 2017
Odessa EHV – Riverton 345 kV Line
  Component of approved Far West Texas Project
  Formal request to ERCOT for Critical Designation Status
  Approved by ERCOT Board of Directors Feb 20, 2018
  CCN expected to be filed at PUC in March 2018
Dynamic Reactive Devices Project
  Submitted to ERCOT RPG on Dec 15, 2017
  Expected in-service in 2019
  Immediate voltage support needs due to load increases
Far West Texas Project 2
  Submitted to ERCOT RPG on Feb 01, 2018
  Proposal to close the 345 kV loop, add autotransformer capacity, and new 138 kV lines
2

## Slide 3: FAR WEST TEXAS PROJECT (PROPOSED)
Yucca Dr
Sand Lake
RIVERTON
SOLSTICE
LYNX
ODESSA EHV
BAKERSFIELD
MOSS
345 kV LINE
345 kV AUTO
~
~

## Slide 4: FAR WEST TEXAS PROJECT (APPROVED)
Yucca Dr
Sand Lake
RIVERTON
SOLSTICE
ODESSA EHV
BAKERSFIELD
MOSS
345 kV LINE
345 kV AUTO
Notes: ERCOT indicated that the approved project could serve up to 717 MW

## Slide 5: FAR WEST TEXAS PROJECT 2 (PROPOSED)
Yucca Dr
Sand Lake
RIVERTON
SOLSTICE
ODESSA EHV
BAKERSFIELD
MOSS
345 kV LINE
138 kV LINE
345 kV AUTO
~
~
SAND LAKE

## Slide 6: Project Description
Close the 345 kV Loop
  Riverton – Sand Lake 345 kV Line
  Sand Lake – Solstice 345 kV Line
Moss – Riverton 345 kV Line (Second Circuit)
Sand Lake 345 kV Sw. Sta.
  (2) - 345/138 kV, 600 MVA Autotransformers
New 138 kV Lines
  Riverton – Owl Hills 138 kV Line
  Riverton – Kyle Ranch 138 kV Line
Estimated Cost: $194M

## Slide 7: Project Schematic

## Slide 8: Culberson Loop Projected Load Growth
 | 2018 | 2019 | 2020 | 2021 | 2022
Confirmed | 580 MW | 775 MW | 893 MW | 964 MW | 1013 MW
Potential | 670 MW | 984 MW | 1163 MW | 1292 MW | 1340 MW

## Slide 9: ERCOT Original FWTP Recommendations (May 2017)
Option 1 - (917 MW)
  New 345 kV line between Riverton – Sand Lake
  345/138 kV autotransformer at Sand Lake
  New 345 kV line between Sand Lake – Solstice (AEP)
Option 2 - (1037 MW)
  New 345 kV line between Riverton – Sand Lake
  345/138 kV autotransformer at Sand Lake
  New 345 kV line between Sand Lake – Solstice (AEP)
  200 MVAR Synchronous Condenser at Culberson
Close the Loop
Close the Loop + DRD
Current Total: 1013 MW
Potential Total: 1340 MW

## Slide 10: Base Case Analysis
Cases used
  SSWG 2023SUM (October 2017)
  DWG 2023SP (Spring 2017)
6 Contingencies with voltage collapse
15 Contingencies with low voltages along the Culberson Loop
Voltage collapse observed in dynamic simulations

## Slide 11: Loss of Radial 345 kV Line

## Slide 12: Final Recommendation
Closing the 345 kV Loop is recommended
The needs for the Far West DRDs remain after the 345 kV construction
  Due to load growth and post-contingency operating conditions