## Slide 1
Day-Ahead Market OD 1/23/18
Carrie Bivens
Manager, Forward Markets
January 31, 2018

## Slide 2: What happened
Monday 01/22/18 (all times approximate)
10 am – 3 pm:
  DAM engine required more iterations than normal, and each iteration after the 3rd took a very long time to complete. Eventually it converged after the 9th iteration but the initial publishing function that prepares the data for the price validation process was unable to complete.
3 pm – 4 pm:
  Investigation pointed to a very large increase in binding constraints developed in the middle iterations causing some undetermined software issue. It was recognized that the data was corrupted in that first solution and the engine needed to be restarted.
4 pm:
  Restarted DAM with a reduced contingency set as a way to bring the number of developed constraints back down to a more reasonable number so as to not to trigger the software issue.
5:00 pm:
  ERCOT released a formal Market Notice about the reduced contingency set.
5:40 pm:
  The second run was normal and price validation completed with no concerns. ERCOT published the second run. DRUC was skipped due to the timeline.

## Slide 3: Why did ERCOT make that decision
We would have needed to abort DAM if a valid DAM solution was not produced soon. There were ongoing investigations as to the exact nature of the software issue. With no software fix on the horizon, the best chance due to the ticking clock was to reduce the contingency set in order to reduce the number of constraints developed.
  We disabled a subset of contingencies, about 700 -- all 69kV contingencies, with the exception of any that had been binding in real-time over the last 30 days, which ended up being only one. It was an action that could be completed quickly and met the requirements of the operating procedure.
Aborting DAM would be more disruptive to the market than disabling certain contingencies.
Operations needed to start preparing for the next Operating Day – next day studies, SASM, etc.

## Slide 4: Relevant references
  Protocol section 4.1.2(2):
  If, despite varying the timing or omitting any procedure, ERCOT is unable to execute the Day-Ahead process, ERCOT may abort all or part of the Day-Ahead process and require all schedules and trades to be submitted in the Adjustment Period.
  DAM Operating Procedure Manual:
  Reduced contingency set for performance issues - If significant performance issues are experienced, ERCOT has the ability to reduce contingencies from 4,500 to approximately 500 based on real-time operational experience. This would be done if significant performance issues experienced and would be noticed through a formal market notice communication.

## Slide 5: Results of further investigation
After completing a detailed post-event analysis by running multiple simulations, the team was able to track the jump in constraints developed to PTP bids sinking at a particular Resource Node (RN), where the RN is located on the low side of the step-up transformers, and also is located in an area with significant transmission outages on this Operating Day.
  Step-up transformers are not currently secured in DAM.
  If power flow divergence occurs, stability limit (SL) constraints are developed to create power flow limits for these transmission elements with large angular spread. Usually these are on elements that are monitor-only, but can also occur on secured elements depending on the commitment pattern established in initial iterations.
  Due to the topology, there was a cascading effect causing large number of additional constraints to be developed.
  There were as many as 146 MW of PTP bids sinking at the RN, flowing over two unsecured step-up transformers rated 5 MW and 11 MW respectively.
  A study case ran, based on the first run OD 1/23/18 savecase, with the two step-up transformers secured resulted in unique binding constraints decreasing from ~1,000 to ~250, no software issue triggered, and the case solving within normal time limits.

## Slide 6: Status of DAM software
After a sequence of trial and error in the post-event analysis, the team was also able to engineer operator actions that could help avoid the software issue.
  This includes multiple constraint flushing actions, which are usually not done past the 3rd iteration.
    Constraint flushing does not impact the final solution but DOES impact performance/run time
  This is not guaranteed to work in every case and performance is a concern. However, it allowed us to return to the full contingency set starting OD 01/25/18.
Long term, ERCOT proposes securing a subset (~5%) of step-up transformers in DAM.
The vendor is evaluating potential code changes but there are risks to allowing the application to handle an unreasonable number of constraints.
  We are also pursuing a number of enhancements to displays and logging to assist with faster monitoring/troubleshooting in the future

## Slide 7: Feedback
Concerns regarding our preferred approach of securing step-up transformers in DAM when the Resource Node is located on the low side?
Do stakeholders prefer a different method for reducing the contingency set in extraordinary cases?