## Slide 1
March 2018 OWG
ERCOT Staff
Southern Cross Transmission Directives
Ancillary Service Related: Directive #9

## Slide 2: Directive #9
ERCOT shall (a) evaluate what modifications to existing and additional ancillary services, if any, are necessary for the reliable interconnection of the Southern Cross DC tie, (b) implement any needed modifications to ancillary-services procurement, (c) recommend how the costs of such required ancillary services are to be allocated, and (d) certify to the Commission when it has completed these actions.
Issues & Corresponding Studies:
Most Severe Single Contingency (MSSC) OWG
  1375 MW or 2000 MW?

## Slide 3: Recap of Feb 2018 OWG
Proposed Recommendation
  Southern Cross DC Tie, a bipole DC line, can import up to 2000 MW into ERCOT.
  ERCOT recommends that the loss of the bipole Southern Cross DC Tie is a credible contingency that qualifies as a single event for the purpose of defining a Balancing Contingency Event per the current BAL-002-2 standard.
  Further, ERCOT recommends that upon interconnection of the Southern Cross DC Tie into the ERCOT grid, ERCOT’s MSSC be changed to 2000 MW.
Requested Follow Ups
  Identify the potential impacts (to Market Rules, Ancillary Services etc.) changing MSSC would have.
  Some more details on DC Ties in the various regions that ERCOT surveyed as a part of this effort.

## Slide 4: Implications of Changing MSSC
In the current Ancillary Service Methodology, when determining quantities for Non Spinning Reserve a floor that is equal to ERCOT’s MSSC is applied to on-peak hours (HE 7 thru HE 22).
  With MSSC change and current A/S Methodology there is a potential for increase in the quantity of Non Spinning Reserves for on-peak hours if Southern Cross DC Tie were to be operational.
In the current Nodal Protocols Section 6.5.9.4.2, Energy Emergency Alert Level 3 (EEA3) may be declared when PRC cannot be maintained above 1375 MW (ERCOT’s minimum Contingency Reserve).
  NERC’s EOP-011-1 has established this tie between EEA3 and MSSC.
  Current EEA Levels
    EEA 1: PRC < 2300 MW and cannot be recovered in 30 min
    EEA 2: PRC < 1750 MW and cannot be recovered in 30 min
    EEA 3: PRC cannot be maintained above 1375 MW
  With MSSC change, to maintain compliance with Nodal Protocols and NERC’s EOP-011-1, EEA3 and EEA2 level will need to be raised.
2000 MW
??
Notes: EEA2 also needs to be raised to be consistent with raising of EEA3 level to 2000 MW

## Slide 5: However…
If the imports over DC Ties into ERCOT were limited to be less than 1375 MW (ERCOT’s current MSSC), there would be no impact of integrating the Southern Cross DC Tie to ERCOT operations and planning practices.
  NE-ISO, NY-ISO & PJM impose similar import limit on the HVDC between them and Hydro-Quebec (Quebec - New England HVDC).
  Hydro-Quebec uses an import limit philosophy on the HVDC tie with IESO as well.
Note that, under this approach, ERCOT should have the flexibility to request more imports over the DC Tie under EEA conditions.

## Slide 6: Lastly…
In the long term, an approach that may be considered is having a dynamic MSSC (based on expected Real Time conditions). This may reduce some of the Non Spinning reserve impact while still allowing greater import over the DC ties.
  This will likely result in changes to Non Spinning reserve requirements closer to Real Time and will also require EEA levels to change dynamically with changing MSSC to maintain compliance with EOP-011.

## Slide 7: Next Steps
ERCOT will put together a whitepaper that summarizes this OWG discussion, the potential options that will aid the reliable interconnection of the Southern Cross DC tie and their associated impacts.
ERCOT will bring a draft of this whitepaper at the April 19, 2018 meeting for OWG’s review.

## Slide 8
Appendix: Other ISO Survey

## Slide 9: Survey of Other ISOs
New England ISO
  MSSC is 2000MW
    Based on Quebec - New England HVDC, a bipole DC line, that can transfer up to 2000 MW.
California ISO
  MSSC is 2400 MW
    Based on Pacific DC Intertie, a bipole DC line.
Hydro Quebec
  MSSC is based on Hydro Unit ~1000 MW
    Methodology includes assessing import on DC Ties. DC Tie with IESO under special operational configuration can become HQ’s MSSC.

## Slide 10: Survey of Other ISOs: ISO New England
MSSC is 2000 MW for ISO New England
  Based on Quebec - New England HVDC, a bipole DC line, that can transfer up to 2000 MW in import.
  NE-HQ Phase 2 interface has been in service since 1991 with a nominal transfer capability of 2000 MW in both directions.
  There are instances where real-time system conditions exist per the established procedures that allow the flow from Hydro Quebec to New England to reach the facility rating of 2000 MW. During all other times, import limits are imposed on the tie to ensure operational reliability criteria is not violated.
  The maximum export (New England to Hydro Quebec) has been limited to 1200 MW since the facility went into service.

## Slide 11: Survey of Other ISOs: CAISO
California ISO
  MSSC is 2400 MW
    Based on Pacific DC Intertie, a bipole DC line.
      This tie is nested within a single AC territory. Loss of the bipole tie may trigger a RAS the trips generation.
    Contingency Reserve Requirement Determination for Day Ahead and Real-Time Markets Day Ahead Market (link)
      DAM
        30 days of data, values averaged per hour.
        Begin with an adder to protect against RT PDCI awards.
        Cap the value at the OTC of the PDCI.
      Real Time
        adjustments made for incremental PDCI awards

## Slide 12: Survey of Other ISOs: Hydro Quebec
Hydro Quebec
  MSSC is based on Hydro Unit ~1000 MW (loss of 2 units at Churchill Falls)
      DC Tie with IESO under special operational configuration can become HQ’s MSSC. This DC Tie is composed of two back to back converter of 625 MW (TTC of 1250 MW in import). Most of the time HQ cannot lose both converters on a single contingency (to lose both on a bus bar fault) since it is designed that way. If QI is operated in a special configuration and both converters are lost, with importing power more than 1000 MW, it will be MSSC. However, this situation is really exceptional.
      DC Tie with NY-ISO: import is limited by two converters of 500 MW (TTC of 1000 MW in import). For the single contingency loses of a 735 kV Tie line with NY, this HVDC line will be lost; but its impact when importing will not be more than the MSSC set by loss of two Hydro Units.
      DC Tie with ISO-NE is a DC line composed of two converters 1250 MW (TTC of 2000 MW in import, because ISO-NE converter are 1000 MW each). Since HQ cannot lose both converters on a single contingency, the loss of one converter will not exceed the MSSC set by loss of two Hydro Units. For stability reason, Hydro Quebec is considering the loss of both converters but that will impact only transmission limits rather than contingency reserve requirement.

## Slide 13
Appendix: Related NERC Rules

## Slide 14: NERC Rules & MSSC
Governed by NERC’s BAL-002 Standard
  ERCOT is required to determine ERCOT’s Most Severe Single Contingency (MSSC) and make preparations to have Contingency Reserve equal to, or greater than MSSC available for maintaining system reliability.
  Following a Reportable Balancing Contingency Event, requires ERCOT to restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period (up to 90 minutes).
NERC’s EOP-011 Standard
  ERCOT is required to declare an Energy Emergency Alert (EEA) Level 3 if ERCOT is unable to meet minimum Contingency Reserve requirements.

## Slide 15: NERC Rules & MSSC
ERCOT’s Approach to comply with BAL-002, EOP-011
  To determine ERCOT’s MSSC, ERCOT seasonally reviews the Net Dependable Capability (NDC) for all Generation Resources (submitted in NDCRC) and NDC of all HVDC Tie imports.
  To meet the Contingency Reserve requirement, ERCOT procures Ancillary Services, sum total of which at any given delivery hour is greater than ERCOT’s current MSSC.
  In Real Time, ERCOT uses Physical Responsive Capability (PRC) to track ERCOT’s Contingency Reserve and ERCOT declares EEA3 when PRC cannot be maintained above 1375 MW.

## Slide 16: Reference Links
NERC Glossary
NERC BAL-002-1
NERC BAL-002-2
NERC FAC-011-3
NERC EOP-011-1
ERCOT’s SOL Methodology
ERCOT’s Current Protocols