## Index
RTP Scope Section Number | Input Assumption | Status | Date
Transmission Topology
3.1.1 | Start Cases | Final | 2018-03-20
3.1.5 | Temperatures used in Dynamic Rating Calculation | Final | 2018-03-20
3.1.2 | RPG Projects Backed out for lack of approval | Final | 2018-03-20
3.1.2 | Recently approved RPG projects | Final | 2018-03-20
3.1.2 | Model updates/corrections | In Progress | 2018-03-20
3.1.3 | Transmission & Generation Outages | Final | 2018-03-20
| CMP modeled in RTP | Not Started | N/A
Generation
3.2.1 | Generation Additions, Retirements and Mothballs | Updated | 2018-03-20
3.2.2 | Renewable generation dispatch | Final | 2018-03-20
3.2.3 | Switchable Generation | Updated | Tuesday, March 20, 2018
3.2.4 | DC tie modeling and dispatch | Final | 2018-03-20
3.2.5 | Reserve Requirements | Final | 2018-03-20
3.2.6 | Fuel Price assumptions | Reviewed | 2018-03-14
3.2.6 | Emission Cost Assumptions | Reviewed | 2018-03-14
Demand
3.3 | Load forecast (Reliability) 90/10 Forecast SSWG forecast Bounded Higher of calc RTP summer peak case forecast RTP Min load case forecast | In Progress
3.3 | Load forecast (economic) Weather year assumption | In progress
Other Studies
5.2.2 | Sensitivity Analysis | Not started | N/A

## Start Cases
Date Last Updated: | 2018-03-20 | Back
Status | Final
SSWG case version | 17SSWG Update 1 Final - October 12, 2017
On Peak Cases
17SSWG_2020_SUM1_U1_Final_10122017.raw
17SSWG_2021_SUM1_U1_Final_10122017.raw
17SSWG_2023_SUM1_U1_Final_10122017.raw
17SSWG_2024_SUM1_U1_Final_10122017.raw
Off peak case
17SSWG_2021_MIN_U1_Final_10122017.raw

## Temp. for Dynamic Ratings
Date Last Updated: | 2018-03-20 | Back
Status | Final
Weather Zone | 90th Percentile Temperature (degree F)
Coast | 102.44
East | 106.25
Far West | 110.405
North Central | 108.35
North | 109
South Central | 105.45
South | 103.98
West | 107.304

## RPG Projects Backed out
Date Last Updated: | 2018-03-20 |  | Back
Status | Final
Based on TPIT dated: | 2017-10-01
ERCOT Project Number | Project Title | Project Description | "from" Location | "to" Location | Associated Projects | Transmission Owner | TSP Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Service Level kV | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Phase Number | MOD Project Number
4274 | Navarro - Corsicana 69 kV Line | Upgrade existing line | Navarro | Corsicana |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R793 | 43600 | 69 | Tier 3 |  |  |  | 3468, 3475, 3479, 3480, 13468 | Y | 4648 | 4274
4825 | Crockett - Jewett 138kV Line | Upgrade existing line | Crockett | Jewett |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6061 | 43600 | 138 | Tier 3 |  |  |  | 3354, 3355, 3357, 3358, 3394 | Y | 5257 | 4825
5490 | Liggett - Hackberry 138 kV DCKT Line | Upgrade existing Liggett - Hackberry 138 KV Double Ckt Line | Liggett | Hackberry |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4222 | 43235 | 138 | Tier 3 |  |  |  | 1996, 1997, 2001, 2002, 2010, 11923, 15020, 15021, 2388, 15025, 15026, 15045, 15046 | Y | 6053 | 5490
4827 | Lufkin - Nacogdoches Southeast 138 kV Line | Upgrade existing line | Lufkin | Nacogdoches |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6062 | 45061 | 138 | Tier 3 |  |  |  | 3120, 3314, 3316, 3315, 3318 | Y | 5259 | 4827
5526 | Forney 345 kV Switching Station | Reconstruct existing 345 kV switching station | Forney |  |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4114 | 43600 | 345 | Tier 3 |  |  |  | 2467, 2433, 2437, 2478, 150189, 2438, 12438 | Y | 6078 | 5526
5436 | Morgan Creek - McDonald 138 kV Line | Upgrade existing line | Morgan Creek | McDonald Rd |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8360 | 45061 | 138 | Tier 3 |  |  |  | 1032, 1333 | Y | 5964 | 5436
5444 | Riverton-Solstice 345 kV Line | Establish new 345 kV line | Riverton | Solstice |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8355 | 45471 | 345 | Tier 1 | 42480 |  |  | 11084, 60404 | Y | 5972 | 5444
5975 | Watermill - Camp Wisdom 138kV DCKT Line | Rebuild existing Watermill - Camp Wisdom 138 kV DCKT Line | Watermill Sw. Sta. | Camp Wisdom |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4216 | 43235 | 138 | Tier 3 |  |  |  | 2430, 2988, 2989, 2990, 3068 | Y | 6515 | 5975
6273 | Saginaw 345/138 kV autotransformer | Install new autotransformer and construct new 345 kV Line at Saginaw | SAGINAW | HICKS |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5274 | 43600 | 345 | Tier 2 |  |  |  | 11957, 11958, 1436, 2081, 1957 | Y | 6828 | 6273
17TPIT0024 | Payne - Anna Switch 138 kV Line | Upgrade existing line | Payne | Anna Switch |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R938-E | 43449 | 138 | Tier 3 |  |  |  | 1713, 1748, 1754, 1758, 2374 | Y | 3386 | 3213
6290 | Plano Tennyson 345/138 kV Sw. Sta. | Rebuild existing switching station | Plano Tennyson |  |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4237 | 44696 | 138 | Tier 3 |  |  |  | 12545, 2359, 2361, 2522, 2523 | Y | 6844 | 6290
4822 | Bell County (BEC) - Gabriel (LCRA) 138 kV | Upgrade existing line | Bell County | Gabriel |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R2008 | 43966 | 138 | Tier 3 |  |  |  | 121, 132, 3640, 3688, 7346, 13640 | Y | 5253 | 4822
5627 | Hutto N- Gab, Hutto N - Hutto 138 kV Lines - Placeholder | Upgrade existing lines | Hutto North | Gabriel |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R2016 | 45061 | 138 | Tier 3 |  |  |  | 3664, 3666, 3667, 3668, 3669, 3677, 7346, 7528, 7532, 13666 | Y | 6182 | 5627
4834 | Cresson - Rocky Creek 138 kV Line | Construct new line | Cresson | Rocky Creek |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5228 | 43966 | 138 | Tier 2 |  |  |  | 1881, 2204 | Y | 5261 | 4834
5467 | Nacogdoches Southeast_HertyN 345kV Line | Establish a new 345kV Line | Nacogdoches Southeast | Herty North |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6075 | 43966 | 345 | Tier 2 |  |  |  | 3119, 3321 | Y | 5996 | 5467
5475 | Lufkin Sw. Sta. - Herty North Sw. Sta. 345 kV Line | Construct a new 345 kV Line from Lufkin Sw. Sta. to Herty North Sw. Sta. | Lufkin Sw. Sta | Herty North Sw. Sta. |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6077 | 43966 | 345 | Tier 2 |  |  |  | 3117, 3321 | Y | 6005 | 5475
5524 | Royse South 345/138 kV Switching Station | Establish new 345/138 kV switching station | South Royse |  |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4234 | 43966 | 345 | Tier 3 |  |  |  | 2469, 2470, 12471, 2467, 2471, 2478, 2702, 2710, 3103, 12702 | Y | 6076 | 5524
6291 | Royse Sw. Sta. - Farmersville Sw. Sta. 345 kV DCKT Line | Rebuild existing 345 kV Line | Royse | Farmersville |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4255 | 45061 | 345 | Tier 3 |  |  |  | 1685, 2461, 2478 | Y | 6845 | 6291
5981 | Shamburger North 345/138 kV Sw. Sta. | Establish Shamburger North 345/138 kV Sw. Sta. | Shamburger North |  |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6083 | 43967 | 345 | Tier 3 |  |  |  | 3217, 3223, 3226, 2470, 3103, 3201, 3206 | Y | 6521 | 5981
16TPIT0054 | Dialville - Palestine South 138 kV Line | Upgrade existing Dialville - Palestine South line section | Dialville | Palestine South |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6019 | 43966 | 138 | Tier 3 |  |  |  | 3111, 3160, 3271, 3110, 3296 | Y | 3283 | 3114
5752 | City of Brady to Heartland: Build 69 kV line | Construct new 69 kV line from City of Brady to Heartland | City of Brady | Heartland | 796 - 0981 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 3587 | 44712 | 69 | Tier 2 |  |  |  | 6383, 60386 | Y | 6317 | 5752

## Recently approved RPG project
Date Last Updated: | 2018-03-20 |  | Back | Back
Status | Final
Project Name | TDSP | Approve Date
IH20 SVC Project | TNMP | 2017-12-06
CenterPoint Energy-Freeport Master Plan Project | CNP | 2017-12-12
Pecos County Transmission Project, Option 1 | AEP | 2018-03-05

## Model updates & corrections
Date Last Updated: | 2018-03-20 |  | Back
Status | In Progress
Model Corrections/Updates Made to the 2017 RTP Cases
Transmission Changes | TO | Case | [5 empty] | Comments
|  | 2019 SUM | 2021 MIN | 2020 SUM | 2022 SUM | 2023 SUM | 2024 SUM
Generation Changes | TO | Case | [5 empty] | Comments
|  | 2019 SUM | 2021 MIN | 2020 SUM | 2022 SUM | 2023 SUM | 2024 SUM
Load Changes | TO | Case | [5 empty] | Comments
|  | 2019 SUM | 2021 MIN | 2020 SUM | 2022 SUM | 2023 SUM | 2024 SUM
Bus Voltage Changes | TO | Case | [5 empty] | Comments
|  | 2019 SUM | 2021 MIN | 2020 SUM | 2022 SUM | 2023 SUM | 2024 SUM
Capacitor Bank Changes | TO | Case | [5 empty] | Comments
|  | 2019 SUM | 2021 MIN | 2020 SUM | 2022 SUM | 2023 SUM | 2024 SUM
Phase Shifters | TO | Case | [5 empty] | Comments
|  | 2019 SUM | 2021 MIN | 2020 SUM | 2022 SUM | 2023 SUM | 2024 SUM
8183 Thomaston | AEP | X | X | X | X | X | X | Control is normally on in normal operation
8255 Hamilton Road | AEP | X | X | X | X | X | X | Control is normally on in normal operation
8909 North Laredo Switch | AEP | X | X | X | X | X | X | Control is normally on in normal operation
85007 Nelson Sharpe | AEP | X | X | X | X | X | X | Control is normally on in normal operation

## Transmission & Gen Outages
Date Last Updated: | 2018-03-20 | Back
Status | Final
No transmission or generation outages with a duration longer than 6 months were available at the time of study

## CMP
Date Last Updated: | N/A |  |  |  |  | Back
Status | Not Started
Constraint Management Plans Modeled in 2017 Regional Transmission Plan Studies
CMP Location and Description | TO | Reliability
|  | 2019 SUM | 2020 MIN | 2020 SUM | 2022 SUM | 2023 SUM
|  | N-1 | N-1 | N-1 | N-1 | N-1

## Gen add, ret. and mothball
Date Last Updated: | 2018-03-20 |  |  |  |  | Back
Status | Updated
Based on GIS report dated: | 2018-02-01
New generators that met PG 6.9 requirements
GINR Reference Number | Project Name | County | Projected Date | Fuel | MW For Grid | Changes From Last Report | Meets Section 6.9 Requirements (1)(b) through (1)(d) | 2019 | 2020 | 2021MIN | 2021 | 2022 | 2023 | 2024 | Comments
12INR0059b | HOVEY (Barilla Solar 1B) | Pecos | 2017-12-01 | Solar | 7 |  | Yes | X | X | X | X | X | X | X
14INR0031 | BTE (Baytown Chiller) | Chambers | 2018-01-01 | Gas | 270 |  | Yes | X | X | X | X | X | X | X
15INR0061 | LASSO | Brewster | 2018-01-01 | Solar | 50 |  | Yes | X | X | X | X | X | X | X
15INR0064 | NBOHR (BearKat Wind A) | Glasscock | 2018-01-01 | Wind | 197 | Projected Date | Yes | X | X | X | X | X | X | X
16INR0023 | LMESASLR (BNB Lamesa Solar 1) | Dawson | 2018-01-01 | Solar | 102 | Projected Date | Yes | X | X | X | X | X | X | X
13INR0049 | FEGC | Harris | 2018-02-01 | Gas | 129 | Projected Date | Yes | X | X | X | X | X | X | X
15INR0045 | RIGGINS | Pecos | 2018-02-01 | Solar | 150 |  | Yes | X | X | X | X | X | X | X
16INR0054 | NA | Harris | 2018-02-01 | Gas | 12 |  | Yes | X | X | X | X | X | X | X
17INR0022 | MIRAGE | Harris | 2018-02-01 | Gas | 11 |  | Yes | X | X | X | - | - | - | - | Generator will go offline after 2020
15INR0082 | FTWIND (Flat Top Wind I) | Comanche | 2018-03-01 | Wind | 200 |  | Yes | X | X | X | X | X | X | X
16INR0087 | RTS Wind Project | McCulloch | 2018-03-01 | Wind | 160 | Project Name | Yes | X | X | X | X | X | X | X
16INR0091 | HICKMAN | Reagan | 2018-04-01 | Wind | 300 | Projected Date | Yes | X | X | X | X | X | X | X
16INR0065 | CASL_GAP (Castle Gap Solar) | Upton | 2018-06-01 | Solar | 180 |  | Yes | X | X | X | X | X | X | X
16INR0086 | Cactus Flats Wind | Concho | 2018-06-01 | Wind | 148 | MW For Grid | Yes | X | X | X | X | X | X | X
18INR0013 | Denton Energy Center | Denton | 2018-07-01 | Gas | 226 |  | Yes | X | X | X | X | X | X | X
13INR0010a | Mariah Del Este | Parmer | 2018-09-01 | Wind | 152 |  | Yes | X | X | X | X | X | X | X
16INR0076 | Brazoria Energy G |  | 2018-10-01 | Gas | 90 |  | Yes | X | X | X | X | X | X | X
18INR0025 | Tahoka Wind | Lynn | 2018-10-01 | WIND | 505 | SFS | Yes | X | X | X | X | X | X | X
13INR0010c | Mariah Del Sur | Parmer | 2018-12-01 | Wind | 218 |  | Yes | X | X | X | X | X | X | X
14INR0023b | LHORN (Longhorn South W) | Briscoe | 2018-12-01 | Wind | 160 |  | Yes | X | X | X | X | X | X | X
14INR0030c | Panhandle Wind 3 | Carson | 2018-12-01 | Wind | 248 |  | Yes | X | X | X | X | X | X | X
14INR0038 | BAC | Galveston | 2018-12-01 | Gas | 390 | Projected Date | Yes | X | X | X | X | X | X | X
15INR0035 | Stella 1 Wind |  | 2018-12-01 | Wind | 201 |  | Yes | X | X | X | X | X | X | X
15INR0064b | BearKat Wind B | Glasscock | 2018-12-01 | Wind | 162 | Projected Date | Yes | X | X | X | X | X | X | X
16INR0023b | Lamesa Solar B (Phase II) | Dawson | 2018-12-01 | Solar | 50 | Projected Date, SFS | Yes | X | X | X | X | X | X | X
16INR0037c | Pumpkin Farm Wind | Floyd | 2018-12-01 | Wind | 281 |  | Yes | X | X | X | X | X | X | X
16INR0112 | Loma Pinta Wind | La Salle | 2018-12-01 | Wind | 200 | NEW | Yes | X | X | X | X | X | X | X
16INR0114 | Upton Solar | Upton | 2018-12-01 | Solar | 102 |  | Yes | X | X | X | X | X | X | X
16INR0115 | Waymark Solar | Pecos | 2018-12-01 | Solar | 182 |  | Yes | X | X | X | X | X | X | X
17INR0005 | Cabezon Wind | Starr | 2018-12-01 | Wind | 238 | Project Name, SFS | Yes | X | X | X | X | X | X | X
17INR0020a | RE Maplewood 2a Solar | Pecos | 2018-12-01 | Solar | 100 |  | Yes | X | X | X | X | X | X | X
15INR0059 | Emerald Grove Solar | Pecos | 2019-01-01 | Solar | 108 | Project Name | Yes | X | X | X | X | X | X | X
11INR0054 | Midway Wind | San Patricio | 2019-03-01 | Wind | 163 |  | Yes | X | X | X | X | X | X | X
11INR0062 | Patriot Wind | Nueces | 2019-04-01 | Wind | 180 | Projected Date | Yes | X | X | X | X | X | X | X
17INR0027b | Coyote Wind | Scurry | 2019-05-01 | Wind | 242 |  | Yes | X | X | X | X | X | X | X
16INR0003 | LEVEE (Freeport LNG) | Brazoria | 2019-06-01 | Gas | 11 |  | Yes | X | X | X | X | X | X | X
16INR0062b | Lockett Wind | Wilbarger | 2019-06-01 | Wind | 184 |  | Yes | X | X | X | X | X | X | X
18INR0043 | Edmondson Ranch Wind | Glasscock | 2019-09-01 | Wind | 292 | SFS | Yes | X | X | X | X | X | X | X
13INR0038 | Wildrose Wind | Swisher | 2019-10-01 | Wind | 212 |  | Yes | - | X | X | X | X | X | X
12INR0060 | Infinity Live Oak Wind | Schleicher | 2019-12-01 | Wind | 200 |  | Yes | - | X | X | X | X | X | X
13INR0005c | Grandview W 3 | Carson | 2019-12-01 | Wind | 188 |  | Yes | - | X | X | X | X | X | X
14INR0044 | West of Pecos Solar | Reeves | 2019-12-01 | Solar | 100 | Projected Date | Yes | - | X | X | X | X | X | X
14INR0045a | Torrecillas Wind A | Webb | 2019-12-01 | Wind | 200 |  | Yes | - | X | X | X | X | X | X
14INR0045b | Torrecillas Wind B | Webb | 2019-12-01 | Wind | 200 |  | Yes | - | X | X | X | X | X | X
17INR0020b | RE Maplewood 2b Solar | Pecos | 2019-12-01 | Solar | 100 |  | Yes | - | X | X | X | X | X | X
17INR0020c | RE Maplewood 2c Solar | Pecos | 2019-12-01 | Solar | 100 |  | Yes | - | X | X | X | X | X | X
17INR0020d | RE Maplewood 2d Solar | Pecos | 2020-12-01 | Solar | 100 |  | Yes | - | - | X | X | X | X | X
17INR0020e | RE Maplewood 2e Solar | Pecos | 2020-12-01 | Solar | 100 |  | Yes | - | - | X | X | X | X | X
Retired units
Unit Name | MW For Grid | 2019 | 2020 | 2021MIN | 2021 | 2022 | 2023 | 2024 | Comments
PEARSALL (PEARSALL_PEARS_1, PEARSALL_PEARS_2, PEARSALL_PEARS_3) | 61 | X | X | X | X | X | X | X | Per Dec 2017 CDR: Since 8/1/2017
GREENS BAYOU STG U5 (GBY_GBY_5) | 371 | X | X | X | X | X | X | X | Per Dec 2017 CDR: As of 12/31/2017
S R BERTRON (SRB_SRBGT_2, SRB_SRB_G3, SRB_SRB_G4) | 420 | X | X | X | X | X | X | X | Per Dec 2017 CDR: As of 12/31/2017
S R BERTRON U1 & U2 (SRB_SRB_G1, SRB_SRB_G2) | 292 | X | X | X | X | X | X | X | Per Dec 2017 CDR: Since 5/15/2013
MONTICELLO (MNSES_UNIT1, MNSES_UNIT2, MNSES_UNIT3) | 1865 | X | X | X | X | X | X | X | Per Dec 2017 CDR: As of 1/4/2018
SANDOW (SDSES_UNIT4, SD5SES_UNIT5) | 1200 | X | X | X | X | X | X | X | Per Dec 2017 CDR: As of 1/11/2018
BIG BROWN (BBSES_UNIT1, BBSES_UNIT2) | 1208 | X | X | X | X | X | X | X | Per Dec 2017 CDR: As of 2/12/2018
Mothballed units
Unit Name | MW For Grid | 2019 | 2020 | 2021MIN | 2021 | 2022 | 2023 | 2024 | Comments
B M DAVIS STG U1 (B_DAVIS_B_DAVIG1) | 330 | X | X | X | X | X | X | X | Per Dec 2017 CDR: On 12/31/2017
SPENCER (STG U4, STG U5) | 118 | X | X | X | X | X | X | X | Per Dec 2017 CDR: As of 1/3/2018
GIBBONS CREEK U1 (GIBCRK_GIB_CRG1) | 470 | [7 empty] | Per Dec 2017 CDR: Return to service between May-June 2018
J T DEELY U1 & U2 | 840 | X | X | X | X | X | X | X | Per Dec 2017 CDR: As of 12/31/2018

## Renewable Generation Dispatch
Date Last Updated: | 2018-03-20 | Back
Status | Final
Solar
Information obtained from the spreadsheet "CDR Summer PeakAveSolarCapacityPercentages 11-20-2017" posted on the ERCOT website under Resource Adequacy.
* SOLARPEAKPCT Values | 75%
* The methodology for calculating SOLARPEAKPCT values is outlined in ERCOT Protocol Section 3.2.6.2.2. See: http://www.ercot.com/content/wcm/current_guides/53528/03_030116_Nodal.doc
Wind
Information obtained from the spreadsheet "CDR Summer PeakAveWindCapacityPercentages 11-20-2017" posted on the ERCOT website under Resource Adequacy.
Outside Study Region
WINDPEAKPCT Values *
Summer, Non-Coastal | Summer, Coastal
14% | 59%
* The methodology for calculating WINDPEAKPCT values is outlined in ERCOT Protocol Section 3.2.6.2.2. See: http://www.ercot.com/content/wcm/current_guides/53528/03-110117_Nodal.doc
Inside Study Region
Average Capacity Factor (15th Percentile)
WZ_FAR_WEST | 4.36%
WZ_NORTH | 5.57%
WZ_NORTH_CENTRAL | 0.74%
WZ_SOUTH_CENTRAL | 1.1%
WZ_SOUTHERN | 18.67%
WZ_WEST | 2.33%
Hydro
Unit specific generation MW dispatch modeled based on historical dispatch levels during the top 20 load hours of the last three years.
AMI_AMISTAG1 (H1) | 18.65
AMI_AMISTAG2 (H2) | 28.7
AUS_AUSTING1 (H1) | 8
AUS_AUSTING1 (H2) | 8.5017
BUC_BUCHANG1 (H1) | 16
BUC_BUCHANG2 (H2) | 16
BUC_BUCHANG3 (H3) | 17
CAN_CANYHYG1 (H1) | 0
CAN_CANYHYG1 (H2) | 0
DND_DENISOG1 (H1) | 40
DND_DENISOG2 (H2) | 40
EA_EAGLE_HY1 (H1) | 0
EA_EAGLE_HY1 (H2) | 0
EA_EAGLE_HY1 (H3) | 0
FAL_FALCONG1 (H1) | 7.55
FAL_FALCONG2 (H2) | 8.3187
FAL_FALCONG3 (H3) | 8.65
INKS_INKS_G1 (H1) | 13.37
MAR_MARBFAG1 (H1) | 19.7455
MAR_MARBFAG2 (H2) | 19.3043
MAR_MARSFOG1 (H1) | 35.5667
MAR_MARSFOG2 (H2) | 35.8158
MAR_MARSFOG3 (H3) | 28.7556
WIR_WIRTZ_G1 (H1) | 28.78
WIR_WIRTZ_G2 (H2) | 29
WND_WHITNEY1 (H1) | 19.8967
WND_WHITNEY2 (H2) | 13.0217
Wind (Min Case)
Non-Coastal | Coastal
52.33% | 25.09%

## Switchable Generation
Date Last Updated: | Tuesday, March 20, 2018 |  |  |  |  | Back
Status | Updated
Operational Resources (Switchable)
UNIT NAME | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027
ANTELOPE IC 1 | ANTLP_G1 | HALE | GAS | WEST | 2016 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
ANTELOPE IC 2 | ANTLP_G2 | HALE | GAS | WEST | 2016 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
ANTELOPE IC 3 | ANTLP_G3 | HALE | GAS | WEST | 2016 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
ELK STATION CTG 1 | AEEC_ELK_1 | HALE | GAS | WEST | 2016 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
ELK STATION CTG 2 | AEEC_ELK_2 | HALE | GAS | WEST | 2016 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
TENASKA FRONTIER STATION CTG 1 | FTR_FTR_G1 | GRIMES | GAS | NORTH | 2000 | 160 | 160 | 160 | - | - | - | - | - | - | -
TENASKA FRONTIER STATION CTG 2 | FTR_FTR_G2 | GRIMES | GAS | NORTH | 2000 | 160 | 160 | 160 | - | - | - | - | - | - | -
Switchable Capacity Unavailable to ERCOT | SWITCH_UNAVAIL |  | GAS |  |  | -843.8 | -843.8 | -843.8 | -523.8 | -543.8 | -543.8 | -543.8 | -543.8 | -543.8 | -543.8
*Note: the Tensaka Frontier is going to keep 300 MW switched out but it won’t be necessarily from particular units.

## DC Tie modeling & dispatch
Date Last Updated: | 2018-03-20 |  | Back
Status | Final
Reliability Analysis
DC Tie dispatch - Summer peak conditions (MW)
DC_E | 600 | Import
DC_N | 220 | Import
DC_L* | 100 | Export
DC_R* | 300 | Export
DC_S* | 30 | Export
* In the events that thermal overloads are resolved by curtialing the DC Tie exports, the events and the curtailed amounts will be documented.
Economic Analysis
DC Tie dispatch - 8760-hour assumptions
DC_E | Import only | Modeled as a pseudo-generator with characteristics developed based on historical operational data
DC_N | Import + export | Modeled as a pseudo-generator and a demand profile with characteristics developed based on historical operational data.
DC_L* | Export only | Demand profile developed based on the historical operational data
DC_R* | Export only
DC_S* | Export only

## Reserve Requirement
Date Last Updated: | 2018-03-20 | Back
Status | Final
Reliabity Cases | 2800 MW
The reserve requirements used in the reliability models account for the outage of ERCOT's two largest units as well as the increased losses observed during such an G-1 & N-1 outage.
Economic Analysis | 1622 MW
The reserve requirements used in the economic models are based on a review of ERCOT’s 2018 Responsive Reserve and Regulation Up requirements. Note that the value is less than 2800 MW since the MW contribution of load resources is not an input into the economic model.

## Fuel Price Assumptions
Date Last Updated: | 2018-03-14 |  |  |  |  | Back
Status | Reviewed
Source | EIA 2018 AEO High Oil and Gas Resource and Technology Case
Natural Gas Price Forecast ($/MMBtu)
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Average
2018 | 3.08 | 3.05 | 3.01 | 2.86 | 2.87 | 2.88 | 2.9 | 2.92 | 2.92 | 2.94 | 3.02 | 3.14 | 2.9658
2019 | 3.37 | 3.35 | 3.3 | 3.15 | 3.15 | 3.15 | 3.18 | 3.2 | 3.2 | 3.22 | 3.31 | 3.44 | 3.2517
2020 | 3.68 | 3.66 | 3.6 | 3.43 | 3.44 | 3.45 | 3.47 | 3.51 | 3.51 | 3.52 | 3.61 | 3.75 | 3.5525
2021 | 3.48 | 3.46 | 3.41 | 3.25 | 3.26 | 3.27 | 3.29 | 3.32 | 3.32 | 3.33 | 3.42 | 3.55 | 3.3633
2022 | 3.38 | 3.35 | 3.3 | 3.14 | 3.15 | 3.16 | 3.19 | 3.21 | 3.21 | 3.23 | 3.31 | 3.44 | 3.2558
2023 | 3.44 | 3.41 | 3.37 | 3.21 | 3.22 | 3.23 | 3.24 | 3.27 | 3.27 | 3.29 | 3.38 | 3.51 | 3.32
2024 | 3.58 | 3.55 | 3.5 | 3.34 | 3.35 | 3.35 | 3.38 | 3.4 | 3.4 | 3.42 | 3.51 | 3.65 | 3.4525

## Emission Cost Assumptions
Date Last Updated: | 2018-03-14 | Back
Status | Reviewed
Source | EPA website
Emission | $/ton
NOx (Seasonal) | 200
NOx (Annual) | 0
SO2 | 0
CO2 | 0

## Reliability case-Load Forecast
Date Last Updated | 2018-03-20 |  |  |  |  | Back
Status | In Progress
SSWG Load in 17SSWG dated 10/12/2017 less Self-Served (MW)
Year | Coast | East | Far West | North | North Central | South Central | Southern | West | NCP Total
2019 | 22958.82 | 2967.43 | 4775.05 | 1678.54 | 25510.83 | 13456.67 | 6070.96 | 2288.64 | 79706.94
2020 | 23601.02 | 3014.97 | 5119.25 | 1706.41 | 26000.65 | 13699.2 | 6533.2 | 2304.42 | 81979.12
2021 | 23627.81 | 3024.46 | 5337.64 | 1714.02 | 26500.87 | 13939.8 | 6731.41 | 2324.35 | 83200.36
2022 | 23774.38 | 3068.06 | 5494.55 | 1712.08 | 26735.56 | 14146.16 | 6830.61 | 2337.09 | 84098.49
2023 | 23913.62 | 3093.33 | 5764.83 | 1723.04 | 27127.34 | 14385.36 | 6928.02 | 2363.26 | 85298.8
2024 | 24064.53 | 3116.63 | 5890.18 | 1735.55 | 27423.1 | 14606.03 | 7023.84 | 2379.05 | 86238.91
ERCOT 90th Percentile Load forecast for RTP (MW)
Year | Coast | East | Far West | North | North Central | South Central | Southern | West | NCP Total
2019 | 21678.3461 | 2770.5363 | 3549.2444 | 1460.7261 | 26363.9497 | 13016.9054 | 6036.6041 | 1951.9431 | 76828.2551
2020 | 22102.5013 | 2789.4063 | 3840.1405 | 1463.9426 | 26621.7731 | 13142.9464 | 6175.4019 | 1978.3188 | 78114.4309
2021 | 22418.5275 | 2808.5689 | 4139.2481 | 1467.1587 | 26887.6166 | 13269.3149 | 6317.4905 | 2005.5313 | 79313.4565
2022 | 22791.406 | 2831.3799 | 4471.0534 | 1471.275 | 27194.3782 | 13417.1612 | 6485.3074 | 2034.4481 | 80696.4093
2023 | 23159.5318 | 2853.2676 | 4801.672 | 1475.1755 | 27489.642 | 13564.336 | 6648.6934 | 2063.5414 | 82055.8597
2024 | 23482.376 | 2871.2928 | 5099.8361 | 1478.1852 | 27746.2601 | 13695.1354 | 6790.9017 | 2090.9087 | 83254.8961
2018 RTP final load forecast based on on 5% boundary threshold (MW)
Year | Coast | East | Far West | North | North Central | South Central | Southern | West | Total
2019
2020
2021
2022
2023
2024
2018 RTP final load forecast for Off-Peak Case (MW) (based on 2021 SSWG Min Case)
Year | Coast | East | Far West | North | North Central | South Central | Southern | West | Total
2021

## Economic Case-Load Forecast
Date Last Updated: | 2018-03-15 |  |  |  |  | Back
Status | In progress
Load forecast (economic)
Weather year assumption | Base: 2009, Other: 2007 and 2010
Demands (MW) in Uplan
Annual Peaks
Year | Coast | East | Far West | North | North Central | South Central | Southern | West | FLAT (with LNG)
2020 (2007) | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
2020 (2009) | 16124 | 2251 | 1407 | 1240 | 24294 | 11900 | 4511 | 1589 | 16145
2020 (2010) | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
2023 (2007) | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
2023 (2009) | 16911 | 2311 | 2223 | 1248 | 24470 | 12393 | 4803 | 1672 | 17036
2023 (2010) | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
Notes
1. Annual peak loads for each of the weather zones in table above include the self-served loads but not losses.
2. Note that the 2009 weather scenario is the base weather scenario used as the starting point in the economic analysis. If needed, there are also the 2007 and 2010 weather scenarios.

## Sensitivity Analysis
Date Last Updated: | N/A | Back
Status | Not started