## Sheet1
FIS Phase Data Elements (With TSP Feedback) |  | This is for WIND IRR Units only! | Last Modified: 3/24/2018
RARF Tab | Field Name | Detailed Description | SCREENING STUDY | STEADY STATE | SHORT CIRCUIT | FACILITY | STABILITY / DYNAMICS | Comments (Centerpoint) | Comments (AEP) | Comments (ONCOR)
General and Site | Project Name | Name of the Project. This will be required in the new GINR application. This is NOT the Site Code, as that will be required later. | X | X | X | X | X
General and Site | County: | County associated with the physical street address of the plant site. | X | X | X | X | X
General and Site | Printed Name: | Enter the Primary Contact person who can address ERCOT questions regarding Resource Registration submittal. Enter the contact's name, title, phone number, and email address. | X | X | X | X | X
General and Site | Title: | Enter the Title of the Primary Contact | X | X | X | X | X
General and Site | Phone Number: | Enter the Phone Number for the Primary Contact | X | X | X | X | X
General and Site | E-mail Address: | Enter the E-mail Address for the Primary Contact | X | X | X | X | X
Private Network - Site | Private Network? (Y/N) | Indicate if the site is a Private Use Network as defined in the Protocol Section 2. | X | X | X | X | X
Private Network - NEW FIELD | List maximum NET load for Private Network | List maximum NET load for Private Network (This is the minimum generation combined with maximum load for the site). Load drawing from bulk transmission system. | X | X | X | X | X
Private Network - NEW FIELD | List maximum NET generation for Private Network | List maximum NET generation for Private Network (This is the maximum generation combined with minimum load for the site). MW injecting into bulk transmission system. | X | X | X | X | X
Station | Latitude of Center of Station | The geographic coordinate that specifies the north-south position of the station provided in decimal degrees | X | X | X | X | X
Station | Longitude of Center of Station | The geographic coordinate that specifies the east-west position of the station provided in decimal degrees | X | X | X | X | X
Station | ONE LINE (POI) | Simple POI One-Line Diagram | X | X | X | X | X
Station - NEW FIELD | .kmz file | Site KMZ file with coordinates on Google Earth | X | X | X | X | X
Unit Information | Commercial Operations Date | Enter the unit's planned Commercial Operations Date. After the unit completes operational performance testing, this field should be updated by the RE with the actual Commercial Operations Date. | X | X | X | X | X
Unit Information | POI Description | POI Description | X | X | X | X | X
Unit Information | Voltage Level | Enter the nominal voltage level at the Point of Interconnection (e.g. 69kV, 138kV, 345kV). If you need assistance in determining the corresponding Voltage Level, please consult your TDSP, or ERCOT. | X | X | X | X | X
Unit Information | Primary Fuel Type | WND -- Wind | X | X | X | X | X
Unit Information | Physical Unit Type | WT -- Wind Turbine | X | X | X | X | X
Unit Information | Real Power Rating | Manufacturer designed MW at rated power factor (gross). | X | X | X | X | X
Capacitor - NEW FIELD | Description of Change | Do you have any reactive equipment? (Yes/No) |  | X | X | X | X | Why this Capacitor tab is needed since the capacitor banks are static device and cannot provide dynamic VAR support to meet the requirement?
Capacitor and Reactor Data | Device Name | Capacitor or Reactor name as provided in the ERCOT model, which must meet the character limitation of the system. |  | X | X | X | X
Capacitor and Reactor Data | Capacitor Or Reactor | Select whether this device is a capacitor (C) or reactor (R) |  | X | X | X | X
Capacitor and Reactor Data | Nominal Mvar | Rated MVAr rating of a capacitor or reactor (name plate data) negative MVAr for reactors and positive MVArs for capacitors |  | X | X | X | X
Capacitor and Reactor Data | Voltage Level kV | Enter voltage level of this capacitor or reactor |  | X | X | X | X
Capacitor and Reactor Data | Automatic Voltage Regulation | Select Y or N whether this device has automatic voltage regulation |  | X | X | X | X
Capacitor and Reactor Data | Voltage Level of Busbar being regulated | Enter voltage of busbar where device is located |  | X | X | X | X
Capacitor and Reactor Data | Desired Regulating Voltage | Desired Regulating Voltage |  | X | X | X | X
Capacitor and Reactor Data | Minimum Regulating Voltage | Lower limit of voltage specified in the voltage regulation scheme |  | X | X | X | X
Capacitor and Reactor Data | Maximum Regulating Voltage | Higher limit of voltage specified in the voltage regulation scheme |  | X | X | X | X
General and Site | Site In-Service (Backfeed) Date: | Date is the date when site was (or is planned to be) commissioned. Entered once initially for the Screening Study. Updated once for FIS. Updated once for the Full Registration. Updated finally for the site commissioning. |  | X | X | X | X | Energization Date
Line Data | Resistance in p.u. (100 MVA Base) | Resistance in p.u. (100 MVA Base) |  | X | X | X | X
Line Data | Reactance in p.u. (100 MVA Base) | Reactance in p.u. (100 MVA Base) |  | X | X | X | X
Line Data | Charging Susceptance in P.u. (100 MVA Base) | Charging Susceptance in p.u. (100 MVA Base) |  | X | X | X | X
Line Data | Segment Length | Length of this line segment between the TO station and the FROM station (circuit miles) |  | X | X | X | X
Line Temperature | Continuous Rating | The continuous MVA rating, including substation terminal equipment in series with the line, at the applicable ambient temperature. The Transmission Element can operate at this rating indefinitely without damage, or violation of NESC clearances. |  | X | X | X | X
Line Temperature | 2-hr Emergency Rating | The two-hour MVA rating, including substation terminal equipment in series with the line, at the applicable ambient temperature. The Transmission Element can operate at this rating for two hours without violation of NESC clearances or equipment failure. |  | X | X | X | X
Line Temperature | Conductor 2-hour Rating | Per definition of "Conductor/Transformer 2-hour Rating" in Section 2 of the ERCOT protocols, The two-hour MVA rating of the conductor or transformer only, excluding substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature. The conductor or transformer can operate at this rating for two hours without violation of National Electrical Safety Code (NESC) clearances or equipment failure. |  | X | X | X | X
Reactive Capability | Mw4 | The gross MW value which is associated with the highest "Seasonal Net Maximum Sustainable Rating" as registered on the RARF, (Net to gross conversion) |  | X | X | X | X | Need to provide the D-curve for cross checking
Reactive Capability | Lagging MVAR Limit Associated With Mw4 Output | The Lagging Reactive Power capability associated with the MW4 curve point, in MVAr. |  | X | X | X | X
Reactive Capability | Leading MVAR Limit Associated With Mw4 Output | The Leading Reactive Power capability associated with the MW4 curve point, in MVAr; input as negative number |  | X | X | X | X
Transformer Data | Generator Step up Transformer? | Select Y or N whether this transformer is a generator step up transformer |  | X | X | X | X
Transformer Data | Positive Sequence Resistance (100 MVA Base) | Positive Sequence Resistance (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) |  | X | X | X | X | We need to add a field to account for three winding transformers or have a drop down field for the user to select whether it is a 2-winding or a three-winding transformer and the impedance fields should change appropriately based upon that. The fileds that we are requesting currently are only valid for two-winding transformers. | There needs to be additional fields for Zps_R, Zps_X, Zpt_R, Zpt_X, Zst_R, and Zst_X for 3-winding GSU transformers (for positive and zero sequence impedance). I do not see this information spelled out in the spreadsheet. The RARF currently has these fields for the GSU, and does not specify for 3-windings: These would be deleted as they would be reduntant.
Transformer Data | Positive Sequence Reactance (100 MVA Base) | Positive Sequence Reactance (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) |  | X | X | X | X |  | These would be deleted as they would be reduntant.
Transformer Data - NEW FIELD | Generator Step up Transformer 2 winding or 3 winding? | Select 2 or 3 whether this transformer has 2 or 3 windings. |  | X | X | X | X
Transformer Data - NEW FIELD | Primary-Secondary Positive Sequence Resistance (100 MVA Base) | Positive Sequence Resistance (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) between primary and secondary windings. |  | X | X | X | X
Transformer Data - NEW FIELD | Primary-Secondary Positive Sequence Reactance (100 MVA Base) | Positive Sequence Reactance (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) between primary and secondary windings. |  | X | X | X | X
Transformer Data - NEW FIELD | Primary-Tertiary Positive Sequence Resistance (100 MVA Base) | Positive Sequence Resistance (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) between primary and tertiary windings. Designed impedance data should be used for buried tertiaries that were not tested. |  | X | X | X | X
Transformer Data - NEW FIELD | Primary-Tertiary Positive Sequence Reactance (100 MVA Base) | Positive Sequence Reactance (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) between primary and tertiary windings. Designed impedance data should be used for buried tertiaries that were not tested. |  | X | X | X | X
Transformer Data - NEW FIELD | Secondary-Tertiary Positive Sequence Resistance (100 MVA Base) | Positive Sequence Resistance (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) between secondary and tertiary windings. Designed impedance data should be used for buried tertiaries that were not tested. |  | X | X | X | X
Transformer Data - NEW FIELD | Secondary-Tertiary Positive Sequence Reactance (100 MVA Base) | Positive Sequence Reactance (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) between secondary and tertiary windings. Designed impedance data should be used for buried tertiaries that were not tested. |  | X | X | X | X
Transformer Data - NEW FIELD | Impedance I/O Code | This is the I/O impedance code of the main power transformer |  | X | X | X | X |  | AEP wants to add this.
Transformer Data | Normal Rating | The continuous MVA rating of the transformer, including substation terminal equipment in series with the transformer, at the applicable ambient temperature. The Transmission Element can operate at this rating indefinitely without damage, or violation of NESC clearances. |  | X | X | X | X | See comment above for three winding transformer. With a three winding transformer, each winding will have it’s own ratings.
Transformer Data | 2-hr Emergency Rating | The two-hour MVA rating of the transformer, including substation terminal equipment in series with the transformer, at the applicable ambient temperature. The Transmission Element can operate at this rating for two hours without violation of NESC clearances or equipment failure. |  | X | X | X | X | See comment above for three winding transformer. Need to request the tranformer rating as that is being used as Rate C in the cases.
Transformer Data | On-Load Voltage Regulation | Select Y or N whether this transformer will change tap settings automatically while online to control voltage. |  | X | X | X | X
Transformer Data | Does Transformer have an On-Load Tap Changer? | Select Y or N whether this transformer has an On-Load Tap changer |  | X | X | X | X
Transformer Data | Location of On-Load Tap Changer - Primary (High) or Secondary (Low) side | If this transformer has an On-Load Tap changer, select whether it is on Primary (High) or Secondary (Low) side. |  | X | X | X | X
Transformer Tap Settings | Primary (High) -Secondary (Low) Flag | Select from list whether taps are on Primary (high) side or Secondary (low) side. Enter both On-Load and No-Load Tap changer data on separate rows if both exist. |  | X | X | X | X
Transformer Tap Settings | Tap Position At Manufactured Nominal Voltage | Tap Position At Manufactured Nominal Voltage |  | X | X | X | X
Transformer Tap Settings | Total Number of Tap Positions | Total Number of Tap Positions |  | X | X | X | X
Transformer Tap Settings | Normal Tap Position | Normal Tap Position |  | X | X | X | X
Transformer Tap Settings | Lowest Tap Position | Lowest Tap Position |  | X | X | X | X
Transformer Tap Settings | Voltage at Lowest Tap Position | Voltage at Lowest Tap Position |  | X | X | X | X
Transformer Tap Settings | Highest Tap Position | Highest Tap Position |  | X | X | X | X
Transformer Tap Settings | Voltage at Highest Tap Position | Voltage at Highest Tap Position |  | X | X | X | X
Transformer Tap Settings | Size of Each Voltage Level Step | Size of Each Voltage Level Step |  | X | X | X | X
Turbine Details | Turbine Manufacturer and Model | From name-plate or manufacturer data sheet |  | X | X | X | X
Turbine Details | MW Rating for this model of Turbine | From name-plate or manufacturer data sheet |  | X | X | X | X | Is this at the unit power factor?
Turbine Details | Number of Turbine Manufacturer/Model | Count of wind turbines in this WGR of the specified Manufacturer/Model |  | X | X | X | X
Unit Information | Name Plate Rating | Manufacturer designed MVA Rating of this unit at its rated power factor (gross). |  | X | X | X | X | This seems to be duplicate to MW Rating for this model of Turbine * Number of Turbine? If it is the case, this one should be called as MW Rating of this unit… It is confusing to call it MW rating for turbine, but MVA rating for the whole unit
Unit Information | Reactive Power Rating | Manufacturer designed MVAr at rated power factor (gross) |  | X | X | X | X
Unit Information | Unit Generating Voltage | Terminal voltage of generating unit, as modeled (typically equivalent to low side of GSU) |  | X | X | X | X
Turbine Details | Turbine Type | Indicate the type of Turbine (eg. Type 1, 2, 3, 4, 5) Type 1 Conventional induction generator Type 2 Variable Rotar-Resistance Induction generator Type 3 WTG – Doubly fed asynchronous generator Type 4 WTG – Full-converter unit Type 5 WTG – Variable Ratio Converter Coupled Synchronous Generator |  |  |  |  | X |  |  | Knowing the turbine type (2, 3, 4, etc.) would be helpful in determining the turbine’s abilities. ONCOR would like this information.
Collector System | Voltage Level kV | Enter the voltage level (in kV) of the collector system. Used when calculating Positive and Zero Sequence resistance and reactance. |  | X | X | X | X | We need the equivalent collector system to perform all the studies (steady state, short circuit and stability).
Collector System | Collection System One-Line Diagram | Collection System One-Line Diagram (Imbed a PDF one-line diagram) |  | X | X | X | X
Collector System | Collection System Detailed Model. Embed a PSS/E Raw & Sequence model, or an ASPEN or a Powerworld Model (to include both positive and zero sequence data) | Collection System Detailed Model. Embed a PSS/E Raw & Sequence model, or an ASPEN or a Powerworld Model (to include both positive and zero sequence data) |  | X | X | X | X
Line Data | Zero Sequence Line Resistance in P.u. (100 MVA Base) | Zero Sequence Line Resistance in p.u. (100 MVA Base) |  |  | X | X | X
Line Data | Zero Sequence Line Reactance in P.u. (100 MVA Base) | Zero Sequence Line Reactance in p.u. (100 MVA Base) |  |  | X | X | X
Line Data | Zero Sequence Charging Susceptance in P.u. (100 MVA Base) | Zero Sequence Charging Susceptance in p.u. (100 MVA Base) |  |  | X | X | X
Line Data - NEW FIELD | Zero Sequence Line Reactance in P.u. Of a mutual coupling, if applicable (100 MVA Base) | Zero Sequence Line Reactance in P.u. Of a mutual coupling, if applicable (100 MVA Base) |  |  | X | X | X
Transformer Data | Zero Sequence Data Winding Connect code (1-5) | Enter zero sequence data winding connect code 1 - 5 as noted below. Transformer Connection Codes: Two Winding Transformers (in order of Voltage highest first) 1 -- Wye-Wye Bank Both Neutrals Grounded 2 -- Wye - Delta Bank Grounded Wye 3 -- Delta - Wye Bank Grounded Wye 4 -- Delta - Delta Bank; Wye-Delta Bank Ungrounded Wye; Delta-Wye Bank Ungrounded Wye; Wye-Wye Bank Either Wye Grounded 5 -- Three Winding only (Test Reports needed for Code 5) |  |  | X | X | X | Substation (Main) Transformer Data
Transformer Data | Zero Sequence Grounding Resistance For An Impedance Grounded Transformer in P.u. (100 MVA Base) | Zero Sequence Grounding Resistance For An Impedance Grounded Generator in p.u. (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) |  |  | X | X | X
Transformer Data | Zero Sequence Grounding Reactance For An Impedance Grounded Transformer In P.u. (100 MVA Base) | Zero Sequence Grounding Reactance For An Impedance Grounded Transformer In P.u. (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) |  |  | X | X | X
Transformer Data | Zero Sequence Resistance In p.u. (100 MVA Base) | Zero Sequence Resistance In p.u. (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) |  |  | X | X | X |  | These would be deleted as they would be reduntant.
Transformer Data | Zero Sequence Reactance In P.u. (100 MVA Base) | Zero Sequence Reactance In P.u. (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) |  |  | X | X | X |  | These would be deleted as they would be reduntant.
Transformer Data - NEW FIELD | Primary-Secondary Zero Sequence Resistance In p.u. (100 MVA Base) | Zero Sequence Resistance In p.u. (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) |  |  | X | X | X |  | There needs to be additional fields for Zps_R, Zps_X, Zpt_R, Zpt_X, Zst_R, and Zst_X for 3-winding GSU transformers (for positive and zero sequence impedance). I do not see this information spelled out in the spreadsheet. The RARF currently has these fields for the GSU, and does not specify for 3-windings:
Transformer Data - NEW FIELD | Primary-Secondary Zero Sequence Reactance In P.u. (100 MVA Base) | Zero Sequence Reactance In P.u. (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) |  |  | X | X | X
Transformer Data - NEW FIELD | Primary-Tertiary Zero Sequence Resistance In p.u. (100 MVA Base) | Zero Sequence Resistance In p.u. (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) |  |  | X | X | X
Transformer Data - NEW FIELD | Primary-Tertiary Zero Sequence Reactance In P.u. (100 MVA Base) | Zero Sequence Reactance In P.u. (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) |  |  | X | X | X
Transformer Data - NEW FIELD | Secondary-Tertiary Zero Sequence Resistance In p.u. (100 MVA Base) | Zero Sequence Resistance In p.u. (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) |  |  | X | X | X
Transformer Data - NEW FIELD | Secondary-Tertiary Zero Sequence Reactance In P.u. (100 MVA Base) | Zero Sequence Reactance In P.u. (100 MVA Base) and the nominal system voltage (69, 138 or 345 kV) |  |  | X | X | X
Transformer Data | High Side Voltage Connection - Wye or Delta | Select whether this high side connection is a Wye or Delta connection |  |  | X | X | X
Transformer Data | High Side Manufactured Nominal Voltage | Enter the high side manufactured nominal voltage for this transformer |  | X | X | X | X
Transformer Data | Low Side Voltage Connection - Wye or Delta | Select whether this low side connection is a Wye or Delta connection |  |  | X | X | X
Transformer Data | Low Side Manufactured Nominal Voltage | Enter the low side manufactured nominal voltage for this transformer |  | X | X | X | X
Turbine Details | What Is The MVA Base That The Following Data Is Based On? | The MVA Base for stated impedances. |  | X | X | X | X
Turbine Details | What Is The Kv Base That The Following Data is Based On? | The KV Base for stated impedances. |  | X | X | X | X
Turbine Details | Subtransient Reactance X'',(Instantaneous Fault Current Period) (unsaturated) | Enter the instantaneous subtransient reactance (unsaturated) for the fault. |  |  | X | X | X
Turbine Details | Transient Reactance, X' (First 2-3 cycles of the Fault) (unsaturated) | Enter the transient reactance (unsaturated) for the first 2-3 cycles of the fault. |  |  | X | X | X
Turbine Details | Positive Sequence Resistance (unsaturated) | Enter the positive sequence resistance (unsaturated) for system models. |  |  | X | X | X
Turbine Details | Synchronous Reactance X (After 4 cycles of the fault) (unsaturated) | Enter the synchronous reactance (unsaturated) after 4 cycles of the fault. |  |  | X | X | X
Turbine Details | Negative Sequence Resistance (unsaturated) | Enter the negative sequence resistance (unsaturated) for system models. |  |  | X | X | X
Turbine Details | Negative Sequence Reactance (unsaturated) | Enter the negative sequence reactance (unsaturated) for system models. |  |  | X | X | X
Turbine Details | Zero Sequence Resistance (unsaturated) | Enter the zero sequence resistance (unsaturated) for system models. |  |  | X | X | X
Turbine Details | Zero Sequence Reactance (unsaturated) | Enter the zero sequence reactance (unsaturated) for system models. |  |  | X | X | X
Turbine Details | Subtransient Reactance X'',(Instantaneous Fault Current Period) (saturated | Enter the instantaneous subtransient reactance (saturated) for the fault. |  |  | X | X | X
Turbine Details | Transient Reactance, X' (First 2-3 cycles of the Fault) (saturated) | Enter the transient reactance (saturated) for the first 2-3 cycles of the fault. |  |  | X | X | X
Turbine Details | Positive Sequence Resistance (saturated) | Enter the positive sequence resistance (saturated) for system models. |  |  | X | X | X
Turbine Details | Synchronous Reactance X (After 4 cycles of the fault) (saturated) | Enter the synchronous reactance (saturated) after 4 cycles of the fault. |  |  | X | X | X
Turbine Details | Negative Sequence Resistance (saturated) | Enter the negative sequence resistance (saturated) for system models. |  |  | X | X | X
Turbine Details | Negative Sequence Reactance (saturated) | Enter the negative sequence reactance (saturated) for system models. |  |  | X | X | X
Turbine Details | Zero Sequence Resistance (saturated) | Enter the zero sequence resistance (saturated) for system models. |  |  | X | X | X
Turbine Details | Zero Sequence Reactance (saturated) | Enter the zero sequence reactance (saturated) for system models. |  |  | X | X | X
Turbine Details | Continuous Rating | Rating that the Pad Mount Transformer can operate at indefinitely without damage |  |  | X | X | X
Turbine Details | Impedance Z | Enter the impedance of the transformer. |  |  | X | X | X
Turbine Details | X/R Ratio | Enter the ratio of the reactance to the resistance of the transformer. |  |  | X | X | X
Turbine Details | Zero Sequence Z | Enter the zero sequence impedance of the transformer. |  |  | X | X | X
Turbine Details | Zero Sequence X/R Ratio | Enter the ratio of the zero sequence reactance to the zero sequence resistance of the transformer. |  |  | X | X | X
Turbine Details | Base MVA For Transformer Data | Enter the base MVA upon which the per unit transformer data is provided. |  |  | X | X | X | Also request the Base kV upon which the pu transformer data is provided.
Turbine Details | High Side Voltage Level (nominal) | Enter the voltage level (in kV) on the high-voltage side of the wind generator pad-mount transformer. |  |  | X | X | X
Turbine Details | Low Side Voltage Level (nominal) | Enter the voltage level (in kV) on the low-voltage side of the wind generator pad-mount transformer. |  |  | X | X | X
Turbine Details | High Side Voltage Connection | Identify the type of connection used for the windings (Wye/Delta and Neutral Grounding) on the high-voltage side of the transformer. |  |  | X | X | X
Turbine Details | Low Side Voltage Connection | Identify the type of connection used for the windings (Wye/Delta and Neutral Grounding) on the low-voltage side of the transformer. |  |  | X | X | X
ONE LINE | Embed a PDF or CAD One Line Diagram | Include a PDF or CAD One Line Diagram of the site |  | X | X | X | X | Substation One Line
Planning | Average Amount of Auxiliary Real Power | Enter average MW for auxiliary Load at full MW output of the unit (For Aux MW >= 1.0, enter all % load splits for MW and MVAr aux loads) |  |  |  |  | X
Planning | Auxiliary Load Power Factor | Enter power factor for auxiliary Load, if average MVAr for auxiliary load is not provided |  |  |  |  | X
Planning | Average Amount of Auxiliary Reactive Power | Enter average MVAr for auxiliary Load at full MW output of the unit |  |  |  |  | X
Dynamic Data | Embed Dynamic Data | Model data (in current PSS/E format utilized by the DWG), with appropriate values provided for all model parameters, test reports that support the model data based on field/commissioning tests, (if available), model libraries in .dll or .obj file format (if using user defined models not included in the PSS/E standard model library), model documentation/user guides (if using user defined models not included in the PSS/E standard model library). Refer to DWG Procedure Manual for requirements. |  |  |  |  | X
Planning | PSSE Models | PSSE MODEL : THE following list of models and data are required: Generator, Turbine-Governor, Excitation System, Power System Stabilizer (required If There Is A Power System Stabilizer), Compensator (required If There Is A Compensator), Over Excitation Limiter (required If There Is An Over Excitation Limiter), and Under Excitation Limiter (required If There Is An Under Excitation Limiter). PLEASE imbed the data files in the Dynamics Data Tab, if files are very large, or numerous, imbed the files in a single zip file. If user-defined models are submitted, include the .obj or.dll or .lib files, and documentation for the model used. |  |  |  |  | X
Planning | Large Motor, Percent Of Total Mw Load | Enter estimated % of total MW Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  |  |  | X
Planning | Small Motor, Percent Of Total Mw Load | Enter estimated % of total MW Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  |  |  | X
Planning | Resistive (heating) Load, Percent Of Total Mw Load | Enter estimated % of total MW Load per Load type. |  |  |  |  | X
Planning | Discharge Lighting, Percent Of Total Mw Load | Enter estimated % of total MW Load per Load type. |  |  |  |  | X
Planning | Other, Percent of total MW Load | Enter estimated % of total MW Load per Load type. |  |  |  |  | X
Planning | Large Motor, Percent of total MVAR Load | Enter estimated % of total MVAr Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  |  |  | X
Planning | Small Motor, Percent of total MVAR Load | Enter estimated % of total MVAr Load per Load type. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. |  |  |  |  | X
Planning | Discharge Lighting, Percent of total MVAR Load | Enter estimated % of total MVAr Load per Load type. |  |  |  |  | X
Planning | Other, Percent Of Total MVAR Load | Enter estimated % of total MVAr Load per Load type. Ensure that Large Motor, percent of total MVAR load + Small Motor, percent of total MVAR load Discharge Lighting, percent of total MVAR load + Other, percent of total MVAR load = 100. |  |  |  |  | X
Protection | Breaker Interruption Time | Time taken (in cycles) between the breaker receiving the trip signal, and the breaker contacts opening to interrupt the flow of current. |  |  |  |  | X
Protection | Undervoltage 1 | Enter the first level undervoltage relay set point in per unit. |  |  |  |  | X
Protection | Time 1 | Enter the first level undervoltage time delay set point. |  |  |  |  | X
Protection | Overvoltage 1 | Enter the first level overvoltage relay set point in per unit. |  |  |  |  | X
Protection | Time 1 | Enter the first level overvoltage relay time delay set point. |  |  |  |  | X
Protection | Underfrequency 1 | Enter the first level underfrequency relay set point in Hz. |  |  |  |  | X
Protection | Time 1 | Enter the first level underfrequency relay time delay set point. |  |  |  |  | X
Protection | Overfrequency 1 | Enter the first level overfrequency relay set point in Hz. |  |  |  |  | X
Protection | Time 1 | Enter the first level overfrequency relay time delay set point. |  |  |  |  | X
Protection | Does the resource have the manufacturer's technical document / Simulation Results / Test Results, etc. describing the turbine technology & VRT optIons purchased with turbine, if any | TURBINE VRT CAPABILITY: Ensure that VRT capability is included as part of the normal dynamic model data submitted. If yes, provide the following: (1) the PSS/E dynamic model including the settings and (2) technical manufacturer's documents describing the VRT capabilities of the purchased packages. Models and documents are to be embedded in the RARF Dynamic Data tab or included in the zip file. |  |  |  |  | X
Protection | Does the Resource use dynamic reactive devices (SVC/statcom, etc.) at the wind farm? - (note: capacitor/reactor banks used for conventional reactive support cannot be considered as dynamic reactive devices) - If yes, please provide supporting documentation. (manufacturer's technical document, PSS/E model etc.), submitted in the Dynamics Data Tab. | TURBINE VRT CAPABILITY: If yes, provide the following (1) the PSS/E dynamic model for the Dynamic Reactive Device (SVC,DVAR,STATCOM), including the settings and (2) a manufacturer's technical document describing the dynamic device and model. Models and documents are to be embedded in the RARF Dynamic Data tab or included in the zip file. |  |  |  |  | X
Protection | Does the Resource have plant voltage protection? If yes, please provide supporting documentation. | TURBINE VRT CAPABILITY: Plant voltage protection is substation main power transformer and equipment protection, If yes, provide a technical description of the protection scheme and voltage settings. The documents are to be embedded in the RARF Dynamic Data tab or included in the zip file. |  |  |  |  | X
Protection | Does The Resource Have Feeder Voltage Protection? If Yes, Please Provide Supporting Documentation. | TURBINE VRT CAPABILITY: Feeder voltage protection is protection on the feeder breakers, If yes, provide a technical description of the protection scheme and voltage settings. The documents are to be embedded in the RARF Dynamic Data tab or included in the zip file. |  |  |  |  | X
Private Network - Unit | Average Amount of Self-serve Private Load | Amount of the total site generation MW output used for self serve and not available for the grid. If multiple generators are registered, proportion the total site load against each generator, not to exceed the nameplate capacity of any generator. |  | X | X | X | X | This data is required for steady state and short circuit studies also.
Private Network - Unit | Average Amount of Self-serve Private Reactive Load | Amount of the total site generation MVAr output used for self serve and not available for the grid. If multiple generators are registered, proportion the total site load against each generator, not to exceed the nameplate capacity of any generator. |  | X | X | X | X | This data is required for steady state and short circuit studies also.
Private Network - Unit | Private Network Gross Unit Capability | MW Gross Generation Capability for the generator |  | X | X | X | X | This data is required for steady state and short circuit studies also.
Private Network - Unit | Private Network Gross Unit Reactive Capability | MVAr Gross Generation Capability for the generator |  | X | X | X | X | This data is required for steady state and short circuit studies also.
General and Site | Resource Site Name |  |  | X | X | X | X | Added back by CNP.
Note: This is captured by the new GINR application in order to perform a Screening Study. ZR - ERCOT
Note on B3: Reich, Zach:
Note on E3: RDWG 31OCT2013: R - Required C - Conditional O - Optional A - Automatic
Note on F3: RDWG 31OCT2013: R - Required C - Conditional O - Optional A - Automatic
Note on G3: RDWG 31OCT2013: R - Required C - Conditional O - Optional A - Automatic
Note on H3: RDWG 31OCT2013: R - Required C - Conditional O - Optional A - Automatic
Note on A48: Jon Snellgrove: Add fields for all three windings.