## Slide 1
PDCWG Report to ROS
Chair: Percy Galliguez, Brazos Electric Power Cooperative, Inc.
Vice Chair: Chad Mulholland, NRG
ROS
April 5th, 2018

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-1 FMEs & IMFR
    3 FMEs in the month of February
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 03/07/18
  NPRR863 – Separation of PFR and RRS Ancillary Service
  Regulation & Frequency Control Reports
  BAL-001-TRE-001
    Operating Condition Guidelines for PFR Performance
    LCRA-Combined Cycle Steam Droop setting clarification or possible SAR
    Performance Evaluation to check for pass/fail before scoring
    No Evaluation of Resources below LSL

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There were 3 FMEs in February
  2/5/2018 14:04:45
    Loss of 816 MW(IMFR=816MW/0.1Hz)
    Interconnection Frequency Response:
    3 of 41(0 Of 27 RRS Providers) Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    1 of 41(0 Of 27 RRS Providers) Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  2/14/2018 06:30:21
    Loss of 784 MW(IMFR=881MW/0.1Hz)
    Interconnection Frequency Response:
    6 of 38(1 Of 22 RRS Providers) Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    5 of 38(1 Of 22 RRS Providers) Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Frequency Measurable Events
  2/22/2018 06:39:04
    Loss of 491 MW(IMFR=1260MW/0.1Hz)
    Interconnection Frequency Response:
    8 of 47(4 Of 29 RRS Providers) Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    3 of 47(0 Of 29 RRS Providers) Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 7: Interconnection Minimum Frequency Response (IMFR) Performance
IMFR Performance currently 1315.456 MW/0.1Hz

## Slide 8: Frequency Control Report
February 2018

## Slide 9: CPS1 Performance

## Slide 10: RMS1 Performance of ERCOT Frequency

## Slide 11: Frequency Profile Analysis

## Slide 12: Time Error Corrections
There were no Time Error Corrections (TEC) in February

## Slide 13: ERCOT Total Energy

## Slide 14: ERCOT Total Energy from Wind Generation

## Slide 15: ERCOT % Energy from Wind Generation

## Slide 16
Questions?