## Slide 1: Transmission Operator Protection System Misoperations 2017
ERCOT Protection System Misoperations Data – 138kV and 345kV Combined

## Slide 2: Protection System Misoperations – 2017
 |  | Q4 | 2017
# of Misoperations | Total | 33 | 176
 | 345 kV | 8 | 37
 | 138 kV | 25 | 138
 | < 100 kV | 0 | 1
By Category | Failure to Trip | 3 | 8
 | Slow Trip | 0 | 0
 | Unnecessary Trip during Fault | 14 | 96
 | Unnecessary Trip – Non Fault | 16 | 72
 | SPS | 0 | 0
By Relay System Type | Electromechanical | 3 | 21
 | Solid State | 0 | 1
 | Microprocessor | 27 | 135
 | Other/ N/A | 3 | 19
By Equipment Protected | Line | 11 | 80
 | Transformer | 5 | 25
 | Generator | 3 | 14
 | Shunt/Series Capacitor | 0 | 7
 | Shunt/Series Reactor | 0 | 6
 | Dynamic VAR system | 0 | 0
 | Bus | 1 | 8
 | Breaker | 13 | 36

## Slide 3
Summary of Human Performance Issues noted for 2017 Q4:
Two 138kV breakers tripped due to incorrect SOTF logic
138kV line tripped due to mis-wired polarity to the backup relay
345kV GSU tripped due to a CT shorting screw left in place.
138kV line over-tripped for an external fault. DCB scheme was disabled on one end of the line.
138kV breaker over-tripped due to CT left open-circuited.
Failure to Trip/Slow Trip Misoperations in 2017 Q4:
138kV bus differential did not trip properly for a 138kV PT failure. An incorrect relay setting template was used.
Transformer relays failed to trip high side breaker due to test switches being left open.
345kV line differential protections failed to trip due to relays being left disabled following commissioning tests.
Protection System Misoperations 2017 Q4

## Slide 4
PRC-027: FERC NOPR issued 11/16/2017. Directed NERC to modify PRC-027 to require initial coordination study six years from the effective date of the standard.
PRC-023 Implementation Guidance document approved at the December Planning Committee meeting
PRC-024 Implementation Guidance document remanded back to SPCS for correction. Document corrections completed and approved by Planning Committee. Sent to ERO Compliance group for their endorsement.
PRC-019 Implementation Guidance document, volunteers taken for document development team.
NERC Update

## Slide 5: System Protection and Control Subcommittee (SPCS)
SPCS Meeting 4/24 and 4/25
  Oncor Electric
  115 W 7th St
  Fort Worth, TX 76102
Retirement of Sam Francis, Oncor
Nomination of new members from SPWG
  Glenn Hargrave, CPS
  Armin Klusman, CenterPoint Energy

## Slide 6: ERCOT SPWG Short Circuit Case Building
Posted Current Year 2018 Short Circuit Case on 3/30/2018
Working on Future Year 2019-2023 Short Circuit Cases
2019-2023 FY Pass Tracking Spreadsheet |  |  |  |  |  | 
ERCOT | Pass0 | Pass1 | Pass2 | Pass3 | Pass4 Final | Posted
ERCOT Scheduled Date | 4/6/2018 | 4/27/2018 | 5/18/2018 | 6/1/2018 | 6/15/2018 | 6/29/2018
ERCOT Actual Date |  |  |  |  |  | 
TDSP Due Date | 4/20/2018 | 5/11/2018 | 5/25/2018 | 6/8/2018 | 6/22/2018 | N/A