## Slide 1: Planning Geomagnetic Disturbance Task Force (PGDTF) Update to the ROS
April 5, 2018
Dylan Preas
PGDTF Chair
<number>
4/5/2018 ROS Meeting

## Slide 2: GIC System Model Working Session
TSP-only working session on March 7th and 8th
Reviewed the PGDTF GIC User Guide – data checks
Reviewed GIC flow results for TSPs/REs submitted data
Made corrections/updates to the GIC System Model
<number>
4/5/2018 ROS Meeting

## Slide 3: GIC System Model Timeline
  Fourth Pass Release RAW & GIC Files – March 1st
  Fourth Pass GIC/VAR Values – March 1st
  GIC Model Review Face-to-Face Meeting (TSP Only) –March 7th & 8th
  Fourth Pass TSP Peak and MIN Update – March 13th
Fourth Release RAW & GIC Files – March 22nd
Fourth GIC/VAR Values – March 22nd
GIC Model Review Face-to-Face Meeting (TSP Only) – April 12th (afternoon)
GIC Model Review Face-to-Face Meeting (TSP Only) – April 13th
Final Pass TSP Peak and MIN Update – April 18th
Final Release RAW & GIC Files – April 25th
Final GIC/VAR Values – April 25th
<number>
4/5/2018 ROS Meeting

## Slide 4: NERC TPL-007-1 R3
“…criteria for acceptable System steady state voltage performance for its System during the benchmark GMD event”
Effective January 1, 2022
Prevent voltage collapse, cascading, and uncontrolled islanding minimizing load loss
PGDTF developed draft criteria for use in the initial GMD Vulnerability Assess
7/9/2015 ROS Meeting
<number>

## Slide 5
(1) The following performance criteria shall be applicable to the Geomagnetic Disturbance (GMD) Vulnerability Assessment:
    (a) Following the occurrence of the benchmark GMD event from the NERC Reliability Standard addressing GMD Planning Performance Requirements, the list of GMD event contingencies as defined in Section 6.11 (2) of the Planning Guide, and any manual or automatic load shedding resulting from the event:
      (i) buses owned by Resources Entities shall not have voltages less than known or assumed minimum generator under-voltage trip limits;
      (ii) buses owned by Resources Entities shall not have voltages exceeding known or assumed maximum generator over-voltage trip limits;
      (iii) load serving buses greater than 100 kV shall not have voltages below 0.88 per unit;
      (iv) buses greater than 100 kV shall not have voltages above 1.05 per unit.
7/9/2015 ROS Meeting
<number>
4.1.1.7 Planning Geomagnetic Disturbance (GMD) System Steady State Voltage Performance Criteria

## Slide 6
    (b) The ERCOT System shall remain stable with no cascading as defined by:
      (i) total load loss greater than 6% of the total initial system load.
If a TSP has communicated to ERCOT that a Facility has unique characteristics and may operate outside of the above ranges and deviation (e.g. Facilities located near a series capacitor) or that the Facility needs to be operated in a more restrictive range (e.g. a nuclear plant, UVLS relay settings) or its system is designed to operate with different voltage limits or voltage deviation then the TSP’s specified limits will be considered acceptable.
7/9/2015 ROS Meeting
<number>
4.1.1.7 Planning Geomagnetic Disturbance (GMD) System Steady State Voltage Performance Criteria
(Continued…)

## Slide 7: Upcoming PGDTF Activities
PGDTF Business Meetings on April 12th (morning)
  Open meeting
  Review ERCOT’s proposed language regarding TPL-007-1 R2 “maintaining the GIC system model”
  Review Vulnerability Assessment Scope
GIC System Model Building Face-to-Face Meeting –
April 12th (afternoon) and April 13th (all-day)
  TSP-only due to confidentiality
  Review transformer data & branch data
  Discuss GIC flow interpretation methods
  Update the GIC System Model as needed
<number>
4/5/2018 ROS Meeting

## Slide 8: Questions
<number>
4/5/2018 ROS Meeting