## Slide 1
Procedures for Re-powering Wind Units – PGRR Update
John Bernecker
ERCOT Resource Integration
April 23, 2018

## Slide 2: What is a re-power?
Some IEs have used terms such as “electrical upgrades” and “mechanical upgrades” to describe re-powering activities
These terms are less useful than detailed information on the proposed changes, including, but not limited to MW size and whether or not a new dynamic model is required
If an existing resource being re-powered has a capacity of 10 MW or greater, then it must go through the GINR process
ERCOT fees are based on total resource size, not the size of the incremental change in capacity
  Language added to PG 5.7.2 and 5.7.3

## Slide 3: Screening Study
Re-powers with an incremental capacity increase of 10 MW or greater require a new Screening Study
  Added waiver language to PG 5.4.1
GINR application fee still applies to all re-powers based on total resource size

## Slide 4: FIS
Full Interconnection Study (FIS) is required if:
  The MW increase is greater than 10 MW
  The control system software is upgraded such that a new dynamic model is required
  The inverters are changed such that a new dynamic model is required
  The change involves:
    Blade replacement only and the manufacturer has not provided evidence that there is no decrease in performance
    A change in turbine manufacturer
    New turbine model by the same manufacturer and a new dynamic model is required
Hard to get these details into the Planning Guide. Recommend they live elsewhere, such as Resource Interconnection Handbook. Also allows flexibility for other technologies re-powering.

## Slide 5: FIS
Depending on the details of the re-powering activities with respect to steady-state and dynamic modeling, it may be possible to reduce the scope of the FIS
  Added reduced scope language to PG 5.4.2.1(7)
ERCOT and the interconnecting TSP make this determination based on evidence provided by the IE and turbine manufacturer
  Added language for additional data request to 5.4.2.1(7)

## Slide 6: FIS
The following data is required to determine whether the FIS scope can be reduced:
  A description from the turbine manufacturer of whatever change will occur to the dynamic characteristics, such as the inertia, frequency, and voltage support
  The updated dynamics model and settings (DYR, DLL, and PDF of the model manual)
  A description from the turbine manufacturer of whatever change will occur to the reactive power capability
  A dynamic simulation demonstrating that the performance of the re-powered machines is equal to or better than that of the existing machines.
    Should be based on a Thévenin equivalent representing the appropriate short circuit current at the POI
    Should provide plots of real power, reactive power, and POI voltage for the following comparisons for the existing turbines and the modified turbines:
      Small voltage deviation, such as switching capacitor or reactor bank to see the voltage support response
      High-voltage and low-voltage ride-through test
      A frequency test to see primary frequency response
Hard to capture this in the Planning Guide. We also need flexibility to adjust as we learn and for other technologies. Recommend placing this guidance in another document.

## Slide 7: FIS

## Slide 8: SSR
SSR study may be avoided with a statement from the turbine manufacturer that the subsynchronous behavior will be exactly the same or better
A PSCAD model / subsync data is required for all re-powers
No language changes in PGRR

## Slide 9: Reactive Power Capability Requirements
ERCOT reads the current language of section 3.15(10) of the ERCOT Protocols to imply that the re-powering of any Generation Resource that qualifies as an “Existing Non-Exempt WGR” under section 3.15(4) does not, by itself, cause that Generation Resource to be subject to the broader reactive power requirements stated in section 3.15(3). However, please note that, as with any other provision in the ERCOT Protocols, section 3.15(10) is subject to future revision.

## Slide 10: Reactive Study
All re-powers are required to submit a Reactive Study
No language change needed

## Slide 11: IA
Not represented in PGRR language.
Concerns stated at last workshop still need to be addressed.

## Slide 12: QSA
Re-powers are not currently subject to Planning Guide section 5.9 requirements
Planning Guide section 5.9 language may be altered in the future
New language is being considered that would include re-powers in the QSA using the same process as new units if a new FIS stability study was required
Language added to PG 5.9

## Slide 13: RARF Submittals
Updated RARFs should be submitted to ERCOT Resource Integration for initial GINR application and Planning Guide section 6.9 compliance
Updated RARFs should be submitted via MIS once Planning Guide section 6.9 compliance has been verified and RE entity is ready to register the resource

## Slide 14: Commissioning
Commissioning Plan, Part 2 checklist, and Part 3 checklist are required for re-powers
Part 2 checklist is being modified for re-powers
  Part 2a required prior to starting any re-power work
    Check existing telemetry to ensure it currently meets ERCOT requirements
    ERCOT approval of Part 2a allows the RE and QSE to proceed with the re-power
  Part 2b required following completion of re-power work and Model Ready Date for re-powered site
    Check model and telemetry for the re-powered site and WGRs
    Includes some items from Part 2 checklist for new units
Part 3 checklist is identical to that for new units
  Unit tests are required prior to Part 3 approval

## Slide 15: Other Items
Nodal Protocols section 16.5 compliance checklist
  ERCOT may develop a shorter form for re-powers
  ERCOT may request data from re-powers that is not on the current form
Re-powers may require operations planning studies prior to synchronization

## Slide 16: Questions?
Contact:
  John.Bernecker@ercot.com
  Jay.Teixeira@ercot.com
  ResourceIntegrationDepartment@ercot.com