## Slide 1: LBNL’s Frequency Response Study for FERC
May 3, 2018
Prepared for
ERCOT Reliability and Operations Subcommittee
Presenters
Joe Eto – Background/Overview
John Undrill – Frequency Response Issues
Sydney Niemeyer - Independent Observations

## Slide 2: Project Objectives and Motivation
To build upon a previous FERC report prepared by LBNL to address frequency response issues holistically considering how all aspects of the US generation fleet (and loads) might change in the future on an interconnection-specific basis
The LBNL 2010 study developed new metrics, but used them to study only the impacts of one new form of generation (i.e., electronically coupled, variable renewable generation) on frequency response

## Slide 3: Project Study Methods
Started from, but expanded previous FERC-sponsored, LBNL modeling and simulation framework
  Used industry standard simulation tool (GE PSLF)  facilitates reproducibility of results
  Examined broader range of frequency response topics  sustained frequency response
  Did not model transmission system or protection
Developed a simplified and highly flexible approach to system modeling
  Conducted several 1000 parametric simulations
  Usefulness confirmed by comparison with more detailed, industry-developed interconnection planning models
Texas Interconnection
Red: 25% Steam
Green: 30% Steam
Blue: 35% Steam
Black: PSS/E Simulation

## Slide 4: Key Study Findings
Rapidly deployed and then sustained primary control action in response to the sudden loss of generation is a fundamental reliability requirement.
This requirement is met by the action of turbine governors and, in some cases, by fast demand response.
Generation interconnection policies determine:
The extent to which the fleet is equipped to provide primary frequency response
Generation dispatch policies determine:
The amount of primary frequency response that can be delivered
  …which depends on the size of the generation loss event the interconnection is designed to withstand
The speed with which primary frequency response will deploy
  …which depends on the types of units dispatched and the headroom assigned to individual units
Notes: NEW SLIDE

## Slide 5: Study Recommendations
Focused attention needed on the collection, maintenance, and validation of operating data and study models
International practices should be reviewed as options for U.S. grid operators to consider for adaptation/adoption
All generators should have the capability to provide sustained primary frequency response
Barriers to adding a frequency bias to plant load controllers should be evaluated and addressed
The contributions of non-traditional resources for primary frequency control should be studied and incorporated, as appropriate, into future operations
The changing composition of loads should be studied and addressed

## Slide 6: List of Reports
Eto, J. H., J. Undrill, C. Roberts, P. Mackin, and J. Ellis (2018). Frequency Control Requirements for Reliable Interconnection Frequency Response. Berkeley: Lawrence Berkeley National Laboratory.
Undrill, J.M. (2018). Primary Frequency Response and Control of Power System Frequency. Berkeley: Lawrence Berkeley National Laboratory.
Undrill, J.M., P. Mackin, and J. Ellis. (2018). Relating the Microcosm Simulations to Full Scale Grid Simulations. Berkeley: Lawrence Berkeley National Laboratory.
Roberts, C. (2018). Review of International Grid Codes. Berkeley: Lawrence Berkeley National Laboratory.
https://certs.lbl.gov/project/interconnection-frequency-response

## Slide 7
FREQUENCY RESPONSE ISSUES
J. Undrill
St Paul, Minn April 2018

## Slide 8: MAIN POINTS
The collective amount of sustainable reserve for Frequency Response must be sufficient to meet, and slightly exceed, the chosen loss of production event
The Frequency Response must be produced on a sufficiently quick time scale and must be sustained
The responsibility to produce Frequency Response must be allocated to, and accepted by, a number of turbines such that individual turbines need to change output by only a small fraction of their full capacities

## Slide 9
Timing with which Frequency Response must be produced depends on basic physics of rotating inertia.
In practical terms, frequency response, must be produced in 2-4 times the system effective inertia constant, H
Timing with which Frequency Response can be produced depends on
the thermal and structural physics of steam and gas turbine plants
the water inertia physics of hydro plants
PRACTICAL POINTS

## Slide 10
Inertia constant, alone, is not (not yet) the most important parameter of the system in determining the required amount of frequency response reserve
Inertia may, or may not, become the determining parameter, depending on the evolution of electronic controls
The timing with which Frequency Response is produced is as important as important system inertia constant (and will continue to be)
The amount and timing of load response to frequency variation is an important aspect of system frequency response
CONCEPTUAL POINTS
Notes: by timing we mean speed??

## Slide 11
Steam turbine and gas turbine plants can respond quickly over a small range, but may not move so quickly outside of that small range
The initial response of (most) hydro plants is significantly slower than initial thermal plant response but (most) hydro plants can carry on at their characteristic rate over their full range
OPERATIONAL POINTS

## Slide 12
Thus responsibility for Frequency Response must be carried by allocating headroom for Frequency Response duty
to a sufficient number of units
such that
each frequency responsive unit needs to assign only a small fraction of the operational range to reserve for frequency response
PRACTICAL POINTS

## Slide 13
To be achieved with the required timing
Frequency response must be implemented by Primary Control Primary control is - Governing Control
Reserve (headroom) for Frequency Response can be managed by Secondary Controls - such as
plant Distributed Control Systems (DCS)
Balancing Area Automatic Generation Control systems (AGC/LFC)
INSTRUMENTATION AND CONTROL

## Slide 14: INSTRUMENTATION AND CONTROL
Governing action is
local and autonomous
not subject to communication latency
not dependent on reliability of communication
Grid level secondary control (balancing controls / AGC)
is dependent on communication channels
is dependent on reliability of communication

## Slide 15
Modeling of turbine-governor controls has been shown by testing (in WECC, Europe, Asia)to give trustworthy indications of dynamic behavior -
to the extent that the physical effects are represented in the models
Models in general use do not represent effects such as:
fuel gas pressure variations and supply adequacy
quenching effects of water injection (for emissions compliance)
boiler control dynamics
actions of power plant and grid operators
Dynamic simulation data bases do not aid in recognition of:
ambient temperature effects
variation of load characteristic with time of day
plant operational practices
MODELING

## Slide 16
MICROCOSM MODEL FOR SIMULATIONS OF FREQUENCY RESPONSE

## Slide 17
CLASSES OF GENERATING CAPACITY

## Slide 18
Model represents diversity of prime mover types

## Slide 19
Model uses standard elements of PSLF, PSS/E

## Slide 20
ggov1 turbine-controller model

## Slide 21
0
50
100
150
Time, sec
200
250
300
0.71
0.72
0.73
0.74
0.75
0.76
0.77
0.78
0.79
0.8
0.81
Power, Valve command, per unit
tgov-0
Blue= test
Red = model
Prime mover models are well correlated with test responses of operating turbines
(Large steam turbine)

## Slide 22
0
5
10
15
20
25
Time, sec
30
35
40
45
50
0.33
0.34
0.35
0.36
0.37
0.38
0.39
0.4
0.41
Fuel valve, pu
0
5
10
15
20
25
30
35
40
45
50
24
26
28
30
32
34
36
Electrical power, pu
Black - test
Red - model
Prime mover models are well correlated with test responses of operating turbines
(Aeroderivative gas turbine)

## Slide 23
How much frequency responsive reserve is needed immediately
(Rfrac)
How much frequency response must be sustained
after initial response (Sfrac)
What is sensitivity of FR reserve requirement to:
system inertia constant (Heff)
timing of turbine responses
withdrawal of initial response
governor dead bands
gas turbine temperature/speed dependence
How should plant (DCS) and turbine (governor) controls be coordinated
QUESTIONS ADDRESSED BY SIMULATIONS

## Slide 24
Frequency response action by wind generation
Frequency response action by photovoltaic generation
(Both were stipulated not to be a part of the simulation study)
Transmission adequacy and voltage control issues
Sensitivity of losses to power unbalance and redistribution
QUESTIONS NOT ADDRESSED

## Slide 25
Deadband was
zeroed-out for simulations intended to show sensitivity to other factors
modeled explicitly in simulations intended to show its effect
DEAD BAND
Notes: Can be removed..

## Slide 26
FORM and LOCATION of DEAD BAND
ARE SIGNIFICANT

## Slide 27
1.54
1.56
1.58
1.6 1.62
Controller input, percent
1.64
1.66
1.68
47.8
48
48.2
48.4
48.6
48.8
49
GE 7FA +/-0.025 Percent
15 mHz in 60Hz system
G1\FSR vs DTN
67
67.5
68
68.5
69
69.5
70
70.5
71
71.5
72
3.25
3.3
3.35
3.4
3.45
TNR-TNH
3.5
3.55
3.6
3.65
FSR
GE 9FA +/-0.025 Percent
12.5 mHz in 50Hz system
DEAD BAND IS MEASURABLE
and is settable in most modern turbine controls

## Slide 28
Frequency, Hz
59.55
8 10 12 14 16
p2500June/r-2-0.cha p2500June/r3-2-0.cha traj.pdf
18
Time, sec
20
22
24
26
28
59.6
59.65
59.7
59.75
59.8
59.85
59.9
59.95
60
60.05
Frequency, Hz
59.86
9.8 9.9 10 10.1 10.2
p2500June/r-2-0.cha p2500June/r3-2-0.cha traj.pdf
10.3 10.4
Time, sec
10.5
10.6
10.7
10.8
59.88
59.9
59.92
59.94
59.96
59.98
60
60.02
8
10
12
14
16
18
Time, sec
20
22
24
26
28
1440
1460
1480
1500
1520
1540
1560
Power, MW
p2500June/r-2-0.cha p2500June/r3-2-0.cha traj.pdf
59
0 10 20 30 40
p2500June/r-2-2.cha p2500June/s-2-2.cha traj.pdf
50
Time, sec
60
70
80
90
100
59.2
59.4
59.6
59.8
60
60.2
Frequency, Hz
Red H=4
Blue H=3
Red Adequate sustaining fraction
Black
Inadequate
0
1 sec
Frequency
Frequency
Frequency
Turbine
Power
0
20 sec
0
20 sec
0
100 sec
BASIC SIMULATION

## Slide 29: Sensitivity to inertia constant

## Slide 30: Sensitivity to inertia constant
Sensitivity to inertia constant

## Slide 31
H of rotating machines (sec) | Inertia of fleet (MW-sec) | Nadir freq (Hz) | 
4 | 48000 | 59.63 | Zero electronic
3 | 36000 | 59.60 | 
4 | 24000 | 59.55 | 50 percent
3 | 18000 | 59.53 | electronic
Sensitivity to inertia constant –
Mixed-thermal fleet

## Slide 32
Sensitivity to speed of primary response

## Slide 33
Sensitivity to speed of secondary control action

## Slide 34: 0 percent electronic
50 percent electronic

## Slide 35: Rf = 0.4
Sf = 0.6
Rf = 0.4
Sf = 0.9
Red - cautious DCS action
Blue - aggressive DCS action

## Slide 36
When operating at "base load" a gas turbine is at its temperature limit - the governor is NOT in command
When at temperature limit the output of a gas turbine decreases as speed decreases
This behavior is counter to what the power system needs to stabilize frequency
BEHAVIOR OF LARGE GAS TURBINES

## Slide 37
0
50
100
150
200
250
300
350
59.9
59.95
60
60.05
60.1
Frequency, Hz
0
50
100
150
200
250
300
350
65
70
75
80
85
Fuel command
Governor Temp limit
0
50
100
150
200
250
300
350
Time, sec
110
120
130
140
Generator MW
Test conditions
Exhaust temperature limit overrides governor

## Slide 38
Exhaust temperature limit overrides governor

## Slide 39
160 seconds
Frequency collapse largely due to adverse speed-sensitivity of gas turbine maximum power

## Slide 40
58.8
1
59
59.2
0.8
1
59.4
0.9
Frequency nadir
0.6
0.8
59.6
Y Responsive frac
0.7
59.8
0.6
X Droop frac
0.4
0.5
60
0.4
0.3
0.2
0.2
0.1
0
0
a2500redo/aoafmin
Sustaining fraction, Sf
Responsive fraction, Sf
Responsive turbines have 9 percent headroom
2 percent loss of production
Minimum requirement for sustained frequency response is 2/0.09 = 22 percent of total generating capacity
Importance of sustained primary response

## Slide 41
0
10
20
30
40
50
60
70
80
90
100
59.6
59.8
60
60.2
999fbus1-freq
0
10
20
30
40
50
10pm1-pm
30
40
100
11pm1-pm
0
10
20
30
40
50
Steam in droop mode
60 70 80 90
100
1200
1250
1300
1350
0
10
20
Steam in load control mode
50 60 70 80 90
1150
1200
1250
CCGT in droop mode
60 70 80 90
100
1050
1100
1150
1200
12pm1-pm
0
10
20
30
40
50
Time, sec
60
70
80
90
100
1060
1080
1100
1120
14pm1-pm
a2500load/a2500fload-0-1.cha / a2500load/a2500fload-2-1.cha / a2500load/a2500fload-4-1.cha a2500fload-012-1.pdf
D = 0
D = 1
D = 2
Frequency
CCGT in load control mode
Effect of load frequency sensitivity

## Slide 42
Responsibility for Frequency Response must be carried by allocating Frequency Response duty as
a small fraction of the operational range
of a sufficiently large number of turbines
Primary response must be delivered on a time scale of 5-10 seconds - with present fleet make up
As system effective inertia constant decreases, the time scale for delivery of primary response will be correspondingly shortened
Thermal/hydro turbines will, eventually, not be able to provide primary control response with the required promptness
Electronically coupled generation and load can, and will have to, provide and sustain primary control response
COMMENTARY AND CONCLUSION

## Slide 43
0
2
4
6
8
10
Time, sec
12
14
16
18
20
59.6
59.65
59.7
59.75
59.8
59.85
59.9
59.95
60
60.05
60.1
Frequency, Hz
ercot Sat Dec 09 13:14:09 2017
Black
PSS/E full scale
Red Decreased steam
Green Nominal steam
Blue Increased steam
FULL SCALE versus MICROCOSM SIMULATION: ERCOT

## Slide 44: Independent Observations of the Study
Sydney Niemeyer

## Slide 45: Aggregate Frequency Control Performance Required
Provided by the fleet of resources that must be kept on-line at all times to respond to generation-loss events?
All generators, to the extent feasible, must be capable of providing sustained primary frequency response?
All non-traditional resources for primary frequency control such as demand response, energy storage, and other forms of electronically coupled loads and generation should be utilized.
The sensitivity of loads to frequency is changing.
Other countries ensure adequate Primary Frequency Control by requiring specific generator governor settings and by spreading the frequency responsive reserves over many generators.

## Slide 46: Frequency Control Performance Required – The Design Event
The simultaneous loss of the largest, single substation facility.
  STP 1 & 2 1375 MW net each, 1430 MW gross each.
    Following a trip of a nuclear generator the auxiliary power demand will increase not decrease.
    Traditional fossil fueled facilities auxiliary power demand decreases significantly following a trip of the plant.
    Net loss to the grid for a nuclear generator would be closer to 1433 MW each or 2866 MW total compared to the present design of 2750 MW.

## Slide 47: Combined Cycle Facilities Operating at Combustion Turbine Exhaust Temperature Limit.
  Any combustion turbine operating at its temperature limit will decrease MW output at lower frequencies. The rate of decrease is about 2.76 MW/1000 MW of capacity/ 0.1 Hz.
  Given a 30,000 MW interconnection with 35% of generation (10,500 MW) from combustion turbines/combined cycle plants. If 80% (8,400 MW) were operating at the temperature limit. This would result in a decrease in generator output of:
    23 MW at 59.9 Hz.
    69 MW at 59.7 Hz.
    162 MW at 59.3 Hz.
    This occurs anytime frequency is below 60 Hz.

## Slide 48: Total Primary Control Required From Generators
2866 MW loss to the grid.
162 MW loss from combustion turbines.
Less Load Resources tripping at 59.7 Hz.
  1400 MW normal purchase used in this example.
Load Dampening:
  25,000 MW Load ~ 61.25 MW/0.1 Hz or 429 MW @ 59.3 Hz.
  35,000 MW Load ~ 85.75 MW/0.1 Hz or 600 MW @ 59.3 Hz.
  45,000 MW Load ~ 110.25 MW/0.1 Hz or 772 MW @ 59.3 Hz.
MW needed from Generators by the frequency nadir, in 3 to 5 seconds:
  2866 + 162 MW = 3028 MW loss
  Less 1400 MW Load Resources = 3028 – 1400 = 1628 MW
  Less Load Dampening: 1628 – 429 = 1199 MW @ 25,000 MW load.
  Less Load Dampening : 1628 – 600 = 1028 MW @ 35,000 MW load.
  Less Load Dampening: 1628 – 772 = 856 MW @ 45,000 MW load.

## Slide 49: Limits of Generator Performance
Frequency events in the ERCOT Interconnection vary from typical values of:
  ERCOT 59.700 to 59.950 Hz. Frequency rarely goes below 59.700 Hz due to Load Resources tripping.
These typical events limit the generator’s exposure and experience of operating at very low frequencies near UFLS.
During the May 15, 2003 ERCOT event where frequency dropped to 59.28 Hz, generators experienced governor demands that they had never seen before. For 5% droop, a 23% increase. For steam generators a sudden drop in throttle steam pressure reduced governor performance and they were only able to deliver 12 to 13% instead of 23%. Combustion turbines delivered around 18%. These limits in delivery must be accounted for and understood.

## Slide 50: Governor Dead-bands
A Large Dead-band of 0.036 Hz as compared to a 0.017 Hz Dead-band will result in less Primary Frequency Response.
  19% less Primary Frequency Response for a 59.90 Hz Deviation
  9.5% less Primary Frequency Response for a 59.80 Hz Deviation
  6.3% less Primary Frequency Response for a 59.70 Hz Deviation
  2.7% less Primary Frequency Response for a 59.30 Hz Deviation
Large Dead-bands on governors reduce Primary Frequency Response and delay the delivery of the response.

## Slide 51: Standards and Requirements on Primary Frequency Control
NERC BAL-003-1 Does not have requirements on governor settings or the speed of delivery of response.
NERC Regional Standard BAL-001-TRE-1 does have requirements on governor settings but not on the speed of delivery of response at the frequency nadir.
MOD-27 does not require any response, only that the models reflect the actual generator performance.

## Slide 52: Summary
The speed of delivery of Primary Frequency Response is critical.
  Steam turbines are fast for a portion of their response but have limited response due to the decay in throttle steam pressure during extreme events.
  Combustion turbines are good responders but are slower than steam turbines.
  Hydro turbines are much slower but can deliver large quantities of response.
Frequency Responsive Reserves must be spread over many generators to successfully deliver the needed response in the time required to prevent UFLS action.

## Slide 53
Thank You
Joe Eto – jheto@lbl.gov
John Undrill - jundrill1@gmail.com
Sydney Niemeyer - sydney.niemeyer@att.net
Eddy Lim - Eddy.Lim@ferc.gov