## Slide 1
HDL/LDL Manual Overrides
Wholesale Markets Subcommittee
Sean Chang
Market Analysis & Validation
5/2/2018

## Slide 2: Introduction
Per protocol language section 6.5.7.1.13 (10):
  No sooner than sixty days after the applicable Operating Day, ERCOT shall provide to the appropriate TAC subcommittee instances of manual overrides of HDL or LDL, including the name of the Generation Resource, the reason for the override, and, as applicable, the cost as calculated in Section 6.6.3.9, Real-Time High Dispatch Limit Override Energy Payment.

## Slide 3: Manual Override Driver
HDL/LDL override for BASTEN_CC1_2 due to RLC logic causing SCED to give base points above HASL for an extended amount of time:
  This led to periods with the total expected generation at a value greater than the Resource’s HSL
  12 SCED intervals (2/10/2018 12:00-12:55)
No costs as calculated as in Section 6.6.3.9, Real-Time High Dispatch Limit Override Energy Payment

## Slide 4: Additional Detail
Resource had significant REGUP, RRS, and REGDN responsibilities with a narrow dispatch range between LASL and HASL
When resource was fully deployed on regulation, SCED could not dispatch resource below HASL since:
(Output – SCED Down Ramp * 5) > HASL
SCED Down Ramp = (Telemetered Down Ramp Rate
– Reg. Down Responsibility / 7)
RLC sets HDL=LDL=(Output – SCED Down Ramp * 5) and SCED ends up giving a base point greater than HASL

## Slide 5: Observations
Typically, this situation does not last long because dispatch returns to normal range once enough regulation has been recalled
RLC logic working as designed
Logic set to ensure that base point could be achieved based on ramp available to resource
Lesson learned during Nodal LFC testing that led to this logic but does have flaw in this situation
Currently exploring potential solutions